## site_summary
plant_id | plant_name | state | ba | owner | operator | customer_group | ssi_prospect | hybrid | hybrid_reasons | chem | enclosure | applications | nameplate_mw | e_rated_mwh | duration_h | dur_band | cod_year | lead_rank | conviction_tier | dominant_signature | eta_true | naive_rte_mean_month | P_aux_pct_nameplate | hvac_excess_mw | eta_trend_pts_per_yr | paux_trend_pct_per_yr | trend_status | fade_pct_per_yr | fade_status | cum_efc | throughput_used | warranty_headroom | warranty_cycles_assumed | envelope_breach_months | availability_months | asym_rated | asym_realised_avgpower_proxy | mwh_at_stake_total | max_charge_mw | max_discharge_mw | P_aux_mw | naive_rte | n | r2 | EAL_MWh_FULL_OUTAGE | EAL_MWh_PARTIAL_AVAILABILITY | EAL_MWh_THERMAL_AUX | EAL_MWh_UNATTRIBUTED | P12_FULL_OUTAGE | P12_PARTIAL_AVAILABILITY | P12_THERMAL_AUX | P12_UNATTRIBUTED | lam_hat_FULL_OUTAGE | lam_hat_PARTIAL_AVAILABILITY | lam_hat_THERMAL_AUX | lam_hat_UNATTRIBUTED | RTE_2019 | RTE_2020 | RTE_2021 | RTE_2022 | RTE_2023 | RTE_2024 | RTE_2025 | EFC_2019 | EFC_2020 | EFC_2021 | EFC_2022 | EFC_2023 | EFC_2024 | EFC_2025 | UTI_2019 | UTI_2020 | UTI_2021 | UTI_2022 | UTI_2023 | UTI_2024 | UTI_2025 | dominant_reason
141 | Agua Fria | AZ | SRP | Salt River Project | Salt River Project |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | System Peak Shaving | 25 | 100 | 4 | 2.5-4.5h | 2021 | 121 | C | HYBRID_ARTEFACT | 0.88371 | 0.80533 | 0.7272 | -0.13773 | -2.4722 | -25.753 | ok | -0.2374 | ok | 875.65 | 0.14594 | 0.85406 | 6000 | 12 | 6 | 1 | 0.59068 | 1543 | 25 | 25 | 0.1818 | 0.82369 | 49 | 0.36749 | 821.0995 | 74.8404 | 29.3554 | 0.18332 | 0.08949 | 0.14465 | 0.04644 | 0.0011993 | 0.0078125 | 0.013021 | 0.0040625 | 0.0001 |  |  | 0.84246 | 0.84633 | 0.78874 | 0.82196 | 0.83554 |  |  | 64.92 | 201.29 | 240.92 | 219.61 | 148.91 |  |  | 0.99021 | 0.9167 | 0.94015 | 0.80006 | 0.4852 | PARTIAL_AVAILABILITY
260 | Dynegy Moss Landing Power Plant Hybrid | CA | CISO | Dynegy -Moss Landing LLC | Dynegy -Moss Landing LLC |  |  | TRUE | rte_gt_1 | LIB | BL | Arbitrage | 750 | 3000 | 4 | 2.5-4.5h | 2021.9333 | 3 | C | HYBRID_ARTEFACT | 0.79721 | 0.82314 | -0.14961 | -0.27054 | 5.1133 | 92.1275 | ok | -0.72958 | ok | 849.7955 | 0.14163 | 0.85837 | 6000 | 0 | 2 | 1 | 0.84986 | 46934 | 750 | 750 | -1.1221 | 0.83591 | 43 | 0.34076 | 0 | 0 | 0 | 0 | 0.03025 | 0.20169 | 0.09146 | 0.20982 | 0.0025597 | 0.018771 | 0.0084059 | 0.019625 |  |  | 0.83758 | 0.83857 | 0.84427 | 0.83073 | 0.43544 |  |  | 331.095 | 164.7019 | 194.1077 | 155.1497 | 4.7413 |  |  | 0.78122 | 0.7384 | 0.63806 | 0.5868 | 0 | LOW_ETA_AND_LOW_UTI
389 | El Centro Hybrid | CA | IID | Imperial Irrigation District | Imperial Irrigation District |  |  | FALSE |  | LIB | BL | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 30 | 20 | 0.66667 | <1.5h | 2016 | 68 | A | UNATTRIBUTED | 0.77993 | 0.51966 | 0.74332 | 0.01194 | 0.086568 | 0.88962 | ok | -0.051143 | ok | 1631.1625 | 0.27186 | 0.72814 | 6000 | 26 | 9 | 1 | 0.69262 | 14216.0299 | 30 | 30 | 0.223 | 0.56876 | 74 | 0.44721 | 391.4498 | 16.4674 | 4.8381 | 5.7773 | 0.15519 | 0.12167 | 0.029407 | 0.13299 | 0.014054 | 0.010811 | 0.0025264 | 0.011892 | 0.49842 | 0.58624 | 0.44454 | 0.4457 | 0.64835 | 0.51283 | 0.58325 | 157.65 | 241.65 | 99 | 114.3 | 240.7 | 182.85 | 240.3 | 0.12149 | 0.15483 | 0.092509 | 0.13823 | 0.39831 | 0.41059 | 0.72831 | LOW_ETA_AND_LOW_UTI
645 | Big Bend | FL | TEC | Tampa Electric Co | Tampa Electric Co |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, System Peak Shaving | 12.6 | 25.2 | 2 | 1.5-2.5h | 2017 | 245 | C | FULL_OUTAGE | 0.90825 | 0.70328 | 0.05887 | -0.00075834 |  |  | ok |  | insufficient_history | 25.9127 | 0.0043188 | 0.99568 | 6000 | 0 | 20 | 1 | 0.92568 | 168.5 | 12.6 | 12.6 | 0.0074176 | 0.85772 | 12 | 0.90474 | 9.9721 | 0.16361 | 0.16067 | 0.00064008 | 0.27826 | 0.093193 | 0.07089 | 0.0011993 | 0.027174 | 0.0081522 | 0.006368 | 0.0001 | RTE_2023: 0.88571; RTE_2025: 0.66809; EFC_2023: 19.6825; EFC_2024: 0; EFC_2025: 6.2302; UTI_2023: 0.085619; UTI_2024: 0; UTI_2025: 0.0096278 | FULL_OUTAGE
792 | Palaau Power Hybrid | HI |  | Maui Electric Co Ltd | Maui Electric Co Ltd |  |  | FALSE |  | OTH | CS | Ramping / Spinning Reserve | 2 | 2 | 1 | <1.5h | 2017 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
990 | Harding Street | IN | MISO | AES Indiana | AES Indiana |  |  | FALSE |  | LIB | BL |  | 20 | 20 | 1 | <1.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 20 | 20
1016 | Butler-Warner Generation Plant | NC | CPLE | Fayetteville Public Works Commission | Fayetteville Public Works Commission |  |  | TRUE | pv_same_plant | LIB | CS | Transmission and Distribution Deferral | 0.5 | 0.5 | 1 | <1.5h | 2019 | 442 | C | HYBRID_ARTEFACT | 0.81993 | 0.67997 | 0.76371 | 0.0012847 | -1.8892 | 34.178 | ok | 0 | ok | 1770 | 0.295 | 0.705 | 6000 | 0 | 0 | 1.6667 | 0.84043 | 0 | 0.3 | 0.5 | 0.0038186 | 0.7308 | 44 | 0.618 | 18.2448 | 0.81484 | 0.44349 | 0.5569 | 0.13542 | 0.11205 | 0.048881 | 0.22481 | 0.012126 | 0.009903 | 0.0042873 | 0.021221 | RTE_2022: 0.68153; RTE_2023: 0.65693; RTE_2024: 0.74725; RTE_2025: 0.70529; EFC_2022: 214; EFC_2023: 180; EFC_2024: 816; EFC_2025: 560; UTI_2022: 0.21849; UTI_2023: 0.24101; UTI_2024: 1.7395; UTI_2025: 1.4048 | LOW_ETA_AND_LOW_UTI
1482 | Bonny Eagle | ME | ISNE | Brookfield White Pine Hydro LLC | Brookfield White Pine Hydro LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Voltage or Reactive Power Support | 8 | 16 | 2 | 1.5-2.5h | 2023 | 119 | A | THERMAL_AUX | 0.77888 | 0.79017 | -0.072271 | 0.025445 | 9.7409 | 135.5103 | ok | 0.045721 | ok | 1193.875 | 0.19898 | 0.80102 | 6000 | 0 | 0 | 1 | 0.8155 | 614.3405 | 8 | 8 | -0.0057817 | 0.78661 | 32 | 0.0021744 | 667.8887 | 15.6538 | 12.4416 | 4.9926 | 0.17028 | 0.076884 | 0.048094 | 0.076884 | 0.015556 | 0.0066667 | 0.0042147 | 0.0066667 | RTE_2023: 0.84048; RTE_2024: 0.80384; RTE_2025: 0.7334; EFC_2023: 286.8125; EFC_2024: 491.5; EFC_2025: 415.5625; UTI_2023: 2.1137; UTI_2024: 3.4257; UTI_2025: 3.6644 | THERMAL_AUX
1507 | William F Wyman Hybrid | ME | ISNE | FPL Energy Wyman LLC | FPL Energy Wyman LLC |  |  | FALSE |  | LIB | CS |  | 16.7 | 10.9 | 0.65269 | <1.5h | 2016 | 131 | A | CELL_DEGRADATION | 0.83322 | 0.80771 | 0.1388 | 0.0099548 | -2.4443 | -28.5301 | ok | 0.19754 | ok | 8314.526 | 1.3858 | 0 | 6000 | 0 | 4 | 0.97006 | 0.85103 | 2088.1127 | 16.7 | 16.2 | 0.023179 | 0.83276 | 83 | 0.44162 | 278.126 | 5.07 | 7.2129 | 9.7023 | 0.14606 | 0.051271 | 0.056147 | 0.27079 | 0.013158 | 0.004386 | 0.0049632 | 0.026316 | 0.85613 | 0.86167 | 0.8316 | 0.80574 | 0.80669 | 0.76796 | 0.75933 | 1290.6422 | 1697.2477 | 939.633 | 610.367 | 484.6789 | 289.3578 | 313.7615 | 0.97609 | 1.1488 | 0.73906 | 0.69679 | 0.97022 | 0.55756 | 0.60364 | LOW_ETA_AND_LOW_UTI
1615 | Nantucket Hybrid | MA | ISNE | New England Power Company | Nantucket Electric Co |  |  | FALSE |  | LIB | BL | Transmission and Distribution Deferral | 6 | 48 | 8 | >4.5h | 2019 | 231 | A | UNDER_DISPATCH | 0.87413 | 0.41166 | 0.45416 | -0.0090157 |  |  | ok |  | insufficient_history | 26.9583 | 0.0044931 | 0.99551 | 6000 | 0 | 9 | 1 | 0.78899 | 6895.007 | 6 | 6 | 0.02725 | 0.61007 | 16 | 0.55213 | 0.88963 | 0.053517 | 0.00050461 | 0.012414 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 |  | 0.067568 | 0.44238 | 0.50464 | 0.61335 | 0.47399 | 0.17143 |  | 0.10417 | 2.4792 | 9.0625 | 10.1458 | 3.4167 | 1.75 |  | 0.00070281 | 0.020575 | 0.064985 | 0.39881 | 0.018651 | 0.0017979 | FULL_OUTAGE
1682 | Cleary Flood Hybrid | MA | ISNE | City of Taunton - (MA) | City of Taunton - (MA) |  |  | FALSE |  | LIB | CS |  | 3 | 6 | 2 | 1.5-2.5h | 2020 |  |  | UNDER_DISPATCH | 0.94286 | 0.70992 | 0.45982 | -2.0868e-05 | -0.27738 | -9.7166 | ok | -0.73373 | ok | 393.8333 | 0.065639 | 0.93436 | 6000 | 0 | 0 | 1 | 0.82692 | 1080.4959 | 3 | 3 | 0.013795 | 0.74915 | 36 | 0.91539 | 26.1368 | 0.79409 | 0.27708 | 0.075981 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  | 0.74201 | 0.71957 | 0.73034 | 0.6961 | 0.76667 | 0.77314 |  | 54.1667 | 55.1667 | 65 | 56.5 | 92 | 71 |  | 0.93695 | 0.25021 | 0.28815 | 0.37854 | 1.9606 | 0.99167
2324 | Reid Gardner | NV | NEVP | Nevada Power Co | Nevada Power Co |  |  | FALSE |  | LIB | CS |  | 220 | 220 | 1 | <1.5h | 2023 | 51 | A | UNATTRIBUTED | 0.81626 | 0.84831 | -0.38025 | 0.43077 |  |  | insufficient_history | -0.024446 | ok | 1453.9901 | 0.24233 | 0.75767 | 6000 | 5 | 0 | 1 | 0.84702 | 2794.3342 | 220 | 220 | -0.83654 | 0.84797 | 23 | 0.032091 | 19053.4068 | 5.5573 | 2071.979 | 332.3336 | 0.20148 | 0.0011993 | 0.2612 | 0.20148 | 0.01875 | 0.0001 | 0.029657 | 0.01875 | RTE_2024: 0.85002; RTE_2025: 0.84618; EFC_2024: 651.1909; EFC_2025: 743.6; UTI_2024: 1.7471; UTI_2025: 2.1661 | THERMAL_AUX
2830 | Walter C Beckjord | OH | PJM | Dayton Power & Light Co | Duke Energy Ohio Inc |  |  | TRUE | rte_gt_1 | LIB | CS |  | 4 | 1.8 | 0.45 | <1.5h | 2015 | 455 | C | HYBRID_ARTEFACT | 0.71279 | 0.67016 | 0.44685 | -0.028869 | 2.0041 | 22.4372 | ok | 0.010323 | ok | 7086.6667 | 1.1811 | 0 | 6000 | 0 | 3 | 1 | 0.84889 | 164 | 4 | 4 | 0.017874 | 0.68197 | 82 | 0.076628 | 64.0134 | 4.1373 | 0.69485 | 1.3195 | 0.10809 | 0.12644 | 0.017732 | 0.12644 | 0.0095321 | 0.011265 | 0.0015049 | 0.011265 | 0.41378 | 0.60871 | 0.74115 | 0.78152 | 0.75316 | 0.75119 | 0.72455 | 477.2222 | 760.5556 | 790.5556 | 940 | 728.8889 | 875.5556 | 605 | 0.26043 | 0.40653 | 0.50598 | 0.43792 | 0.52105 | 0.44224 | 0.3989 | LOW_ETA_AND_LOW_UTI
6304 | Kotzebue Hybrid | AK |  | Kotzebue Electric Assn Inc | Kotzebue Electric Assn Inc |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CT | Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, System Peak Shaving, Load Management, Backup Power, Excess Wind and Solar Generation | 1.2 | 1 | 0.83333 | <1.5h | 2015 | 291 | C | HYBRID_ARTEFACT | 0.72944 | 0.92778 | -0.041573 | 1.5223e-05 | -7.2631 | -23.9474 | ok | 0.11537 | ok | 480.5833 | 0.080097 | 0.9199 | 6000 | 34 | 3 | 1 | 0.49729 | 6 | 1.2 | 1.2 | -0.00049887 | 0.8481 | 33 | 0.68875 | 4.126 | 0.17357 | 0.058366 | 0.060894 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 | 0.9186 | 0.26923 | 0.19626 | 0.35 | 0.88889 | 1 | 0.79592 | 79 | 21 | 21 | 49 | 16 | 12 | 39 | 0.057614 | 0.013179 | 0.017463 | 0.059609 | 0.02183 | 0.02901 | 0.14924 | LOW_ETA_AND_LOW_UTI
6377 | Ocracoke Hybrid | NC | PJM | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage | 1 | 1 | 1 | <1.5h | 2017 |  |  | HYBRID_ARTEFACT | 0.8846 | 0.52479 | 0.14522 | 0.00036604 |  |  | ok |  | insufficient_history | 197 | 0.032833 | 0.96717 | 6000 | 0 | 0 | 1 | 0.64583 | 0 | 0.5 | 0.5 | 0.0014522 | 0.81098 | 16 | 0.17808 | 2.0988 | 0.13565 | 0.024635 | 0.043264 | 0.10809 | 0.12644 | 0.019147 | 0.12644 | 0.0095321 | 0.011265 | 0.0016274 | 0.011265 |  | 2 |  |  | 0.83696 | 0.30769 | 0.27193 |  | 14 | 0 | 0 | 77 | 44 | 62 |  | 0.084281 | 0 | 0 | 0.043706 | 0.0058115 | 0.017648
6704 | Pebbly Beach Generating Station Hybrid | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | NAB | CS | Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support | 1 | 6.8 | 6.8 | >4.5h | 2012 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
8063 | DeCordova Steam Electric Station | TX | ERCO | DeCordova Power Company LLC | Luminant Generation Company LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 269.1 | 263 | 0.97733 | <1.5h | 2022 | 73 | A | UNDER_DISPATCH | 2.1061 | 0.66292 | 1.5243 | 1.1575 | 21.5781 | 123.6667 | ok | 0.32841 | ok | 551.2738 | 0.091879 | 0.90812 | 6000 | 4 | 5 | 1 | 0.73806 | 127972.8605 | 263 | 263 | 4.1019 | 0.64955 | 36 | 0.3792 | 163.6328 | 44.7437 | 77.842 | 165.5389 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2022: 0.73816; RTE_2023: 0.67451; RTE_2024: 0.69006; RTE_2025: 0.58245; EFC_2022: 165.0837; EFC_2023: 134.7529; EFC_2024: 137.9087; EFC_2025: 113.5285; UTI_2022: 1.5106; UTI_2023: 0.26464; UTI_2024: 0.62776; UTI_2025: 0.49697 | PARTIAL_AVAILABILITY
10156 | Fresno Cogen Partners | CA | CISO | Fresno Power Investors LP | Wellhead Services, Inc |  |  | FALSE |  | LIB | CS | Load Following | 16 | 16 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.36808 | 0.29026 | -0.028311 | 0.0013881 |  |  | ok | 1.4919 | ok | 43.4375 | 0.0072396 | 0.99276 | 6000 | 0 | 0 | 1 | 0.38983 | 33262.0389 | 16 | 16 | -0.0045298 | 0.38469 | 15 | 0.13964 | 12.2703 | 1.0066 | 0.34596 | 0.053505 | 0.13809 | 0.19981 | 0.057374 | 0.03647 | 0.012384 | 0.018576 | 0.0050785 | 0.003096 | RTE_2023: 0.40091; RTE_2024: 0.31058; RTE_2025: 0.2167; EFC_2023: 11; EFC_2024: 19.625; EFC_2025: 12.8125; UTI_2023: 0.019431; UTI_2024: 0.024462; UTI_2025: 0.012134
10444 | Lockhart Solar PV, LLC | CA | CISO | Terra-Gen Operating Co-Solar | Terra-Gen Operating Co-Solar |  |  | TRUE | pv_same_plant | LIB | CS |  | 69 | 69 | 1 | <1.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.66057 |  |  |  |  | insufficient_history |  | insufficient_history | 218.8986 | 0.036483 | 0.96352 | 6000 | 0 | 0 | 1 | 0.84526 | 0 | 69 | 69 |  |  |  |  | 4935.6243 | 134.9596 | 2.1209 | 236.7426 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.82948; EFC_2025: 218.8986; UTI_2025: 1.0499
10493 | Rumford Falls Hydro Facility | ME | ISNE | Brookfield Power New England | Brookfield Power New England |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 8 | 16 | 2 | 1.5-2.5h | 2023 | 203 | B | CELL_DEGRADATION | 0.8457 | 0.79438 | 0.79634 | 0.043189 | -12.3101 | -118.4463 | ok | -0.2228 | ok | 909.875 | 0.15165 | 0.84835 | 6000 | 0 | 2 | 1 | 0.7649 | 698.8454 | 8 | 8 | 0.063707 | 0.79413 | 24 | 0.10566 | 700.4269 | 16.4164 | 6.5175 | 5.2359 | 0.17028 | 0.076884 | 0.024628 | 0.076884 | 0.015556 | 0.0066667 | 0.0021053 | 0.0066667 | RTE_2024: 0.80367; RTE_2025: 0.78452; EFC_2024: 462.0625; EFC_2025: 447.8125; UTI_2024: 2.8657; UTI_2025: 3.5194 | PARTIAL_AVAILABILITY
50064 | University of California Santa Cruz | CA | CISO | Forefront Power, LLC | University of California Santa Cruz |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 1 | 1 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.9279 | 0.87969 | 0.086671 | -6.5954e-05 |  |  | ok | 0 | ok | 308 | 0.051333 | 0.94867 | 6000 | 0 | 2 | 1 | 0.88889 | 22.5 | 1 | 1 | 0.00086671 | 0.88761 | 22 | 0.3116 | 10.9069 | 0.89471 | 0.32469 | 0.04756 | 0.13809 | 0.19981 | 0.060381 | 0.03647 | 0.012384 | 0.018576 | 0.0053621 | 0.003096 | RTE_2024: 0.89447; RTE_2025: 0.87838; EFC_2024: 178; EFC_2025: 130; UTI_2024: 0.25844; UTI_2025: 0.15732
50300 | VESI Pomona | CA | CISO | VESI Pomona Energy Storage, Inc. | VESI Pomona Energy Storage, Inc. |  |  | FALSE |  | LIB | BL | Frequency Regulation | 40 | 40 | 1 | <1.5h | 2019.5 | 456 | A | UNATTRIBUTED | 0.9922 | 0.85019 | 0.96886 | -0.0019866 | -1.1975 | 10.0174 | ok | 0.055568 | ok | 8653.7917 | 1.4423 | 0 | 6000 | 0 | 0 | 1 | 0.89263 | 45328.9849 | 40 | 40 | 0.38754 | 0.85988 | 84 | 0.6703 | 1099.5805 | 49.1093 | 23.0273 | 33.5635 | 0.13542 | 0.11205 | 0.042405 | 0.22481 | 0.012126 | 0.009903 | 0.0036936 | 0.021221 | 0.89405 | 0.8806 | 0.89213 | 0.8819 | 0.86309 | 0.79747 | 0.76782 | 1124 | 874 | 1485.35 | 1415.85 | 596.35 | 465.7 | 350.875 | 0.67498 | 0.58087 | 3.6974 | 1.7007 | 0.86054 | 0.53598 | 0.50075 | ELEVATED_P_AUX
54134 | Great Lakes Hydro America - ME | ME | ISNE | Great Lakes Hydro America LLC | Great Lakes Hydro America LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 20 | 20 | 1 | <1.5h | 2020 | 191 | B | UNATTRIBUTED | 0.88399 | 0.80198 | 0.53069 | -0.021483 | -0.94561 | -6.9196 | ok | 0.19443 | ok | 2637.25 | 0.43954 | 0.56046 | 6000 | 1 | 2 | 1.25 | 0.96863 | 3472.9489 | 8 | 10 | 0.10614 | 0.80608 | 36 | 0.36365 | 202.8075 | 55.4556 | 0.36811 | 38.9115 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 |  |  | 0.96905 | 0.80929 | 0.80721 | 0.79915 | 0.81212 |  |  | 784.4 | 599.6 | 435.25 | 416 | 402 |  |  | 0.65124 | 0.67291 | 0.79185 | 0.65384 | 0.67752 | PARTIAL_AVAILABILITY
54296 | Biola University Hybrid | CA | CISO | Biola University | Biola University |  |  | TRUE | rte_gt_1 | LIB | CS |  | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2018 | 382 | C | HYBRID_ARTEFACT | 0.85003 | 0.79077 | 0.086512 | 0.00010298 | -3.4933 | 26.1669 | ok | 0 | ok | 356.5 | 0.059417 | 0.94058 | 6000 | 0 | 2 | 1 | 0.84615 | 3 | 0.3 | 0.3 | 0.00025954 | 0.80193 | 65 | 0.028644 | 1.9703 | 0.067345 | 0.00050461 | 0.017183 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | 0.81818 | 0.89286 | 0.84615 | 0.84906 | 0.7931 | 0.67568 | 0.34483 | 18 | 50 | 66 | 90 | 46 | 50 | 20 | 0.8 | 0.62084 | 0.14019 | 0.22825 | 0.0764 | 0.14769 | 0.074209 | LOW_ETA_AND_LOW_UTI
54639 | Berlin Gorham | NH | ISNE | Great Lakes Hydro America LLC | Great Lakes Hydro America LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 14 | 14 | 1 | <1.5h | 2023 | 175 | A | PARTIAL_AVAILABILITY | 0.90483 | 0.8499 | 0.51748 | 0.0097865 | 2.8996 | 28.1787 | ok | 0.21106 | ok | 1289.9286 | 0.21499 | 0.78501 | 6000 | 1 | 6 | 1 | 0.86559 | 152 | 14 | 14 | 0.072447 | 0.85068 | 24 | 0.39217 | 557.13 | 30.4683 | 0.37921 | 3.2392 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.84951; RTE_2025: 0.85189; EFC_2024: 656.4286; EFC_2025: 633.5; UTI_2024: 1.6462; UTI_2025: 1.611 | PARTIAL_AVAILABILITY
55370 | Green Mountain Storage, LLC | PA | PJM | Green Mountain Storage, LLC | Green Mountain Storage, LLC |  |  | FALSE |  | LIB | CT |  | 10.4 | 10.4 | 1 | <1.5h | 2016 |  |  | UNDER_DISPATCH | 0.88713 | 0.75598 | 0.73379 | -0.0072561 |  |  | insufficient_history | -0.081089 | ok | 9830.2244 | 1.6384 | 0 | 6000 | 0 | 0 | 1 | 0.87335 | 39219.343 | 10.4 | 10.4 | 0.076314 | 0.83924 | 17 | 0.9797 | 0 | 0 | 0 | 0 | 0.10809 | 0.12644 | 0.019147 | 0.12644 | 0.0095321 | 0.011265 | 0.0016274 | 0.011265 | 0.82743 | 0.85328 | 0.84807 | 0.87336 | 0.85176 | 0.57714 | 0 | 889.8077 | 1618.8462 | 1643.9423 | 1915.0962 | 1291.1538 | 98.5577 | 0 | 0.43271 | 0.82707 | 0.92433 | 0.94182 | 0.72855 | 0.0027854 | 0
55510 | Border Hybrid Energy Center | CA | CISO | CalPeak Power - Border LLC | CalPeak Power, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 54.1 | 54.1 | 1 | <1.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 0 | 1 | 0 | 0 | 52 | 52 | [16 empty] | RTE_2025: 0; EFC_2025: 0; UTI_2025: 0
56472 | Grapeland Hybrid | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | BL | Frequency Regulation | 10 | 10 | 1 | <1.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
56475 | Center Hybrid | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | BL | Frequency Regulation | 10 | 10 | 1 | <1.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
56961 | Notrees Windpower Hybrid | TX | ERCO | DEGS Wind 1 LLC | Deriva Energy |  |  | FALSE |  | LIB | BL | Excess Wind and Solar Generation | 36 | 13.6 | 0.37778 | <1.5h | 2012 | 457 | B | UNDER_DISPATCH | 1.1042 | 0.68079 | 0.98583 | -0.021055 | -1.3547 | -5.3582 | ok | 0.19849 | ok | 7154.5956 | 1.1924 | 0 | 6000 | 6 | 2 | 1 | 0.85349 | 33258.801 | 36 | 36 | 0.3549 | 0.74991 | 77 | 0.59672 | 162.1089 | 13.2981 | 0.1148 | 11.3102 | 0.10997 | 0.16034 | 0.0011985 | 0.3725 | 0.0097087 | 0.014563 | 0.0001 | 0.038835 | 0.76253 | 0.77375 | 0.80106 | 0.79723 | 0.76192 | 0.67891 | 0.33045 | 590.7353 | 710.8824 | 677.1324 | 634.5588 | 494.8529 | 281.3971 | 171.3971 | 0.41896 | 0.51114 | 0.38867 | 1.6776 | 0.94606 | 1.2933 | 0.87914 | PARTIAL_AVAILABILITY
56981 | Pyron Wind Farm LLC Hybrid | TX | ERCO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | rte_gt_1 | LIB | CS | Excess Wind and Solar Generation | 9.9 | 9.9 | 1 | <1.5h | 2018 | 449 | C | HYBRID_ARTEFACT | 0.97322 | 0.64322 | 1.6359 | 0.034491 | -1.4886 | 30.1354 | ok | 0.74971 | ok | 3067.5758 | 0.51126 | 0.48874 | 6000 | 7 | 2 | 1 | 0.78747 | 15.5 | 9.9 | 9.9 | 0.16196 | 0.73911 | 71 | 0.37685 | 30.9966 | 2.5427 | 0.02195 | 2.1626 | 0.10997 | 0.16034 | 0.0011985 | 0.3725 | 0.0097087 | 0.014563 | 0.0001 | 0.038835 | 0.82556 | 0.81308 | 0.82621 | 0.7469 | 0.51985 | 0.67749 | 0.21592 | 443.1313 | 522.4242 | 523.4343 | 292.1212 | 263.2323 | 499.2929 | 80.8081 | 0.36104 | 0.33323 | 0.71873 | 0.5723 | 0.55209 | 0.58848 | 0.11104 | ELEVATED_P_AUX
56984 | Inadale Wind Farm LLC Hybrid | TX | ERCO | RWE Clean Energy | RWE Clean Energy |  |  | FALSE |  | LIB | CS | Excess Wind and Solar Generation | 9.9 | 9.9 | 1 | <1.5h | 2018 | 78 | A | UNATTRIBUTED | 0.77548 | 0.50406 | 0.71029 | -0.001828 | 7.0112 | 10.5973 | ok | 0.86749 | ok | 2006.0606 | 0.33434 | 0.66566 | 6000 | 5 | 0 | 1 | 0.71305 | 2056.8873 | 9.9 | 9.9 | 0.070319 | 0.54181 | 32 | 0.72761 | 48.4545 | 3.9748 | 0.034313 | 3.3806 | 0.10997 | 0.16034 | 0.0011985 | 0.3725 | 0.0097087 | 0.014563 | 0.0001 | 0.038835 | 0.74945 | 0.7157 | 0.71274 | 0.64874 | 0.57251 | 0.49623 | 0.48865 | 343.8384 | 373.0303 | 400 | 240.101 | 129.596 | 93.0303 | 82.6263 | 0.27135 | 0.23821 | 0.60614 | 0.55938 | 0.2394 | 0.12887 | 0.14886 | LOW_ETA_AND_LOW_UTI
57045 | Rolling Thunder Wind Farm Hybrid | SD | SWPP | Clearlight Energy Holdings LP | Clearlight Energy Holdings LP |  |  | FALSE |  | LIB | CS | Backup Power, Excess Wind and Solar Generation | 0.8 | 0.8 | 1 | <1.5h | 2018 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.3 | 0.3
57082 | Kaheawa Wind Power II LLC | HI |  | Evergreen Wind, LLC | Evergreen Wind, LLC |  |  | TRUE | colocated_firming | LIB | BL | Frequency Regulation, Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, Voltage or Reactive Power Support, Backup Power | 10 | 20 | 2 | 1.5-2.5h | 2012 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
57087 | Kahuku Wind Power LLC | HI |  | Evergreen Wind, LLC | Evergreen Wind, LLC |  |  | FALSE | [11 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
57206 | Soldotna | AK |  | Homer Electric Assn Inc | Homer Electric Assn Inc |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Load Management | 46.5 | 93 | 2 | 1.5-2.5h | 2022 | 154 | A | UNDER_DISPATCH | 1.1293 | 0.74966 | 0.34002 | 0.013436 |  |  | ok | -2.1248 | ok | 101.0108 | 0.016835 | 0.98316 | 6000 | 1 | 8 | 1 | 0.81781 | 44653.6686 | 46.5 | 46.5 | 0.15811 | 0.75278 | 36 | 0.68769 | 112.6079 | 36.9498 | 0.13549 | 5.8924 | 0.066273 | 0.3373 | 0.0011985 | 0.18593 | 0.0057143 | 0.034286 | 0.0001 | 0.017143 | RTE_2023: 0.72019; RTE_2024: 0.75851; RTE_2025: 0.77768; EFC_2023: 31.3011; EFC_2024: 33.3011; EFC_2025: 36.4086; UTI_2023: 0.14496; UTI_2024: 0.13519; UTI_2025: 0.14217 | PARTIAL_AVAILABILITY
57242 | Mililani South Solar Farm | HI |  | Mililani I Solar LLC | Mililani I Solar LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 39 | 156 | 4 | 2.5-4.5h | 2022 | 40 | C | HYBRID_ARTEFACT | 0.92127 | 0.91288 | 0.1743 | 0.010379 | -8.8823 | 107.7069 | ok | -0.14791 | ok | 621.8462 | 0.10364 | 0.89636 | 6000 | 0 | 9 | 1 | 0.98386 | 4231.5 | 39 | 39 | 0.067978 | 0.91168 | 30 | 0.033695 | 23.1853 | 402.9016 | 53.3587 | 30.2357 | 0.0011993 | 0.31703 | 0.038587 | 0.085813 | 0.0001 | 0.031776 | 0.0033474 | 0.0074766 | RTE_2023: 0.98497; RTE_2024: 0.9759; RTE_2025: 0.82316; EFC_2023: 128.1474; EFC_2024: 251.2628; EFC_2025: 242.4359; UTI_2023: 1.1236; UTI_2024: 0.93699; UTI_2025: 0.82842 | PARTIAL_AVAILABILITY
57325 | FPL Energy Illinois Wind LLC Hybrid | IL | PJM | FPL Energy Illinois Wind LLC | FPL Energy Illinois Wind LLC |  |  | TRUE | rte_gt_1 | LIB | CS |  | 20 | 8.3 | 0.415 | <1.5h | 2014 | 458 | C | HYBRID_ARTEFACT | 0.89811 | 0.90938 | 0.029268 | 0.031486 | -0.73845 | 31.6001 | ok | 0.0098119 | ok | 24216.6064 | 4.0361 | 0 | 6000 | 0 | 3 | 1 | 0.97999 | 2826 | 20 | 20 | 0.0058536 | 0.93624 | 83 | 0.030211 | 312.0215 | 20.1663 | 3.3869 | 6.4319 | 0.10809 | 0.12644 | 0.017732 | 0.12644 | 0.0095321 | 0.011265 | 0.0015049 | 0.011265 | 0.89895 | 1.0536 | 0.8646 | 0.86622 | 1.0041 | 0.96105 | 0.75106 | 1305.4217 | 4130.1205 | 3134.3373 | 3531.6867 | 3801.3253 | 2170.3614 | 704.0964 | 0.75742 | 2.3005 | 2.1564 | 1.6355 | 2.8652 | 0.98301 | 0.40325 | PARTIAL_AVAILABILITY
57447 | Laurel Mountain Hybrid | WV | PJM | AES Distributed Energy | AES Distributed Energy |  |  | FALSE |  | LIB | CS | Excess Wind and Solar Generation | 16 | 16 | 1 | <1.5h | 2011 | 49 | A | UNATTRIBUTED | 0.80524 | 0.69513 | 1.3409 | 0.061662 | -3.8966 | -28.4876 | ok | 0.040805 | ok | 10103.2344 | 1.6839 | 0 | 6000 | 0 | 6 | 1 | 0.67 | 11268.0965 | 16 | 16 | 0.21454 | 0.70183 | 77 | 0.37989 | 439.6984 | 28.4182 | 4.8181 | 9.0637 | 0.10809 | 0.12644 | 0.017898 | 0.12644 | 0.0095321 | 0.011265 | 0.0015192 | 0.011265 | 0.73428 | 0.7019 | 0.69042 | 0.70303 | 0.68174 | 0.69381 | 0.67184 | 817.9375 | 636.625 | 548.0625 | 620.25 | 746.375 | 571.3125 | 232.625 | 0.40193 | 0.32553 | 0.35046 | 0.30653 | 0.39456 | 0.29502 | 0.23156 | LOW_ETA_AND_LOW_UTI
57560 | Chino Valley Solar | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 19 | 76 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.91859 | 0.79353 | 0.96913 | 0.070426 | -3.4265 | -57.0148 | ok | -0.33285 | ok | 487.4211 | 0.081237 | 0.91876 | 6000 | 0 | 0 | 1 | 0.83067 | 0 | 19 | 19 | 0.18413 | 0.84998 | 23 | 0.98778 | 13.8789 | 0.75901 | 0.95421 | 61.5453 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2024: 0.84297; RTE_2025: 0.85255; EFC_2024: 226.25; EFC_2025: 261.1711; UTI_2024: 0.92371; UTI_2025: 0.87076
57561 | Cotton Center Solar Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 17 | 51 | 3 | 2.5-4.5h | 2023 | 222 | C | HYBRID_ARTEFACT | 0.86715 | 0.82986 | 0.50841 | 0.062456 | -0.83474 | -29.6936 | ok | 0.45118 | ok | 571.5686 | 0.095261 | 0.90474 | 6000 | 7 | 2 | 1 | 0.84502 | 71 | 17 | 17 | 0.08643 | 0.82954 | 24 | 0.030485 | 9.3835 | 217.852 | 0.64514 | 0.16367 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.82561; RTE_2025: 0.83318; EFC_2024: 273.5686; EFC_2025: 298; UTI_2024: 1.0398; UTI_2025: 0.89059 | PARTIAL_AVAILABILITY
57562 | Paloma Solar Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 17 | 51 | 3 | 2.5-4.5h | 2023 | 397 | C | HYBRID_ARTEFACT | 0.85475 | 0.83029 | 0.34884 | 0.061737 | -7.3065 | -153.1079 | ok | -0.51817 | ok | 588.0784 | 0.098013 | 0.90199 | 6000 | 7 | 2 | 1 | 0.83479 | 0 | 17 | 17 | 0.059303 | 0.82998 | 24 | 0.017992 | 9.4605 | 219.6412 | 0.65044 | 0.16501 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.82817; RTE_2025: 0.83173; EFC_2024: 289.2745; EFC_2025: 298.8039; UTI_2024: 1.0921; UTI_2025: 0.90313 | PARTIAL_AVAILABILITY
57563 | Hyder Solar Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 16 | 48 | 3 | 2.5-4.5h | 2023 | 392 | C | HYBRID_ARTEFACT | 0.97373 | 0.83464 | 1.5852 | 0.049674 |  |  | ok | -0.31706 | ok | 547.4583 | 0.091243 | 0.90876 | 6000 | 8 | 0 | 1 | 0.86692 | 0 | 16 | 16 | 0.25363 | 0.83587 | 24 | 0.43118 | 8.3743 | 194.4225 | 0.57576 | 0.14607 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.83388; RTE_2025: 0.83771; EFC_2024: 263.3333; EFC_2025: 284.125; UTI_2024: 1.0213; UTI_2025: 0.88361 | ELEVATED_P_AUX
57583 | Battery Energy Storage System | AK |  | Golden Valley Elec Assn Inc | Golden Valley Elec Assn Inc |  |  | FALSE |  | NIB | BL | Frequency Regulation, Ramping / Spinning Reserve | 40 | 11 | 0.275 | <1.5h | 2003 | 386 | B | UNDER_DISPATCH |  | 0.092839 |  |  |  |  | insufficient_history | -0.43075 | ok | 437.9015 | 0.072984 | 0.92702 | 6000 | 29 | 4 | 10 | 0.20785 | 61955.2213 | 4 | 40 |  |  |  |  | 17.5353 | 0.73767 | 0.21673 | 0.2588 | 0.15519 | 0.12167 | 0.029407 | 0.13299 | 0.014054 | 0.010811 | 0.0025264 | 0.011892 | 0.05533 | 0.049492 | 0.078389 | 0.14009 | 0.10807 | 0.10804 | 0.061204 | 17.3636 | 13.2727 | 26.5455 | 37.4545 | 26.9091 | 32.7273 | 21.7273 | 0.013235 | 0.0084559 | 0.015778 | 0.031212 | 0.044465 | 0.068418 | 0.05601 | PARTIAL_AVAILABILITY
57584 | University of California San Diego Hybri | CA | CISO | University of California San Diego | University of California San Diego |  |  | FALSE |  | LIB | CS | Load Following, Load Management | 2.5 | 5 | 2 | 1.5-2.5h | 2015 | 248 | A | UNATTRIBUTED | 0.84818 | 0.85566 | -0.012113 | -0.0029713 | -1.1209 | -18.0885 | ok | 1.2793 | ok | 3020.4 | 0.5034 | 0.4966 | 6000 | 0 | 7 | 1 | 0.87234 | 259.365 | 2.5 | 2.5 | -0.00030282 | 0.86149 | 76 | 0.07749 | 26.5993 | 0.90916 | 0.0068122 | 0.23198 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | 0.87234 | 0.85443 | 0.85956 | 0.86772 | 0.86323 | 0.84805 | 0.81203 | 492 | 270 | 264.4 | 164 | 174.2 | 117.2 | 21.6 | 0.34327 | 0.20217 | 0.27098 | 0.60866 | 0.52355 | 0.37441 | 0.097132 | LOW_ETA_AND_LOW_UTI
57693 | DOE Golden NWTC Research Side Hybrid | CO | PSCO | DOE National Renewable Energy Laboratory | DOE National Renewable Energy Laboratory |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 1.3 | 1.3 | 1 | <1.5h | 2019 |  |  | HEALTHY | [8 empty] | insufficient_history | 12.3077 | 0.0020513 | 0.99795 | 6000 | 0 | 0 | 1 | 0.39725 | 0 | 1.3 | 1.3 | [16 empty] | RTE_2019: 0.39024; EFC_2019: 12.3077; UTI_2019: 0.0092536
57996 | Auwahi Wind Energy Hybrid | HI |  | Auwahi Wind Energy LLC | Auwahi Wind Energy LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 11 | 4.4 | 0.4 | <1.5h | 2012 | 217 | A | UNDER_DISPATCH | 1.1137 | 0.90603 | 0.23002 | 0.0018186 |  |  | ok | -0.07637 | ok | 3143.3144 | 0.52389 | 0.47611 | 6000 | 0 | 5 | 1 | 0.9593 | 1819.1354 | 11 | 11 | 0.025302 | 0.91321 | 36 | 0.3073 | 109.8535 | 4.6213 | 1.554 | 1.6213 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 | 0.74455 | 0.90304 | 0.86212 | 0.86519 | 0.86766 | 0.89528 | 0.96965 | 225.2273 | 249.7727 | 270 | 258.1818 | 225 | 254.5455 | 290.4545 | 0.16425 | 0.1526 | 0.21098 | 0.29627 | 0.34571 | 0.55844 | 0.88972 | PARTIAL_AVAILABILITY
57997 | Foothills Solar Plant Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 35 | 105 | 3 | 2.5-4.5h | 2023 | 389 | C | HYBRID_ARTEFACT | 0.93541 | 0.81269 | 1.3951 | 0.14362 |  |  | ok | -0.13418 | ok | 509.9333 | 0.084989 | 0.91501 | 6000 | 8 | 2 | 1 | 0.80803 | 0 | 35 | 35 | 0.4883 | 0.81324 | 24 | 0.33619 | 17.5853 | 408.2702 | 1.209 | 0.30673 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.80451; RTE_2025: 0.82129; EFC_2024: 242.0667; EFC_2025: 267.8667; UTI_2024: 0.96131; UTI_2025: 0.84762 | ELEVATED_P_AUX
58223 | Hoag Hospital Cogen Plant | CA | CISO | Hoag Memorial Presbyterian Hospital | Hoag Memorial Presbyterian Hospital |  |  | FALSE |  | LIB | CS |  | 1 | 4.2 | 4.2 | 2.5-4.5h | 2020 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
58236 | Marshalltown Generating Station | IA | MISO | Interstate Power and Light Co | Interstate Power and Light Co |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 0.3 | 0.6 | 2 | 1.5-2.5h | 2020 | 268 | C | HYBRID_ARTEFACT | 0.89339 | 0.90779 | -0.038402 | 0.00025954 | -7.5456 | -169.8884 | ok |  | insufficient_history | 651.6667 | 0.10861 | 0.89139 | 6000 | 2 | 28 | 1 | 0.88235 | 54.5 | 0.3 | 0.3 | -0.00011521 | 0.90092 | 36 | 0.037764 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.026571 | 0.17213 | 0.016809 | 0.0082711 | 0.002276 | 0.015742 |  | 0.83333 | 0.91156 | 0.9037 | 0.89041 |  |  |  | 8.3333 | 223.3333 | 203.3333 | 216.6667 | 0 | 0 |  | 0.93891 | 1.1489 | 1.0945 | 1.1336 | 0 | 0 | FULL_OUTAGE
58256 | Los Alamos PV Site | NM | PNM | Los Alamos County - (NM) | Los Alamos County - (NM) |  |  | TRUE | pv_same_plant | NAB | CS | Ramping / Spinning Reserve, Backup Power | 1.8 | 8.3 | 4.6111 | >4.5h | 2012 |  |  | HYBRID_ARTEFACT |  | 0.32094 |  |  |  |  | insufficient_history |  | insufficient_history | 199.5984 | 0.033266 | 0.96673 | 6000 | 0 | 0 | 1 | 0.30584 | 0 | 1.8 | 1.8 | [8 empty] | 0.26681 | 0.050409 | 0.070199 | 0.14373 | 0.025862 | 0.0043103 | 0.0063012 | 0.012931 | RTE_2019: 0.24454; RTE_2020: 0.021053; RTE_2021: 0; RTE_2022: 0; EFC_2019: 26.988; EFC_2020: 1.6867; EFC_2021: 0; EFC_2022: 0; UTI_2019: 0.39713; UTI_2020: 0; UTI_2021: 0; UTI_2022: 0
58383 | Hyder II Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 14 | 42 | 3 | 2.5-4.5h | 2023 | 113 | C | HYBRID_ARTEFACT | 0.997 | 0.82856 | 1.9181 | 0.033621 | -1.2734 | -8.9529 | ok | 0.37253 | ok | 554.5476 | 0.092425 | 0.90758 | 6000 | 8 | 4 | 1 | 0.83671 | 487.5 | 14 | 14 | 0.26853 | 0.8296 | 24 | 0.50632 | 7.4532 | 173.0377 | 0.51243 | 0.13 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.8235; RTE_2025: 0.83542; EFC_2024: 268.8333; EFC_2025: 285.7143; UTI_2024: 1.0547; UTI_2025: 0.87937 | ELEVATED_P_AUX
58405 | ESS Battery Microgrid | AK |  | Kodiak Electric Assn Inc | Kodiak Electric Assn Inc |  |  | TRUE | colocated_firming | LIB | CS | Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, Transmission and Distribution Deferral, System Peak Shaving, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 3 | 3 | 1 | <1.5h | 2012 |  |  | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 16.2222 | 0.0027037 | 0.9973 | 6000 | 0 | 0 | 1 | 0.086957 | 0 | 3 | 3 |  |  |  |  | 0.51574 | 0.021696 | 0.0072957 | 0.0076118 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 | 0.016393 | 0.0041494 | 0.01992 | 0.0042017 | 0.0181 | 0.013953 | 0.025532 | 1.3333 | 0.33333 | 1.6667 | 0.33333 | 1.3333 | 1 | 2 | 0.00097096 | 0.00020923 | 0.0013852 | 0.00040479 | 0 | 0 | 0.0053055
58462 | McCoy Solar Energy Project Hybrid | CA | CISO | McCoy Solar, LLC | McCoy Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 230 | 920 | 4 | 2.5-4.5h | 2021 | 8 | C | HYBRID_ARTEFACT | 0.92817 | 0.85634 | 0.26756 | 0.35653 | -2.6035 | -151.5059 | ok | 0.2499 | ok | 1076.6065 | 0.17943 | 0.82057 | 6000 | 9 | 4 | 1 | 0.74061 | 12543.5 | 230 | 230 | 0.6154 | 0.90768 | 33 | 0.09387 | 11914.3521 | 1737.5235 | 731.2206 | 727.3445 | 0.080762 | 0.20113 | 0.069817 | 0.25527 | 0.0070175 | 0.018713 | 0.0062643 | 0.024561 |  |  | 0.89428 | 0.89593 | 0.59158 | 0.91542 | 0.83164 |  |  | 151.8533 | 259.5457 | 132.5391 | 256.3228 | 276.3457 |  |  | 1.327 | 1.0001 | 0.44127 | 0.94502 | 1.0451 | PARTIAL_AVAILABILITY
58475 | Battery Utility of Ohio | OH | PJM | Battery Utility of Ohio LLC | Battery Utility of Ohio LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 4 | 2 | 0.5 | <1.5h | 2014 |  |  | HEALTHY | [7 empty] | 0.06605 | ok | 19369.25 | 3.2282 | 0 | 6000 | 0 | 0 | 1 | 0.87371 | 0 | 4 | 4 | [16 empty] | RTE_2019: 0.87308; RTE_2020: 0.8693; RTE_2021: 0.85988; RTE_2022: 0.22222; EFC_2019: 2782.5; EFC_2020: 2238; EFC_2021: 899; EFC_2022: 1; UTI_2019: 1.507; UTI_2020: 1.2338; UTI_2021: 0.48902; UTI_2022: 0
58537 | OCI Alamo Solar I Hybrid | TX | ERCO | OCI Energy LLC | OCI Energy LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Frequency Regulation | 1 | 0.3 | 0.3 | <1.5h | 2016 |  |  | HEALTHY | [7 empty] | 0.072754 | ok | 8981.9444 | 1.497 | 0 | 6000 | 5 | 0 | 1 | 0.62195 | 0 | 1 | 1 | [16 empty] | RTE_2019: 0.59633; RTE_2020: 0.62462; RTE_2021: 0.6199; RTE_2022: 1.9833; EFC_2019: 1516.6667; EFC_2020: 1386.6667; EFC_2021: 1620; EFC_2022: 793.3333; UTI_2019: 1.2256; UTI_2020: 0.88548; UTI_2021: 2.4549; UTI_2022: 1.9082
58579 | Laverne Battery | MN | MISO | Northern States Power Co - Minnesota | Northern States Power Co - Minnesota |  |  | FALSE |  | NAB | CS | Transmission and Distribution Deferral | 1.1 | 7.6 | 6.9091 | >4.5h | 2013 |  |  | HEALTHY | [8 empty] | insufficient_history | 954.2105 | 0.15904 | 0.84096 | 6000 | 1 | 0 | 1 | 0.65944 | 0 | 1 | 1 | [16 empty] | RTE_2019: 0.66114; EFC_2019: 136.3158; EFC_2020: 0; UTI_2019: 2.0095; UTI_2020: 0
58585 | Sierra Nevada Brewing Co Hybrid | CA | CISO | Sierra Nevada Brewing Co | Sierra Nevada Brewing Co |  |  | TRUE | pv_same_plant | LIB | CS |  | 0.5 | 1 | 2 | 1.5-2.5h | 2017 | 307 | C | HYBRID_ARTEFACT | 0.80218 | 0.68438 | 0.071934 | 5.0736e-05 | 1.8298 | -7.1028 | ok | -1.2627 | ok | 919.6667 | 0.15328 | 0.84672 | 6000 | 0 | 4 | 1 | 0.81818 | 9.5645 | 0.5 | 0.5 | 0.00035967 | 0.78238 | 29 | 0.050417 | 3.9406 | 0.13469 | 0.0010092 | 0.034367 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | 0.82474 | 0.73611 | 0.82308 | 0.78698 | 0.78862 | 0.77551 | 0.38462 | 160 | 53 | 107 | 133 | 97 | 38 | 25 | 2.6523 | 0.8 | 0.47946 | 0.4935 | 0.38069 | 0.1055 | 0.069645 | LOW_ETA_AND_LOW_UTI
58625 | Santa Rita Jail Hybrid | CA | CISO | Fuel Cell Energy | County of Alameda GSA - (CA) |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving | 2 | 4 | 2 | 1.5-2.5h | 2012 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.3 | 0.3
58639 | KRS I Anahola Solar Hybrid | HI |  | Kauai Island Utility Cooperative | Kauai Island Utility Cooperative |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, Backup Power, Excess Wind and Solar Generation | 6 | 4.6 | 0.76667 | <1.5h | 2015 |  |  | HYBRID_ARTEFACT |  | 0.10738 |  |  |  |  | insufficient_history |  | insufficient_history | 92.3007 | 0.015383 | 0.98462 | 6000 | 0 | 0 | 3 | 0.45283 | 0 | 2 | 6 | [8 empty] | 0.15519 | 0.12167 | 0.032383 | 0.13299 | 0.014054 | 0.010811 | 0.0027908 | 0.011892 | RTE_2019: 0.19213; RTE_2020: 0.056604; RTE_2021: 0.025078; RTE_2022: 0.08011; EFC_2019: 18.0435; EFC_2020: 4.5652; EFC_2021: 1.7391; EFC_2022: 6.3043; UTI_2019: 0.0038354; UTI_2020: 0.0016325; UTI_2021: 0.00092468; UTI_2022: 0.0065176
58640 | KRS II Koloa Solar | HI |  | Kauai Island Utility Cooperative | Kauai Island Utility Cooperative |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
58899 | Prosperity Energy Storage Facility Hybri | NM | PNM | Public Service Co of NM | Public Service Co of NM |  |  | TRUE | pv_same_plant | PBB | CS | Arbitrage, Load Management, Excess Wind and Solar Generation | 0.8 | 1.3 | 1.625 | 1.5-2.5h | 2011 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
59020 | Gila Bend Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 32 | 96 | 3 | 2.5-4.5h | 2023 | 192 | C | HYBRID_ARTEFACT | 0.84217 | 0.81792 | 0.22654 | 0.077527 | -9.445 | -101.7834 | ok | -0.73223 | ok | 528.6562 | 0.088109 | 0.91189 | 6000 | 7 | 3 | 1 | 0.83107 | 112 | 32 | 32 | 0.072494 | 0.82534 | 24 | 0.90464 | 17.1339 | 397.7908 | 1.178 | 0.29885 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.81885; RTE_2025: 0.83176; EFC_2024: 260.7083; EFC_2025: 267.9479; UTI_2024: 0.98376; UTI_2025: 0.84181 | PARTIAL_AVAILABILITY
59118 | Cameron Wind 1 LLC | TX | ERCO | Cameron Wind 1 LLC | Cameron Wind 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 16.4 | 32.8 | 2 | 1.5-2.5h | 2024 | 134 | A | THERMAL_AUX | 0.76003 | 0.74328 | 0.054612 | -0.07869 | 1.1641 | 93.8256 | ok | -25.3178 | ok | 384.4817 | 0.06408 | 0.93592 | 6000 | 3 | 2 | 1 | 0.84697 | 346.5 | 16.4 | 16.4 | 0.0089563 | 0.76615 | 23 | 0.031708 | 76.244 | 16.6785 | 93.7724 | 37.2362 | 0.022471 | 0.086899 | 0.28752 | 0.47079 | 0.0018939 | 0.0075758 | 0.03388 | 0.05303 | RTE_2024: 0.82054; RTE_2025: 0.71619; EFC_2024: 189.2988; EFC_2025: 195.1829; UTI_2024: 0.87276; UTI_2025: 0.6703 | THERMAL_AUX
59150 | RE Mustang LLC | CA | CISO | RE Mustang LLC | MN8 Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 75 | 75 | 1 | <1.5h | 2021 | 453 | C | HYBRID_ARTEFACT | 0.85916 | 0.85774 | 0.022994 | 0.072541 | -1.3948 | -110.47 | ok | 0.014815 | ok | 4669.44 | 0.77824 | 0.22176 | 6000 | 1 | 2 | 1 | 0.88539 | 5801.8815 | 75 | 75 | 0.017245 | 0.85927 | 36 | 0.01008 | 16234.0999 | 369.9206 | 3.7205 | 23.5966 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  |  | 0.85701 | 0.85923 | 0.85051 | 0.86489 | 0.86096 |  |  | 184.12 | 1279.1067 | 944.5867 | 1166.8933 | 1094.7333 |  |  | 1.0619 | 1.4712 | 1.329 | 1.3361 | 1.3159 | PARTIAL_AVAILABILITY
59256 | Vaca Dixon Battery Storage System | CA | CISO | Pacific Gas & Electric Co. | Pacific Gas & Electric Co. |  |  | FALSE |  | NAB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 2 | 14 | 7 | >4.5h | 2013 | 339 | A | UNATTRIBUTED | 0.77365 | 0.29941 | 3.39 |  |  |  | ok |  | insufficient_history | 94.6429 | 0.015774 | 0.98423 | 6000 | 0 | 3 | 1 | 0.48864 | 1746.1275 | 2 | 2 | 0.067801 | 0.47364 | 10 | 0.47985 |  |  |  |  | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2019: 0.12796; RTE_2020: 0.22449; RTE_2021: 0.46843; EFC_2019: 7.7143; EFC_2020: 14.1429; EFC_2021: 26.5; UTI_2019: 0.012184; UTI_2020: 0.0075381; UTI_2021: 0.40443 | LOW_ETA_AND_LOW_UTI
59257 | Yerba Buena | CA | CISO | Pacific Gas & Electric Co. | Pacific Gas & Electric Co. |  |  | FALSE |  | NAB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, Backup Power | 4 | 28 | 7 | >4.5h | 2013 | 394 | A | UNATTRIBUTED | 0.65786 | 0.35477 | 4.3079 | -0.02542 |  |  | insufficient_history | 0.36089 | ok | 564.494 | 0.094082 | 0.90592 | 6000 | 0 | 0 | 1 | 0.60517 | 5673.0361 | 4 | 4 | 0.17232 | 0.46577 | 15 | 0.51999 |  |  |  |  | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2019: 0.44791; RTE_2020: 0.20175; RTE_2021: 0.060942; EFC_2019: 87.8214; EFC_2020: 20.5714; EFC_2021: 2.3571; UTI_2019: 1.3062; UTI_2020: 0.0012872; UTI_2021: 0 | LOW_ETA_AND_LOW_UTI
59296 | Northwest Ohio Wind | OH | PJM | NorthStar Clean Energy | Northwest Ohio Wind, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_tight | LIB | CS | Arbitrage, Co-Located Renewable Firming, System Peak Shaving, Load Management | 0.8 | 3.4 | 4.25 | 2.5-4.5h | 2021 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.2 | 0.2
59444 | Desert Star Hybrid | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Load Following, Excess Wind and Solar Generation | 10 | 30 | 3 | 2.5-4.5h | 2023 | 148 | C | HYBRID_ARTEFACT | 0.931 | 0.82667 | 1.4655 | 0.032981 | -7.3092 | -72.0418 | ok | 0.23013 | ok | 634.8 | 0.1058 | 0.8942 | 6000 | 7 | 5 | 1 | 0.83254 | 264 | 10 | 10 | 0.14655 | 0.82692 | 24 | 0.27725 | 6.1688 | 143.2183 | 0.42412 | 0.1076 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.82338; RTE_2025: 0.83021; EFC_2024: 304.2667; EFC_2025: 330.5333; UTI_2024: 1.2181; UTI_2025: 0.96794 | ELEVATED_P_AUX
59661 | Tehachapi Energy Storage Project | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | BL | Ramping / Spinning Reserve | 8 | 32 | 4 | 2.5-4.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 8 | 8
59772 | KCP&L SmartGrid Innovation Park | MO | SWPP | Evergy Metro | Evergy Metro |  |  | FALSE |  | LIB | CS |  | 1 | 1 | 1 | <1.5h | 2012 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
59871 | Desert Quartzite | CA | CISO | Desert Quartzite LLC | Desert Quartzite LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 150 | 150 | 1 | <1.5h | 2024 | 421 | C | HYBRID_ARTEFACT | 0.98194 | 0.86352 | 1.3751 | 0.60681 |  |  | insufficient_history |  | insufficient_history | 993.4467 | 0.16557 | 0.83443 | 6000 | 1 | 0 | 1 | 0.92889 | 0 | 150 | 150 | 2.0627 | 0.87088 | 13 | 0.44509 | 14710.5796 | 402.2456 | 6.3212 | 705.6091 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.8976; RTE_2025: 0.8692; EFC_2024: 60.7133; EFC_2025: 932.7333; UTI_2024: 1.2094; UTI_2025: 1.3145 | ELEVATED_P_AUX
59939 | RE Tranquillity | CA | CISO | SP Tranquillity Solar Storage, LLC | Southern Power Co |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Load Management, Excess Wind and Solar Generation | 72 | 288 | 4 | 2.5-4.5h | 2021.4861 | 415 | C | HYBRID_ARTEFACT | 0.93866 | 0.86019 | 0.89687 | 0.0074883 | -0.36223 | -9.4639 | ok | -0.60826 | ok | 884.4358 | 0.14741 | 0.85259 | 6000 | 0 | 4 | 1 | 0.87352 | 3060.4675 | 67 | 67 | 0.64574 | 0.86625 | 36 | 0.74565 | 3181.1951 | 463.928 | 195.2398 | 194.2048 | 0.080762 | 0.20113 | 0.069817 | 0.25527 | 0.0070175 | 0.018713 | 0.0062643 | 0.024561 |  |  | 0.84336 | 0.84686 | 0.84191 | 0.86744 | 0.88087 |  |  | 22.6719 | 195.3715 | 162.8576 | 239.5243 | 264.0104 |  |  | 0.42885 | 0.75281 | 0.49538 | 0.9183 | 0.88384 | PARTIAL_AVAILABILITY
59949 | AES Warrior Run Energy Storage Project | MD | PJM | AES Tait LLC | AES Tait LLC |  |  | FALSE |  | LIB | BL |  | 11 | 5 | 0.45455 | <1.5h | 2015 | 130 | A | UNATTRIBUTED | 0.83581 | 0.80291 | 0.38435 | 0.042415 | 0.72608 | 16.9949 | ok | 0.074673 | ok | 14649.0167 | 2.4415 | 0 | 6000 | 0 | 2 | 1 | 0.8092 | 763.5728 | 5 | 5 | 0.042279 | 0.80945 | 64 | 0.54889 |  |  |  |  | 0.10809 | 0.12644 | 0.018123 | 0.12644 | 0.0095321 | 0.011265 | 0.0015387 | 0.011265 | 0.81523 | 0.8232 | 0.80997 | 0.81583 | 0.78579 | 0.63978 |  | 1800.2 | 1788 | 1813.2 | 2104.2 | 1358 | 234.8 |  | 0.96304 | 0.91094 | 1.0582 | 1.0081 | 0.74955 | 0 |  | LOW_ETA_AND_LOW_UTI
59957 | Grand Ridge Battery Projects | IL | PJM | Invenergy Services LLC | Invenergy Services LLC |  |  | TRUE | rte_gt_1,dc_coupled | LIB | CT | Arbitrage, Frequency Regulation, Excess Wind and Solar Generation | 36 | 13.5 | 0.375 | <1.5h | 2014.75 |  |  | HYBRID_ARTEFACT | 0.42024 | 0.21619 | -0.3972 | -0.31652 |  |  | ok | -0.38631 | ok | 1681.4259 | 0.28024 | 0.71976 | 6000 | 0 | 0 | 1 | 0.8594 | 0 | 33 | 33 | -0.14299 | 0.51229 | 18 | 0.0065877 | 0 | 0 | 0 | 0 | 0.10809 | 0.12644 | 0.017732 | 0.12644 | 0.0095321 | 0.011265 | 0.0015049 | 0.011265 | 0.23498 | 0.34311 | 0.25674 | 0.74194 | 0.14923 | 0.31836 | 0.0076149 | 81.1111 | 514 | 172.7407 | 282.8148 | 95.1111 | 121.2593 | 2.0741 | 0.034568 | 0.27757 | 0.0092431 | 0.013096 | 0.070091 | 0.027443 | 0
59959 | Elwood Energy Storage Center | IL | PJM | West Chicago Battery Storage LLC | West Chicago Battery Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 19.8 | 7.9 | 0.39899 | <1.5h | 2015 | 459 | A | UNATTRIBUTED | 0.80433 | 0.67531 | 0.38147 | 0.034888 | -5.855 | -29.1572 | ok | 1.3141 | ok | 7017.8165 | 1.1696 | 0 | 6000 | 0 | 2 | 1 | 0.81547 | 1558.627 | 19.8 | 19.8 | 0.075531 | 0.74801 | 34 | 0.93856 |  |  |  |  | 0.10809 | 0.12644 | 0.019211 | 0.12644 | 0.0095321 | 0.011265 | 0.0016329 | 0.011265 | RTE_2019: 0.78773; RTE_2020: 0.70802; RTE_2021: 0.54094; EFC_2019: 1510.2532; EFC_2020: 469.6203; EFC_2021: 129.6203; UTI_2019: 0.75354; UTI_2020: 0.2421; UTI_2021: 0.098059 | LOW_ETA_AND_LOW_UTI
59960 | Jake Energy Storage Center | IL | PJM | Joliet Battery Storage LLC | Joliet Battery Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 19.8 | 7.9 | 0.39899 | <1.5h | 2015 | 451 | A | THERMAL_AUX | 0.82503 | 0.52155 | 0.3743 | 0.015643 | 14.6823 | 115.4076 | ok | 3.4515 | ok | 3658.9451 | 0.60982 | 0.39018 | 6000 | 0 | 0 | 1 | 0.78937 | 731.3852 | 19.8 | 19.8 | 0.074112 | 0.71521 | 24 | 0.96759 |  |  |  |  | 0.10809 | 0.12644 | 0.038686 | 0.12644 | 0.0095321 | 0.011265 | 0.0033563 | 0.011265 | RTE_2019: 0.75304; RTE_2020: 0.53988; RTE_2021: 0.12798; EFC_2019: 814.0506; EFC_2020: 125.9494; EFC_2021: 5.443; UTI_2019: 0.44011; UTI_2020: 0.056554; UTI_2021: 0.0049735 | THERMAL_AUX
59966 | Camp Lejeune Solar and Energy Storage | NC | DUK | Duke Energy Progress - (NC) | Duke Energy Progress - (NC) |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, System Peak Shaving, Backup Power, Excess Wind and Solar Generation | 11 | 11 | 1 | <1.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 11 | 11
59993 | Babcock Solar Energy Center Hybrid | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Load Management, Excess Wind and Solar Generation | 10 | 40 | 4 | 2.5-4.5h | 2018 | 406 | C | HYBRID_ARTEFACT | 0.73129 | 0.61317 | 0.29433 | 0.014077 | -0.99052 | 23.349 | ok | 3.9563 | ok | 745.1 | 0.12418 | 0.87582 | 6000 | 0 | 10 | 1 | 0.99521 | 1310 | 10 | 10 | 0.029433 | 0.74345 | 65 | 0.28188 | 3.9755 | 1.4132 | 0.20031 | 0.0016642 | 0.048771 | 0.27747 | 0.035322 | 0.0011993 | 0.0041667 | 0.027083 | 0.0030536 | 0.0001 | 0.76273 | 0.77042 | 0.78676 | 0.74232 | 0.53677 | 0.51568 | 0.37708 | 123.6 | 150.425 | 130.15 | 119.625 | 75.55 | 33.7 | 9.05 | 0.70255 | 0.97766 | 0.65764 | 0.50584 | 0.18049 | 0.055667 | 0.013573 | LOW_ETA_AND_LOW_UTI
59995 | AEP Milton NaS | WV | PJM | Appalachian Power Co | Appalachian Power Co |  |  | FALSE |  | NAB | CS | Load Management | 2 | 2 | 1 | <1.5h | 2009 |  |  | HEALTHY | [7 empty] | 3.202 | ok | 1403.3333 | 0.23389 | 0.76611 | 6000 | 0 | 0 | 1 | 0.6794 | 0 | 2 | 2 | [16 empty] | RTE_2019: 0.69129; RTE_2020: 0.41092; EFC_2019: 131; EFC_2020: 71.5; UTI_2019: 0.066575; UTI_2020: 0.036402
60014 | Manatee Solar Energy Center | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Excess Wind and Solar Generation | 409 | 900 | 2.2005 | 1.5-2.5h | 2021 | 359 | C | HYBRID_ARTEFACT | 0.81905 | 0.60418 | 0.41217 | 0.80235 | 8.1847 | -30.3607 | ok | -1.6404 | ok | 192.9989 | 0.032166 | 0.96783 | 6000 | 0 | 4 | 5.4899 | 0.92765 | 3009.5 | 74.5 | 409 | 1.6858 | 0.68416 | 43 | 0.47491 | 10635.6592 | 678.5826 | 3.2906 | 61.8365 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 | RTE_2022: 0.5558; RTE_2023: 0.3839; RTE_2024: 0.70528; RTE_2025: 0.85071; EFC_2022: 44.8511; EFC_2023: 20.9244; EFC_2024: 46.8289; EFC_2025: 80.3944; UTI_2022: 0.20065; UTI_2023: 0.090742; UTI_2024: 0.18002; UTI_2025: 0.32888 | LOW_ETA_AND_LOW_UTI
60016 | MESA 1 | WA | BPAT | PUD No 1 of Snohomish County - (WA) | PUD No 1 of Snohomish County - (WA) |  |  | FALSE |  | LIB | CS | Arbitrage, Load Management | 2 | 1 | 0.5 | <1.5h | 2015.5 | 429 | B | FULL_OUTAGE |  | 0.69408 |  |  |  |  | insufficient_history |  | insufficient_history | 1081 | 0.18017 | 0.81983 | 6000 | 0 | 61 | 1 | 0.84146 | 835.565 | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.15519 | 0.12167 | 0.030178 | 0.13299 | 0.014054 | 0.010811 | 0.0025947 | 0.011892 | 0.78689 |  |  | 0 |  | 0.2 | 0 | 240 | 0 | 0 | 0 | 0 | 1 | 0 | 0.0076034 | 0 | 0 | 0 | 0 | 0 | 0 | FULL_OUTAGE
60021 | MESA 2 | WA | BPAT | PUD 1 of Snohomish County | PUD 1 of Snohomish County |  |  | FALSE |  | FLB | CS | Arbitrage, System Peak Shaving, Load Management | 2.4 | 8 | 3.3333 | 2.5-4.5h | 2017 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 0 | 1 | 0 | 0 | 2.2 | 2.2 | [16 empty] | RTE_2019: 0; RTE_2020: 0; EFC_2019: 0; EFC_2020: 0; UTI_2019: 0; UTI_2020: 0
60061 | Citrus Solar Energy Center Hybrid | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_tight | LIB | CS | Excess Wind and Solar Generation | 4 | 16 | 4 | 2.5-4.5h | 2018 | 241 | C | HYBRID_ARTEFACT | 0.8843 | 0.88461 | -0.020692 | -0.0019119 | -2.9521 | 19.0703 | ok | 0.08307 | ok | 725.7083 | 0.12095 | 0.87905 | 6000 | 0 | 4 | 1 | 0.77743 | 47 | 4 | 4 | -0.00082767 | 0.9106 | 82 | 0.0068744 | 33.792 | 12.0121 | 1.7027 | 0.014146 | 0.048771 | 0.27747 | 0.035322 | 0.0011993 | 0.0041667 | 0.027083 | 0.0030536 | 0.0001 | 0.89331 | 1.1352 | 0.93291 | 0.86943 | 0.76015 | 0.79551 | 0.88102 | 106.75 | 127 | 111.25 | 51.1875 | 78.4375 | 79.75 | 82.375 | 0.42689 | 0.73454 | 0.56684 | 0.20568 | 0.33919 | 0.30025 | 0.28593 | PARTIAL_AVAILABILITY
60092 | Blythe Solar II, LLC | CA | CISO | Blythe Solar II, LLC | Blythe Solar II, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 115 | 538.6 | 4.6835 | >4.5h | 2021 | 417 | C | HYBRID_ARTEFACT | 0.94801 | 0.88554 | 0.69854 | -0.31462 | 0.14097 | -23.8238 | ok | -0.088513 | ok | 915.8522 | 0.15264 | 0.84736 | 6000 | 9 | 2 | 1 | 0.9124 | 2557 | 115 | 115 | 0.80332 | 0.88979 | 57 | 0.26225 | 88.5026 | 545.8674 | 6.0848 | 174.0994 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 |  |  | 0.86738 | 0.87832 | 0.86394 | 0.91862 | 0.90546 |  |  | 136.3275 | 202.9428 | 136.1753 | 186.5058 | 253.9009 |  |  | 1.6207 | 1.4505 | 3.9987 | 2.037 | 2.101 | PARTIAL_AVAILABILITY
60093 | Blythe Solar 110, LLC | CA | CISO | Blythe Solar 110, LLC | Blythe Solar 110, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 63 | 301.2 | 4.781 | >4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.92316 | 0.88768 | 0.59879 | 0.040002 | 3.2831 | 79.3429 | ok | 0.18399 | ok | 1396.4475 | 0.23274 | 0.76726 | 6000 | 9 | 0 | 1 | 0.86742 | 0 | 63 | 63 | 0.37724 | 0.8883 | 36 | 0.15111 | 51.5375 | 317.8738 | 3.5434 | 101.3829 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 |  |  | 0.8674 | 0.84752 | 0.88186 | 0.8895 | 0.89268 |  |  | 243.7815 | 375.747 | 229.6846 | 283.5458 | 263.6886 |  |  | 3.4111 | 2.6503 | 4.6062 | 2.7133 | 2.2281
60094 | Blythe Solar III, LLC Hybrid | CA | CISO | Blythe Solar III, LLC | Blythe Solar III, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 115 | 538.6 | 4.6835 | >4.5h | 2021 | 85 | C | HYBRID_ARTEFACT | 0.9293 | 0.87691 | 0.61831 | -0.2106 | -1.3007 | -79.1371 | ok | -0.0064917 | ok | 835.6387 | 0.13927 | 0.86073 | 6000 | 7 | 2 | 1 | 0.81859 | 1104 | 115 | 115 | 0.71105 | 0.88207 | 51 | 0.21175 | 87.5154 | 539.7788 | 6.017 | 172.1575 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 |  |  | 0.89138 | 0.86484 | 0.84808 | 0.90236 | 0.89959 |  |  | 54.4541 | 210.635 | 134.9313 | 184.3966 | 251.2217 |  |  | 1.6407 | 1.5563 | 3.0826 | 2.1206 | 2.0718 | PARTIAL_AVAILABILITY
60095 | Blythe Solar IV, LLC | CA | CISO | Blythe Solar IV, LLC | Blythe Solar IV, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 47 | 47 | 1 | <1.5h | 2022 | 448 | C | HYBRID_ARTEFACT | 0.83788 | 0.82004 | 0.056537 | -0.038351 | -3.1368 | -142.6497 | ok | -0.069277 | ok | 2644.2181 | 0.4407 | 0.5593 | 6000 | 5 | 0 | 2.7857 | 0.84533 | 0 | 4.2 | 11.7 | 0.026572 | 0.84086 | 35 | 0.058027 | 3699.2578 | 303.4572 | 103.2078 | 16.1308 | 0.13809 | 0.19981 | 0.056808 | 0.03647 | 0.012384 | 0.018576 | 0.0050253 | 0.003096 | RTE_2023: 0.80928; RTE_2024: 0.83673; RTE_2025: 0.8598; EFC_2023: 663.9362; EFC_2024: 927.9149; EFC_2025: 886.383; UTI_2023: 0.95038; UTI_2024: 1.1345; UTI_2025: 1.3649 | LOW_ETA_AND_LOW_UTI
60123 | Castle Gap Solar Hybrid | TX | ERCO | Upton County Solar 2 LLC | Upton County Solar 2 LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 9.9 | 42 | 4.2424 | 2.5-4.5h | 2019 | 106 | C | HYBRID_ARTEFACT | 0.57006 | 0.63054 | -0.69187 | -0.15333 | 6.1909 | -68.0358 | ok | 0.77169 | ok | 1010.1429 | 0.16836 | 0.83164 | 6000 | 6 | 7 | 1 | 0.43272 | 786.5 | 9.9 | 9.9 | -0.068495 | 0.56768 | 61 | 0.038134 | 6.2197 | 2.1164 | 0.69119 | 0.54242 | 0.033884 | 0.19305 | 0.052721 | 0.15832 | 0.0028726 | 0.017874 | 0.0046432 | 0.014363 | 0.44131 | 0.40703 | 0.38058 | 0.49738 | 0.89033 | 0.8798 | 0.80416 | 59.881 | 232.1429 | 202.0238 | 173.9762 | 182.8571 | 129.8333 | 29.4286 | 1.3226 | 1.5837 | 0.98714 | 0.71987 | 0.6415 | 0.50728 | 0.028574 | LOW_ETA_AND_LOW_UTI
60213 | NA 1(Hagerstown) | MD | PJM | Innolith Snook LLC | Innolith Snook LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 2 | 1 | 0.5 | <1.5h | 2017 |  |  | HEALTHY | [7 empty] | 0.024577 | ok | 4686.25 | 0.78104 | 0.21896 | 6000 | 0 | 0 | 1 | 0.79956 | 0 | 2 | 2 | [16 empty] | RTE_2019: 0.83919; RTE_2020: 0.8; EFC_2019: 1195; EFC_2020: 1400; UTI_2019: 0.60398; UTI_2020: 4.7211
60231 | Genentech-Oceanside Hybrid | CA | CISO | Tesla Inc. | Tesla Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Backup Power | 2 | 2 | 1 | <1.5h | 2016 | 74 | C | HYBRID_ARTEFACT | 0.80088 | 0.76576 | 0.14391 | -0.00082586 | -0.63472 | 96.1605 | ok | 0.36219 | ok | 4822.5 | 0.80375 | 0.19625 | 6000 | 0 | 6 | 1 | 0.80093 | 1712 | 1 | 1 | 0.0028783 | 0.79826 | 28 | 0.81549 | 25.3084 | 1.1765 | 0.24222 | 0.94908 | 0.15254 | 0.13124 | 0.022511 | 0.29943 | 0.013793 | 0.011724 | 0.00192 | 0.029655 |  |  | 0.80136 | 0.81934 | 0.80086 | 0.79377 | 0.72414 |  |  | 411.5 | 644 | 3539 | 102 | 126 |  |  | 0.59185 | 0.7407 | 5.2923 | 0.019231 | 0.21045 | LOW_ETA_AND_LOW_UTI
60233 | RE Garland | CA | CISO | SP Garland Solar Storage, LLC | Southern Power Co |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Load Management, Excess Wind and Solar Generation | 88 | 352 | 4 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.91388 | 0.86901 | 0.48296 | 0.15061 | -0.81304 | -18.1153 | ok | -0.27121 | ok | 934.108 | 0.15568 | 0.84432 | 6000 | 1 | 1 | 1 | 0.87652 | 751.104 | 87 | 87 | 0.425 | 0.87441 | 36 | 0.50699 | 4375.0768 | 638.0371 | 268.512 | 267.0886 | 0.080762 | 0.20113 | 0.069817 | 0.25527 | 0.0070175 | 0.018713 | 0.0062643 | 0.024561 |  |  | 0.82106 | 0.85296 | 0.86592 | 0.87219 | 0.88207 |  |  | 53.5369 | 230.6449 | 166.1705 | 229.2188 | 254.5369 |  |  | 0.55321 | 0.88872 | 0.53719 | 0.91141 | 0.93287
60249 | Silicon Valley Clean Water | CA | CISO | Silicon Valley Clean Water | Silicon Valley Clean Water |  |  | FALSE |  | LIB | CS |  | 1 | 2 | 2 | 1.5-2.5h | 2020 | 326 | B | FULL_OUTAGE | [8 empty] | insufficient_history | 16.5 | 0.00275 | 0.99725 | 6000 | 0 | 36 | 1 |  | 0 | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.095923 | 0.18264 | 0.092976 | 0.14038 | 0.0084034 | 0.016807 | 0.0085598 | 0.012605 | EFC_2020: 16.5; EFC_2021: 0; EFC_2022: 0; EFC_2023: 0; EFC_2024: 0; EFC_2025: 0; UTI_2020: 1.7928; UTI_2021: 0; UTI_2022: 0; UTI_2023: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
60297 | Clinton Battery | OH | PJM | Clinton Battery Utility, LLC | Clinton Battery Utility, LLC |  |  | FALSE |  | LIB | CS |  | 10 | 4.1 | 0.41 | <1.5h | 2016 | 105 | A | THERMAL_AUX | 0.82437 | 0.7252 | 0.33484 | 0.0020116 | -9.6279 | 20.2992 | ok | 0.15097 | ok | 10445 | 1.7408 | 0 | 6000 | 0 | 6 | 1 | 0.93544 | 806.6772 | 5 | 5 | 0.033484 | 0.72474 | 30 | 0.38171 | 52.8198 | 3.4138 | 1.2657 | 1.0888 | 0.10809 | 0.12644 | 0.038308 | 0.12644 | 0.0095321 | 0.011265 | 0.0033222 | 0.011265 | 0.93549 | 0.8328 | 0.35946 | 0.2336 | 0.8245 | 0.72673 | 0.55383 | 2175.122 | 1830.7317 | 351.2195 | 224.878 | 436.5854 | 358.0488 | 174.3902 | 1.143 | 0.92349 | 0.19925 | 0.11146 | 0.26437 | 0.18438 | 0.1099 | THERMAL_AUX
60299 | HMV Minster Energy Storage System | OH | PJM | Summit Ridge Energy | Summit Ridge Energy |  |  | TRUE | rte_gt_1 | LIB | CS | Load Management, Voltage or Reactive Power Support | 7 | 7 | 1 | <1.5h | 2016 | 460 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 13222.2619 | 2.2037 | 0 | 6000 | 0 | 24 | 1 | 0.99987 | 0 | 7 | 7 | [8 empty] | 0.10809 | 0.12644 | 0.019536 | 0.12644 | 0.0095321 | 0.011265 | 0.0016611 | 0.011265 | 1 | [6 empty] | 3449.2857 | 0 | 0 | 0 | 0 | 0 |  | 1.7684 | 0 | 0 | 0 | 0 | 0 |  | FULL_OUTAGE
60316 | Scott Solar Farm | VA | PJM | Dominion Energy Inc. | Dominion Energy Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Ramping / Spinning Reserve | 40 | 48 | 1.2 | <1.5h | 2022 | 346 | C | HYBRID_ARTEFACT | 0.81884 | 0.75453 | 0.044606 | 0.027636 | 1.0212 | 74.9105 | ok | -0.18595 | ok | 147.1458 | 0.024524 | 0.97548 | 6000 | 0 | 0 | 0.2 | 0.83489 | 0 | 10 | 2 | 0.017842 | 0.80109 | 21 | 0.38949 | 209.3099 | 22.8934 | 11.6861 | 0.039429 | 0.10516 | 0.19926 | 0.082624 | 0.0011993 | 0.0092593 | 0.018519 | 0.0075191 | 0.0001 | RTE_2024: 0.80472; RTE_2025: 0.77663; EFC_2024: 75.2917; EFC_2025: 71.8542; UTI_2024: 0.04155; UTI_2025: 0.035846 | LOW_ETA_AND_LOW_UTI
60390 | Beech Ridge Energy Storage | WV | PJM | Invenergy Services LLC | Invenergy Services LLC |  |  | TRUE | dc_coupled | LIB | CT | Frequency Regulation | 31.5 | 12.5 | 0.39683 | <1.5h | 2015 | 437 | C | HYBRID_ARTEFACT | 0.43691 | 0.28164 | -0.038976 | 0.1315 |  |  | ok | -0.55637 | ok | 1602.78 | 0.26713 | 0.73287 | 6000 | 0 | 2 | 1 | 0.37355 | 143 | 31.5 | 31.5 | -0.012277 | 0.42195 | 22 | 0.029484 | 0 | 0 | 0 | 0 | 0.10809 | 0.12644 | 0.017732 | 0.12644 | 0.0095321 | 0.011265 | 0.0015049 | 0.011265 | 0.12248 | 0.35144 | 0.32765 | 0.22691 | 0.13947 | 0.39748 | 0.080692 | 17.52 | 531.44 | 481.04 | 191.44 | 108.56 | 189.36 | 26.48 | 0.0061345 | 0.29704 | 0.27262 | 0.12759 | 0.061804 | 0.045853 | 0 | PARTIAL_AVAILABILITY
60441 | Salem Smart Power Center | OR | PGE | Portland General Electric Co | Portland General Electric Co |  |  | TRUE | colocated_firming,dc_coupled | LIB | BL | Co-Located Renewable Firming, System Peak Shaving, Load Management | 5 | 5 | 1 | <1.5h | 2013 | 391 | C | HYBRID_ARTEFACT |  | 0.13566 |  |  |  |  | insufficient_history | 0.06972 | ok | 527.4744 | 0.087912 | 0.91209 | 6000 | 0 | 2 | 1 | 0.2459 | 2.5 | 5 | 5 | [8 empty] | 0.15519 | 0.12167 | 0.030741 | 0.13299 | 0.014054 | 0.010811 | 0.0026447 | 0.011892 | 0.13889 | 0.11085 | 0.19006 | 0.13318 | 0.12208 | 0.019231 |  | 65.3846 | 36.9231 | 50 | 11.4 | 9.4 | 0.2 |  | 0.039878 | 0.022524 | 0.035347 | 0.013856 | 0.014934 | 0 |  | PARTIAL_AVAILABILITY
60444 | Glacier Battery Storage | WA | PSEI | Puget Sound Energy Inc | Puget Sound Energy Inc |  |  | FALSE |  | LIB | CT | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, System Peak Shaving | 2 | 4.4 | 2.2 | 1.5-2.5h | 2016 | 432 | B | CAPACITY_FADE | [7 empty] | -16.1989 | ok | 1154.6212 | 0.19244 | 0.80756 | 6000 | 0 | 12 | 1 | 0.85066 | 75.7064 | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.27826 | 0.093193 | 0.069605 | 0.0011993 | 0.027174 | 0.0081522 | 0.0062438 | 0.0001 | 0.85052 | 0.84615 | 0.43316 | 0.23118 | 0.11475 | 0.04 |  | 333.6364 | 12.5 | 18.4091 | 9.7727 | 1.5909 | 0.22727 | 0 |  | 0.16291 | 0.08156 | 0.04211 | 0.010826 | 0 | 0 | FULL_OUTAGE
60467 | Red Rock | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 41 | 164 | 4 | 2.5-4.5h | 2023 | 155 | C | HYBRID_ARTEFACT | 0.91854 | 0.82994 | 0.34998 | 0.018865 |  |  | insufficient_history |  | insufficient_history | 241.9858 | 0.040331 | 0.95967 | 6000 | 3 | 2 | 1 | 0.90044 | 219.5 | 41 | 41 | 0.14349 | 0.89235 | 12 | 0.23323 | 23.4899 | 545.3543 | 1.615 | 0.40972 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2024: 0.86257; RTE_2025: 0.89211; EFC_2024: 15.5; EFC_2025: 223.9024; UTI_2024: 0.33891; UTI_2025: 0.7374 | PARTIAL_AVAILABILITY
60491 | Springbok 3 Solar Farm Hybrid | CA | LDWP | 64KT 8me LLC | 64KT 8me LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CT | Frequency Regulation, Voltage or Reactive Power Support | 1.5 | 1.5 | 1 | <1.5h | 2019 | 332 | C | FULL_OUTAGE | 0.8607 | 0.88773 | -0.010078 |  |  |  | insufficient_history |  | insufficient_history | 78 | 0.013 | 0.987 | 6000 | 1 | 54 | 1 | 0.78378 | 13.5 | 1.5 | 1.5 | -0.00015117 | 0.86029 | 10 | 0.061439 | 0 | 0 | 0 | 0 | 0.15519 | 0.12167 | 0.030989 | 0.13299 | 0.014054 | 0.010811 | 0.0026668 | 0.011892 |  | 0.83544 | 0.89474 | [5 empty] | 44 | 34 | 0 | 0 | 0 | 0 |  | 0.079656 | 0.0032339 | 0 | 0 | 0 | 0 | FULL_OUTAGE
60506 | ETT Presidio NaS Battery | TX | ERCO | Electric Transmission Texas LLC | Electric Transmission Texas LLC |  |  | TRUE | rte_gt_1 | NAB | BL | Backup Power | 4 | 4 | 1 | <1.5h | 2010 |  |  | HYBRID_ARTEFACT | 0.86844 | 0.88427 | -0.012553 | -0.0005716 | 1.3123 | 65.6391 | ok | 2.2168 | ok | 820.7917 | 0.1368 | 0.8632 | 6000 | 0 | 3 | 1 | 0.85106 | 73 | 4 | 4 | -0.00050212 | 0.88391 | 45 | 0.067349 |  |  |  |  | 0.10997 | 0.16034 | 0.0011985 | 0.3725 | 0.0097087 | 0.014563 | 0.0001 | 0.038835 | RTE_2019: 0.89324; RTE_2020: 0.90345; RTE_2021: 0.86768; RTE_2022: 0.87603; EFC_2019: 62.75; EFC_2020: 65.5; EFC_2021: 85.25; EFC_2022: 53; UTI_2019: 0.048848; UTI_2020: 0.044344; UTI_2021: 0.10229; UTI_2022: 0.1318
60518 | Stafford Hill Solar Hybrid | VT | ISNE | Green Mountain Power Corp | Green Mountain Power Corp |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 2 | 3.4 | 1.7 | 1.5-2.5h | 2015 | 440 | C | FULL_OUTAGE | 1.1512 | 0.77354 | -0.099117 | 0.0679 |  |  | insufficient_history |  | insufficient_history | 1643.5294 | 0.27392 | 0.72608 | 6000 | 1 | 50 | 1 | 3.0567 | 0 | 2 | 2 | -0.0019823 | 2.4572 | 13 | 0.042055 | 0 | 0 | 0 | 0 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 5.7447 | 2.4569 | 3 |  |  |  |  | 79.4118 | 1298.5294 | 0.88235 | 0 | 0 | 0 | 0 | 1.3698 | 6.8087 | 0 | 0 | 0 | 0 | 0 | FULL_OUTAGE
60546 | KIUC Kapaia PV and BA Storage Project Hy | HI |  | Tesla Inc. | Tesla Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 13 | 52 | 4 | 2.5-4.5h | 2017 | 98 | C | HYBRID_ARTEFACT | 0.90671 | 0.88635 | 0.31736 | 0.0017141 | 0.73524 | 35.9652 | ok | 0.14435 | ok | 1379.6923 | 0.22995 | 0.77005 | 6000 | 0 | 8 | 1 | 0.89412 | 1352.4885 | 11 | 11 | 0.041256 | 0.88693 | 36 | 0.18104 | 351.8342 | 125.0671 | 20.9214 | 0.14728 | 0.048771 | 0.27747 | 0.041417 | 0.0011993 | 0.0041667 | 0.027083 | 0.0036037 | 0.0001 |  |  | 0.87118 | 0.88266 | 0.88684 | 0.88864 | 0.88529 |  |  | 235.5192 | 292.0769 | 307.4423 | 274.5385 | 270.1154 |  |  | 1.1718 | 1.1996 | 1.0034 | 1.0861 | 0.9235 | PARTIAL_AVAILABILITY
60561 | Cedartown Battery Energy Storage Project | GA | SOCO | Georgia Power Co | Georgia Power Co |  |  | TRUE | colocated_firming | LIB | CT | Co-Located Renewable Firming, Transmission and Distribution Deferral, System Peak Shaving, Load Management, Excess Wind and Solar Generation | 1 | 2 | 2 | 1.5-2.5h | 2015 |  |  | HEALTHY | [8 empty] | insufficient_history | 57.375 | 0.0095625 | 0.99044 | 6000 | 0 | 0 | 1 | 0.40833 | 0 | 1 | 1 | [16 empty] | RTE_2019: 0.38028; EFC_2019: 13.5; UTI_2019: 0.2303
60562 | GMP Solar - Panton Hybrid | VT | ISNE | GMP VT Solar LLC | Green Mountain Power Corp |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | OT | Frequency Regulation, Excess Wind and Solar Generation | 1 | 4 | 4 | 2.5-4.5h | 2018 | 280 | C | HYBRID_ARTEFACT | 1.6267 | 0.76864 | 2.326 | -0.0041133 | 5.6833 | 32.395 | ok | 0.21191 | ok | 1886.4167 | 0.3144 | 0.6856 | 6000 | 1 | 4 | 1 | 1.0018 | 55 | 1 | 1 | 0.02326 | 1.1752 | 71 | 0.041305 | 21.4663 | 1.7609 | 0.026492 | 0.0067208 | 0.064667 | 0.095415 | 0.0011985 | 0.0011993 | 0.005571 | 0.0083565 | 0.0001 | 0.0001 | 1.6911 | 0.55267 | 1.6221 | 1.7801 | 1.6424 | 1.5795 | 1 | 416 | 196.75 | 242.5 | 251 | 186 | 181.25 | 170.25 | 2.2269 | 1.3871 | 1.169 | 1.0285 | 0.74061 | 0.81054 | 0.84094 | PARTIAL_AVAILABILITY
60565 | Borrego Springs Energy Storage | CA | CISO | SDGE Batteries | SDGE Batteries |  |  | TRUE | rte_gt_1 | LIB | CS | System Peak Shaving, Backup Power | 1.5 | 4.5 | 3 | 2.5-4.5h | 2013.3333 | 239 | C | HYBRID_ARTEFACT | 0.60141 | 0.6442 | -0.060076 | 0.0015619 |  |  | ok | 2.408 | ok | 201.7407 | 0.033623 | 0.96638 | 6000 | 0 | 15 | 1 | 0.78261 | 93.748 | 1.5 | 1.5 | -0.00090114 | 0.625 | 21 | 0.53629 | 0 | 0 | 0 | 0 | 0.30696 | 0.095163 | 0.052234 | 0.23407 | 0.030556 | 0.0083333 | 0.0045979 | 0.022222 | 0.89474 | 0.87204 | 0.83226 | 1.2703 | 0.65414 | 0.6087 | 0.71429 | 7.5556 | 40.8889 | 28.6667 | 20.8889 | 19.3333 | 37.3333 | 1.1111 | 0.025806 | 0.21577 | 0.13017 | 0.087744 | 0.081327 | 0.14847 | 0 | LOW_ETA_AND_LOW_UTI
60566 | Pala Energy Storage Yard | CA | CISO | SDGE Batteries | SDGE Batteries |  |  | TRUE | rte_gt_1 | LIB | CS | System Peak Shaving | 1 | 2 | 2 | 1.5-2.5h | 2015 | 461 | C | HYBRID_ARTEFACT | 0.92925 | 0.87981 | 8.4451 | 0.024918 |  |  | insufficient_history |  | insufficient_history | 6635.119 | 1.1059 | 0 | 6000 | 0 | 0 | 1 | 0.89663 | 0 | 1 | 1 | 0.084451 | 0.88273 | 12 | 0.51019 | 2132.8698 | 72.9014 | 0.54624 | 18.601 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | RTE_2019: 0.83871; RTE_2025: 0.88273; EFC_2019: 7.4286; EFC_2020: 0; EFC_2021: 0; EFC_2022: 0; EFC_2025: 6582.5; UTI_2019: 0.12316; UTI_2020: 0; UTI_2021: 0; UTI_2022: 0; UTI_2025: 22.4109 | ELEVATED_P_AUX
60567 | Ortega Highway Energy Storage | CA | CISO | SDGE Batteries | SDGE Batteries |  |  | TRUE | rte_gt_1 | LIB | CS | System Peak Shaving | 2 | 6 | 3 | 2.5-4.5h | 2015 | 309 | C | FULL_OUTAGE |  | 0.63095 |  |  |  |  | insufficient_history |  | insufficient_history | 17.1111 | 0.0028519 | 0.99715 | 6000 | 0 | 27 | 1 | 0.093333 | 10.897 | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.30696 | 0.095163 | 0.052234 | 0.23407 | 0.030556 | 0.0083333 | 0.0045979 | 0.022222 | 0.57143 |  |  | 0.90323 | 0.11268 |  |  | 0.66667 | 0 | 0 | 4.6667 | 9.3333 | 0 | 0 | 0.038536 | 0 | 0 | 0.033603 | 0.027642 | 0 | 0 | FULL_OUTAGE
60568 | Canyon Crest Academy | CA | CISO | SDGE Batteries | SDGE Batteries |  |  | TRUE | rte_gt_1 | LIB | CS | System Peak Shaving | 1 | 3 | 3 | 2.5-4.5h | 2014 | 311 | C | FULL_OUTAGE |  | 0.73077 |  |  |  |  | insufficient_history | 1.7154 | ok | 464.8333 | 0.077472 | 0.92253 | 6000 | 0 | 27 | 1 | 0.8775 | 19.989 | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.30696 | 0.095163 | 0.052234 | 0.23407 | 0.030556 | 0.0083333 | 0.0045979 | 0.022222 | 0.81373 | 0.88664 | 0.87179 | 2.05 | 0.27273 |  | 1 | 55.3333 | 73 | 56.6667 | 41 | 2 | 0 | 1.6667 | 0.18894 | 0.38523 | 0.29302 | 0.29522 | 0 | 0 | 0 | FULL_OUTAGE
60569 | El Cajon Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Load Following, Ramping / Spinning Reserve | 7.5 | 30 | 4 | 2.5-4.5h | 2017 | 434 | B | UNDER_DISPATCH | 0.91281 | 0.85301 | 0.43692 | 0.00074168 | 0.66515 | 9.2678 | ok | 1.0731 | ok | 1356.0833 | 0.22601 | 0.77399 | 6000 | 0 | 3 | 1 | 0.86998 | 15866.371 | 7.5 | 7.5 | 0.032769 | 0.86193 | 83 | 0.63522 | 908.2553 | 13.5465 | 7.6404 | 11.5214 | 0.30696 | 0.095163 | 0.042899 | 0.23407 | 0.030556 | 0.0083333 | 0.0037386 | 0.022222 | 0.84782 | 0.86528 | 0.88114 | 0.84866 | 0.85876 | 0.84779 | 0.87787 | 171.4 | 149.4333 | 193.2333 | 126.7333 | 114.1 | 128.6667 | 144 | 0.83946 | 1.056 | 0.79549 | 0.44794 | 0.45029 | 0.46494 | 0.57632 | PARTIAL_AVAILABILITY
60570 | Escondido Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Load Following, Ramping / Spinning Reserve | 30 | 120 | 4 | 2.5-4.5h | 2017 | 87 | A | UNDER_DISPATCH | 0.90928 | 0.86094 | 0.36039 | -0.038497 | 1.301 | 18.9664 | ok | 1.4695 | ok | 1904.7097 | 0.31745 | 0.68255 | 6000 | 0 | 11 | 1 | 0.86233 | 57471.274 | 30 | 30 | 0.10812 | 0.87824 | 68 | 0.63637 | 0 | 0 | 0 | 0 | 0.30696 | 0.095163 | 0.042899 | 0.23407 | 0.030556 | 0.0083333 | 0.0037386 | 0.022222 | 0.87243 | 0.87975 | 0.88599 | 0.891 | 0.87789 | 0.80548 | 0 | 356.6417 | 227.2333 | 250.9333 | 245.0333 | 129.8917 | 41.1333 | 0 | 1.9039 | 1.8123 | 1.2678 | 1.0191 | 0.4335 | 0.14623 | 0 | FULL_OUTAGE
60607 | CMEEC - Polaris Park Solar Hybrid | CT | ISNE | Tesla Inc. | Tesla Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Backup Power | 0.8 | 3.3 | 4.125 | 2.5-4.5h | 2017 | 344 | C | HYBRID_ARTEFACT | 0.81112 | 0.56871 | 0.20366 | -0.00095492 |  |  | ok | 6.8544 | ok | 120.303 | 0.020051 | 0.97995 | 6000 | 0 | 0 | 1 | 0.92593 | 0 | 0.8 | 0.8 | 0.0016292 | 0.76296 | 21 | 0.033445 | 1.4311 | 0.11739 | 0.0017661 | 0.00044806 | 0.064667 | 0.095415 | 0.0011985 | 0.0011993 | 0.005571 | 0.0083565 | 0.0001 | 0.0001 |  |  | 0.68367 | 0.40782 | 0.35437 | 1 | 0.29936 |  |  | 20.303 | 22.1212 | 22.1212 | 41.5152 | 14.2424 |  |  | 0.10153 | 0.089392 | 0.073578 | 0.17326 | 0.057645 | LOW_ETA_AND_LOW_UTI
60609 | CMEEC - Norwich Stott St Solar Hybrid | CT | ISNE | Tesla Inc. | Tesla Inc. |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Backup Power | 0.8 | 3 | 3.75 | 2.5-4.5h | 2016 | 277 | C | HYBRID_ARTEFACT | 0.7044 | 0.73805 | -0.045572 | -0.00073613 |  |  | insufficient_history | 8.1092 | ok | 94 | 0.015667 | 0.98433 | 6000 | 0 | 16 | 1 | 0.73684 | 24.68 | 0.8 | 0.8 | -0.00036458 | 0.74359 | 20 | 0.032788 | 0 | 0 | 0 | 0 | 0.064667 | 0.095415 | 0.0011985 | 0.0011993 | 0.005571 | 0.0083565 | 0.0001 | 0.0001 |  |  | 0.7234 | 0.66038 | 0.79747 | 0.7069 |  |  |  | 34 | 11.6667 | 21 | 27.3333 | 0 |  |  | 0.17002 | 0.047148 | 0.070277 | 0.13195 | 0 | LOW_ETA_AND_LOW_UTI
60617 | AEP Churubusco NaS | IN | PJM | Indiana Michigan Power Co | Indiana Michigan Power Co |  |  | FALSE |  | NAB | CS | Load Management | 2 | 2 | 1 | <1.5h | 2009 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2 | 2
60618 | AEP Bluffton NaS | OH | PJM | Ohio Power Co | Ohio Power Co |  |  | FALSE |  | NAB | CS | Load Management | 2 | 2 | 1 | <1.5h | 2008 |  |  | HEALTHY | [7 empty] | 7.0056 | ok | 1676.4167 | 0.2794 | 0.7206 | 6000 | 0 | 0 | 1 | 0.2174 | 0 | 2 | 2 | [16 empty] | RTE_2019: 0.2172; RTE_2020: 0.043975; RTE_2021: 0; EFC_2019: 149; EFC_2020: 25; EFC_2021: 0; UTI_2019: 0.07708; UTI_2020: 0.012724; UTI_2021: 0
60641 | Henrietta D Energy Storage LLC | CA | CISO | Henrietta D Energy Storage, LLC | Convergent Energy and Power LP |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 10 | 40 | 4 | 2.5-4.5h | 2021 | 18 | A | UNATTRIBUTED | 0.88452 | 0.75991 | 1.0351 | 0.036027 |  |  | ok | 1.0168 | ok | 636.6208 | 0.1061 | 0.8939 | 6000 | 1 | 0 | 1 | 0.83197 | 7858.1895 | 10 | 10 | 0.10351 | 0.81153 | 18 | 0.89824 | 390.664 | 56.9723 | 26.0127 | 23.8492 | 0.080762 | 0.20113 | 0.075292 | 0.25527 | 0.0070175 | 0.018713 | 0.0067964 | 0.024561 | RTE_2024: 0.78663; RTE_2025: 0.80284; EFC_2024: 140.375; EFC_2025: 192.1; UTI_2024: 0.55391; UTI_2025: 0.75643 | ELEVATED_P_AUX
60649 | Rabbit Hill Energy Storage Project | TX | ERCO | Rabbit Hill Energy Storage Project | Rabbit Hill Energy Storage Project |  |  | FALSE |  | LIB | CS | Frequency Regulation | 9.9 | 9.9 | 1 | <1.5h | 2020 |  |  | UNDER_DISPATCH | 0.90942 | 0.57943 | 0.79983 | 0.0015314 | -4.2378 | -13.7081 | ok | 0.36948 | ok | 762.1212 | 0.12702 | 0.87298 | 6000 | 6 | 0 | 1 | 0.78141 | 10299.0507 | 9.9 | 9.9 | 0.079183 | 0.65666 | 31 | 0.73525 | 55.3804 | 11.105 | 6.3511 | 1.6099 | 0.053242 | 0.18177 | 0.083488 | 0.087152 | 0.0045593 | 0.016717 | 0.007605 | 0.0075988 |  | 0.61777 | 0.53675 | 0.60538 | 0.65886 | 0.43814 | 0.70761 |  | 104.6465 | 90 | 127.3737 | 164.8485 | 68.6869 | 206.5657 |  | 0.092848 | 0.13638 | 0.30718 | 0.30791 | 0.11362 | 0.42484
60654 | Townsite Solar Project Hybrid | NV | WALC | Townsite Solar, LLC | Townsite Solar, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, Co-Located Renewable Firming, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 90 | 360 | 4 | 2.5-4.5h | 2021 | 430 | C | HYBRID_ARTEFACT | 0.84491 | 0.86192 | -0.26917 | 0.31615 | 0.59411 | 46.2037 | ok | -0.18905 | ok | 1101.8194 | 0.18364 | 0.81636 | 6000 | 7 | 2 | 1 | 0.8674 | 0 | 90 | 90 | -0.24226 | 0.8609 | 48 | 0.067142 | 4443.5128 | 405.0109 | 161.5962 | 0.99206 | 0.08949 | 0.14465 | 0.047201 | 0.0011993 | 0.0078125 | 0.013021 | 0.0041324 | 0.0001 | RTE_2022: 0.87081; RTE_2023: 0.86237; RTE_2024: 0.85507; RTE_2025: 0.85375; EFC_2022: 296.1278; EFC_2023: 292.1139; EFC_2024: 274.0972; EFC_2025: 239.4806; UTI_2022: 1.2108; UTI_2023: 1.0719; UTI_2024: 1.0618; UTI_2025: 0.90831 | PARTIAL_AVAILABILITY
60656 | McHenry Battery Storage | IL | PJM | McHenry Battery Storage | McHenry Battery Storage |  |  | FALSE |  | LIB | CS |  | 20 | 7.8 | 0.39 | <1.5h | 2016 | 454 | A | FULL_OUTAGE | 0.89847 | 0.8851 | 0.29681 | 0.015702 |  |  | insufficient_history |  | insufficient_history | 4681.6239 | 0.78027 | 0.21973 | 6000 | 0 | 12 | 1 | 0.88625 | 12514.0803 | 19.8 | 19.8 | 0.059361 | 0.88599 | 13 | 0.33359 | 2053.3251 | 132.7089 | 24.1016 | 42.3263 | 0.10809 | 0.12644 | 0.019147 | 0.12644 | 0.0095321 | 0.011265 | 0.0016274 | 0.011265 | 0.61187 |  |  | 0 | 0 | 0.87088 | 0.88686 | 34.359 | 0 | 0 | 0 | 0 | 243.8462 | 4303.2051 | 0.017615 | 0 | 0 | 0 | 0 | 0 | 2.5246 | FULL_OUTAGE
60660 | Willey Battery Utility | OH | PJM | Willey Battery Utility, LLC | Willey Battery Utility, LLC |  |  | FALSE |  | LIB | CS |  | 6 | 2 | 0.33333 | <1.5h | 2016 |  |  | UNATTRIBUTED | 0.82412 | 0.81287 | 0.16008 | -0.032404 | 0.4686 | 15.816 | ok | 0.015527 | ok | 37719.5 | 6.2866 | 0 | 6000 | 0 | 0 | 1 | 0.84644 | 358.8944 | 6 | 6 | 0.0096049 | 0.82071 | 33 | 0.18314 | 414.8626 | 26.8131 | 4.8945 | 8.5518 | 0.10809 | 0.12644 | 0.019243 | 0.12644 | 0.0095321 | 0.011265 | 0.0016357 | 0.011265 | 0.84678 | 0.83925 | 0.8501 | 0.837 | 0.80842 | 0.82774 | 0.82633 | 4501.5 | 3521.5 | 3777 | 3802.5 | 2918 | 3294 | 2400.5 | 2.4946 | 1.9235 | 2.2404 | 1.8983 | 2.1688 | 1.8263 | 1.8209
60661 | Mira Loma Energy Storage Facility | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, Transmission and Distribution Deferral, Load Management, Voltage or Reactive Power Support | 20 | 80 | 4 | 2.5-4.5h | 2016 | 170 | A | THERMAL_AUX | 0.88062 | 0.83324 | 0.28609 | -0.023217 | 4.8364 | 115.5094 | ok |  | insufficient_history | 309.6375 | 0.051606 | 0.94839 | 6000 | 5 | 0 | 1 | 0.8958 | 177.8477 | 20 | 20 | 0.057217 | 0.85367 | 24 | 0.6698 | 2333.4312 | 34.8029 | 78.9614 | 29.6002 | 0.30696 | 0.095163 | 0.15242 | 0.23407 | 0.030556 | 0.0083333 | 0.015039 | 0.022222 | RTE_2024: 0.85048; RTE_2025: 0.8561; EFC_2024: 133.3875; EFC_2025: 176.25; UTI_2024: 0.46876; UTI_2025: 0.50758 | THERMAL_AUX
60690 | Blue Summit Storage, LLC | TX | ERCO | Blue Summit Storage, LLC | Blue Summit Storage, LLC |  |  | FALSE |  | LIB | CS |  | 30 | 12.6 | 0.42 | <1.5h | 2017 | 462 | B | CELL_DEGRADATION | 0.87195 | 0.78155 | 0.49201 | -0.00064278 | -2.8372 | -25.5025 | ok | 0.073569 | ok | 8189.1204 | 1.3649 | 0 | 6000 | 5 | 6 | 1 | 0.83995 | 9569.9159 | 30 | 30 | 0.1476 | 0.79917 | 84 | 0.72119 | 330.2746 | 27.0931 | 0.23389 | 23.0429 | 0.10997 | 0.16034 | 0.0011985 | 0.3725 | 0.0097087 | 0.014563 | 0.0001 | 0.038835 | 0.80289 | 0.82187 | 0.8184 | 0.80457 | 0.79954 | 0.78634 | 0.68877 | 1126.2698 | 1214.2857 | 1248.9683 | 1138.3333 | 797.6984 | 660.7143 | 407.3016 | 0.89875 | 0.78664 | 1.0804 | 2.7641 | 1.5247 | 3.3521 | 1.9247 | PARTIAL_AVAILABILITY
60698 | Stanton Energy Reliability Center Hybrid | CA | CISO | W Power LLC | Wellhead Services, Inc |  |  | TRUE | rte_gt_1 | LIB | CS | Load Following, Ramping / Spinning Reserve | 20 | 9 | 0.45 | <1.5h | 2020 | 347 | C | HYBRID_ARTEFACT | 0.43863 | 0.3611 | -0.0020493 | 0.00094768 |  |  | ok | -0.2893 | ok | 150.5556 | 0.025093 | 0.97491 | 6000 | 0 | 5 | 1 | 0.26471 | 59 | 20 | 20 | -0.00040987 | 0.43426 | 33 | 0.0022354 | 30.8256 | 0.70241 | 0.0070645 | 0.044806 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  | 0.95604 | 0.18884 | 0.25937 | 0.34398 | 0.37002 | 0.32397 |  | 9.6667 | 29.3333 | 37.6667 | 26.3333 | 25.7778 | 21.7778 |  | 0.020095 | 0.047929 | 0.046456 | 0.043716 | 0.025611 | 0.028033 | PARTIAL_AVAILABILITY
60699 | DESI-1 Battery Energy Storage Facility | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 2.4 | 3.9 | 1.625 | 1.5-2.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2.4 | 2.4
60760 | PPA Grand | CA | CISO | esVolta LP | esVolta LP |  |  | FALSE |  | LIB | BL | Frequency Regulation | 2 | 8 | 4 | 2.5-4.5h | 2016 | 195 | A | UNATTRIBUTED | 0.78976 | 0.59465 | 0.57223 | -0.00061042 |  |  | insufficient_history | 2.9069 | ok | 1484.0312 | 0.24734 | 0.75266 | 6000 | 0 | 0 | 1 | 0.82298 | 205.0762 | 2 | 2 | 0.011445 | 0.68491 | 15 | 0.84291 |  |  |  |  | 0.30696 | 0.095163 | 0.055239 | 0.23407 | 0.030556 | 0.0083333 | 0.0048782 | 0.022222 | 0.82211 | 0.83757 | 0.83333 | 0.83597 | 0.71586 | 0.34759 |  | 292.875 | 189.5 | 187.5 | 138.875 | 57 | 8.125 |  | 1.7756 | 1.4536 | 0.75919 | 0.54713 | 0.17436 | 0 |  | LOW_ETA_AND_LOW_UTI
60791 | SunAnza | CA | CISO | Sierra Southwest Cooperative | Arizona Electric Pwr Coop Inc |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Co-Located Renewable Firming, Transmission and Distribution Deferral, Excess Wind and Solar Generation | 4.4 | 9.2 | 2.0909 | 1.5-2.5h | 2022.5455 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 4.4 | 4.4
60815 | Hampshire College Hybrid | MA | ISNE | Tesla Inc. | Tesla Inc. |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Backup Power | 1 | 1 | 1 | <1.5h | 2017 | 366 | C | HYBRID_ARTEFACT | 0.68184 | 0.51503 | 0.14605 | -0.0014873 | -4.1516 | 76.2003 | ok | -2.1465 | ok | 238 | 0.039667 | 0.96033 | 6000 | 0 | 1 | 1 | 0.7619 | 2.709 | 0.6 | 0.6 | 0.0014605 | 0.61472 | 25 | 0.29221 | 6.2771 | 0.11443 | 0.21651 | 0.21897 | 0.14606 | 0.051271 | 0.073289 | 0.27079 | 0.013158 | 0.004386 | 0.006601 | 0.026316 |  |  | 0.58974 | 0.66667 | 0.50877 | 0.54054 | 0.55488 |  |  | 46 | 32 | 29 | 40 | 91 |  |  | 0.049745 | 0.047939 | 0.049434 | 0.08226 | 0.1772 | LOW_ETA_AND_LOW_UTI
60906 | Mt. Tom Solar Project Hybrid | MA | ISNE | Mt. Tom Solar, LLC | Mt. Tom Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 3.1 | 6.1 | 1.9677 | 1.5-2.5h | 2019 | 295 | C | HYBRID_ARTEFACT | 0.85148 | 0.57745 | 0.5187 | -5.9389e-05 | -9.4049 | -41.7658 | ok | 0.96472 | ok | 334.5902 | 0.055765 | 0.94423 | 6000 | 0 | 1 | 1.55 | 0.92473 | 5.5 | 2 | 3.1 | 0.01608 | 0.64771 | 29 | 0.82082 | 26.1427 | 0.40848 | 0.011606 | 0.65141 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 0.52577 | 0.53084 | 0.47561 | 0.55139 | 0.52646 | 0.70228 | 0.61522 | 41.8033 | 46.5574 | 44.7541 | 55.4098 | 32.623 | 65.7377 | 47.7049 | 0.82051 | 0.73767 | 0.20298 | 0.24563 | 0.15221 | 0.93753 | 0.64114 | LOW_ETA_AND_LOW_UTI
60959 | Chocksett Rd Energy Storage Project | MA | ISNE | Sterling Municipal Light Department - (MA) | Sterling Municipal Light Department - (MA) |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage, Transmission and Distribution Deferral, Load Management, Backup Power | 2 | 3.9 | 1.95 | 1.5-2.5h | 2017 | 225 | C | HYBRID_ARTEFACT | 0.61144 | 0.50937 | 0.26547 | -0.0021277 |  |  | ok | -1.8416 | ok | 276.7308 | 0.046122 | 0.95388 | 6000 | 0 | 9 | 1 | 0.73333 | 66.5 | 2 | 2 | 0.0053094 | 0.5376 | 24 | 0.11397 | 7.9565 | 0.12432 | 0.0035323 | 0.19825 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 0.78443 | 0.76048 | 0.74194 | 1.3571 | 0.48553 | 0.55866 | 0.52841 | 33.5897 | 32.5641 | 29.4872 | 34.1026 | 38.7179 | 25.641 | 23.8462 | 0.55054 | 0.51598 | 0.13374 | 0.15118 | 0.1899 | 0.085948 | 0.38057 | LOW_ETA_AND_LOW_UTI
60964 | Apache Solar I | AZ | WALC | Sierra Southwest Cooperative | Arizona Electric Pwr Coop Inc |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 20 | 80 | 4 | 2.5-4.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 20 | 20
60974 | Glendale Battery Energy Storage System | CA | LDWP | City of Glendale - (CA) | City of Glendale - (CA) |  |  | TRUE | rte_gt_1 | LIB | CS | Voltage or Reactive Power Support | 2 | 1 | 0.5 | <1.5h | 2017 | 364 | C | FULL_OUTAGE |  | 1 |  |  |  |  | insufficient_history |  | insufficient_history | 216.5 | 0.036083 | 0.96392 | 6000 | 0 | 21 | 2 | 1.3684 | 30.615 | 1 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 | 2.3636 | 1 | 1.3333 | 0.70673 | 0 | 0 | 0.16667 | 26 | 6 | 4 | 147 | 0 | 0 | 1 | 0.25508 | 0.0037463 | 0 | 0.1824 | 0 | 0 | 0 | FULL_OUTAGE
60996 | Iron Horse Battery Storage Hybrid | AZ | TEPC | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 10 | 2.5 | 0.25 | <1.5h | 2017 | 443 | C | FULL_OUTAGE | 0.82869 | 0.52623 | 0.66954 | 0.0067717 |  |  | insufficient_history | -0.53119 | ok | 1773.8 | 0.29563 | 0.70437 | 6000 | 12 | 24 | 1 | 0.71468 | 419.995 | 10 | 10 | 0.066954 | 0.52901 | 12 | 0.79301 | 76.3301 | 3.211 | 1.0798 | 1.1265 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 | 0.625 | 0.62353 | 0.62921 | 0.71564 |  |  | 0.52901 | 200 | 53 | 224 | 604 | 0 | 0 | 342.8 | 0.15036 | 0.035408 | 0.19626 | 0.7236 | 0 | 0 | 1.0088 | FULL_OUTAGE
61068 | AES Lawai Solar Hybrid | HI |  | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 20 | 100 | 5 | >4.5h | 2018 | 420 | C | HYBRID_ARTEFACT | 0.99442 | 0.97195 | 0.10149 | -0.017582 | -0.23917 | -5.1083 | ok | -0.22694 | ok | 935.69 | 0.15595 | 0.84405 | 6000 | 0 | 5 | 1 | 0.99962 | 2810.5 | 20 | 20 | 0.020298 | 0.97348 | 70 | 0.59019 | 1652.0405 | 99.3814 | 0.93706 | 23.0522 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 |  | 0.98321 | 0.98502 | 0.9834 | 0.95264 | 0.97879 | 0.96139 |  | 254.16 | 105.21 | 46.8 | 120.3 | 197.55 | 211.67 |  | 1.6603 | 0.72906 | 0.30519 | 2.1598 | 2.0373 | 1.9259 | PARTIAL_AVAILABILITY
61098 | Battle Mountain Solar Project | NV | NEVP | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Voltage or Reactive Power Support, Backup Power, Excess Wind and Solar Generation | 25 | 25 | 1 | <1.5h | 2021 | 48 | C | HYBRID_ARTEFACT | 0.92801 | 0.91855 | -0.016069 | 0.010698 | -0.63077 | 6.9559 | ok | -0.40823 | ok | 4850.76 | 0.80846 | 0.19154 | 6000 | 0 | 4 | 1 | 0.87125 | 3277.5 | 25 | 25 | -0.0040173 | 0.92884 | 54 | 0.0016559 | 2165.8197 | 78.9628 | 1.0622 | 25.1845 | 0.15484 | 0.10609 | 0.0011985 | 0.10609 | 0.014019 | 0.0093458 | 0.0001 | 0.0093458 |  |  | 0.943 | 0.94129 | 0.91667 | 0.91959 | 0.92967 |  |  | 503.6 | 1136.32 | 1053.8 | 1026.08 | 1130.96 |  |  | 0.64267 | 1.4728 | 1.8126 | 2.5004 | 3.1934 | PARTIAL_AVAILABILITY
61107 | Vanadium Redox Flow Battery Plant | CA | CISO | San Diego Gas & Electric Co | SDGE Batteries |  |  | TRUE | colocated_firming | FLB | CS | Frequency Regulation, Load Following | 2 | 8 | 4 | 2.5-4.5h | 2017 | 441 | C | HYBRID_ARTEFACT | 0.68766 | 0.39402 | 6.0364 | -0.010817 | 2.4203 | 19.3976 | ok | 0.22587 | ok | 1662.6146 | 0.2771 | 0.7229 | 6000 | 0 | 0 | 1 | 0.54567 | 0 | 2 | 2 | 0.12073 | 0.48739 | 23 | 0.85568 | 237.7162 | 3.5455 | 2.4593 | 3.0155 | 0.30696 | 0.095163 | 0.052234 | 0.23407 | 0.030556 | 0.0083333 | 0.0045979 | 0.022222 | 0.60892 | 0.68115 | 0.63756 | 0.6769 | 0.4887 | 0.31789 | 0.44774 | 216.625 | 213.625 | 193.5 | 220.5 | 216.25 | 79.75 | 179.375 | 0.73965 | 1.1273 | 1.0006 | 1.5878 | 0.87875 | 0.23511 | 0.54907 | ELEVATED_P_AUX
61168 | Eland Solar & Storage Center, Phase 1 Hy | CA | LDWP | Arevon Asset Management | 68SF 8me LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Load Following, Voltage or Reactive Power Support | 150 | 600 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.91691 | 0.87958 | 0.53143 | 0.31788 |  |  | insufficient_history |  | insufficient_history | 316.0967 | 0.052683 | 0.94732 | 6000 | 0 | 0 | 1 | 0.87386 | 0 | 150 | 150 | 0.79714 | 0.88188 | 14 | 0.70814 | 7275.1193 | 397.8613 | 237.8396 | 571.0239 | 0.081309 | 0.081309 | 0.038731 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033604 | 0.031802 | RTE_2024: 0.89192; RTE_2025: 0.88028; EFC_2024: 43.8617; EFC_2025: 272.235; UTI_2024: 0.97019; UTI_2025: 0.99163
61169 | Eland Solar & Storage Center, Phase 2 Hy | CA | LDWP | Arevon Asset Management | 69SV 8me LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Voltage or Reactive Power Support | 150 | 600 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.89284 |  |  |  |  | insufficient_history |  | insufficient_history | 114.6367 | 0.019106 | 0.98089 | 6000 | 0 | 0 | 1 | 0.8988 | 0 | 150 | 150 |  |  |  |  | 7160.4892 | 391.5924 | 240.835 | 562.0266 | 0.081309 | 0.081309 | 0.039802 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034572 | 0.031802 | RTE_2025: 0.89318; EFC_2025: 114.6367; UTI_2025: 0.95131
61186 | Boston Medical Center CHP Plant | MA | ISNE | Boston Medical Center | Boston Medical Center |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support, Backup Power | 1 | 1.1 | 1.1 | <1.5h | 2023 | 235 | A | UNATTRIBUTED | 0.69749 | 0.60141 | 0.05437 | 0.00022412 |  |  | ok | -0.75049 | ok | 160.9091 | 0.026818 | 0.97318 | 6000 | 0 | 0 | 1 | 0.82857 | 58.4569 | 0.6 | 0.6 | 0.0005437 | 0.7382 | 20 | 0.11413 | 1.4827 | 0.081087 | 0.0010092 | 0.0086206 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2023: 0.71642; RTE_2024: 0.64815; RTE_2025: 0.60204; EFC_2023: 43.6364; EFC_2024: 63.6364; EFC_2025: 53.6364; UTI_2023: 0.08567; UTI_2024: 0.045119; UTI_2025: 0.044021 | LOW_ETA_AND_LOW_UTI
61197 | Pima Energy Storage System | AZ | TEPC | Pima Energy Storage System | Pima Energy Storage System |  |  | TRUE | rte_gt_1 | LIB | CS |  | 10 | 10 | 1 | <1.5h | 2017 | 375 | C | HYBRID_ARTEFACT |  | 0.14559 |  |  |  |  | insufficient_history | -3.8361 | ok | 303.7 | 0.050617 | 0.94938 | 6000 | 12 | 9 | 1.25 | 0.84286 | 11 | 8 | 10 |  |  |  |  | 6.1889 | 0.26035 | 0.076491 | 0.091341 | 0.15519 | 0.12167 | 0.029407 | 0.13299 | 0.014054 | 0.010811 | 0.0025264 | 0.011892 | 0.19882 | 0.47942 | 0.12987 | 0.09462 | 0.085791 | 0.28212 | 0.13224 | 40.4 | 93.2 | 32 | 25.5 | 12.8 | 10.1 | 8.9 | 0.013894 | 0.0096634 | 0.023552 | 0.031576 | 0.014403 | 0.0073968 | 0.018807 | FULL_OUTAGE
61204 | AES ES Alamitos, LLC | CA | CISO | AES ES Alamitos, LLC | AES ES Alamitos, LLC |  |  | FALSE |  | LIB | BL | Arbitrage | 100 | 400 | 4 | 2.5-4.5h | 2021 | 82 | A | THERMAL_AUX | 0.94552 | 0.8735 | 0.99627 | 0.075326 | -0.19589 | -3.1301 | ok | 0.32557 | ok | 1338.95 | 0.22316 | 0.77684 | 6000 | 0 | 5 | 1 | 0.89523 | 34043.4943 | 100 | 100 | 0.99627 | 0.87779 | 60 | 0.49434 | 4092.8304 | 596.8759 | 1121.9341 | 249.8581 | 0.080762 | 0.20113 | 0.25018 | 0.25527 | 0.0070175 | 0.018713 | 0.027979 | 0.024561 |  |  | 0.89553 | 0.87998 | 0.87073 | 0.85384 | 0.87563 |  |  | 377.635 | 284.3425 | 237.275 | 202.405 | 237.2925 |  |  | 1.818 | 1.0788 | 0.75223 | 0.78535 | 0.88357 | PARTIAL_AVAILABILITY
61334 | Volkman Road Solar Array Hybrid | IN | MISO | Southern Indiana Gas & Elec Co | Southern Indiana Gas & Elec Co |  |  | TRUE | pv_same_plant | LIB | CT | System Peak Shaving | 1 | 4.6 | 4.6 | >4.5h | 2019 | 196 | C | HYBRID_ARTEFACT | 0.90287 | 0.9205 | -0.016941 | -0.00012444 | -0.3436 | -84.5356 | ok | -0.48971 | ok | 411.5217 | 0.068587 | 0.93141 | 6000 | 0 | 12 | 1 | 0.92063 | 166.5 | 1 | 1 | -0.00016941 | 0.91045 | 22 | 0.084642 | 0 | 0 | 0 | 0 | 0.26681 | 0.050409 | 0.072405 | 0.14373 | 0.025862 | 0.0043103 | 0.006515 | 0.012931 | 0.91391 | 0.89973 | 0.89538 | 0.91667 | 0.91667 | 0.91104 | 0.89691 | 30 | 72.1739 | 80 | 110 | 35.8696 | 64.5652 | 18.913 | 0.45879 | 0.48426 | 0.66022 | 0.79289 | 0.071398 | 0.69268 | 0 | FULL_OUTAGE
61362 | NRG Elbow Creek Energy Storage Project | TX | ERCO | NRG Texas Power LLC | NRG Texas Power LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 2 | 0.7 | 0.35 | <1.5h | 2017 |  |  | HEALTHY | [7 empty] | -0.17637 | ok | 2159.2857 | 0.35988 | 0.64012 | 6000 | 2 | 0 | 1 | 0.69709 | 0 | 2 | 2 | [16 empty] | RTE_2019: 0.69231; RTE_2020: 0.70248; RTE_2021: 0.76033; RTE_2022: 0.77188; EFC_2019: 398.5714; EFC_2020: 485.7143; EFC_2021: 394.2857; EFC_2022: 415.7143; UTI_2019: 0.32209; UTI_2020: 0.31017; UTI_2021: 0.29682; UTI_2022: 0.93695
61365 | Fallbrook Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 40 | 40 | 1 | <1.5h | 2023 | 41 | B | UNATTRIBUTED | 0.83293 | 0.79676 | 0.51164 | -0.045934 | 1.3266 | 16.2926 | ok | 0.24775 | ok | 2347.275 | 0.39121 | 0.60879 | 6000 | 0 | 1 | 1 | 0.79304 | 7515.6098 | 40 | 40 | 0.20466 | 0.80188 | 30 | 0.46217 | 3033.9368 | 248.8796 | 86.9202 | 13.2296 | 0.13809 | 0.19981 | 0.058244 | 0.03647 | 0.012384 | 0.018576 | 0.0051604 | 0.003096 | RTE_2023: 0.79691; RTE_2024: 0.7969; RTE_2025: 0.80975; EFC_2023: 532.375; EFC_2024: 896; EFC_2025: 918.9; UTI_2023: 1.4339; UTI_2024: 1.2474; UTI_2025: 1.2726 | LOW_ETA_AND_LOW_UTI
61366 | Top Gun Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Load Following, Ramping / Spinning Reserve | 30 | 120 | 4 | 2.5-4.5h | 2021 | 416 | B | UNDER_DISPATCH | 0.90905 | 0.80617 | 0.94654 | -0.0075043 | 0.083991 | -4.8994 | ok | 0.23319 | ok | 886.8417 | 0.14781 | 0.85219 | 6000 | 0 | 2 | 1 | 0.8357 | 34448.2949 | 30 | 30 | 0.28396 | 0.82993 | 53 | 0.54878 | 1508.8337 | 220.04 | 82.8702 | 92.1109 | 0.080762 | 0.20113 | 0.062951 | 0.25527 | 0.0070175 | 0.018713 | 0.005606 | 0.024561 |  |  | 0.77408 | 0.77604 | 0.84144 | 0.83251 | 0.85182 |  |  | 75.0083 | 118.825 | 203.7333 | 204.2417 | 285.0333 |  |  | 0.72636 | 0.41271 | 0.71183 | 0.71989 | 1.0284 | PARTIAL_AVAILABILITY
61431 | Beacon BESS 1 | CA | LDWP | Los Angeles Department of Water & Power | Los Angeles Department of Water & Power |  |  | TRUE | colocated_firming | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, Voltage or Reactive Power Support | 20 | 10 | 0.5 | <1.5h | 2018 | 446 | C | HYBRID_ARTEFACT | 0.74977 | 0.63963 | 0.31843 | 0.023469 | -4.9757 | -23.4022 | ok | -0.27364 | ok | 1919.825 | 0.31997 | 0.68003 | 6000 | 1 | 3 | 1 | 0.55404 | 319 | 20 | 20 | 0.063687 | 0.64532 | 76 | 0.22412 | 347.6116 | 14.6232 | 4.2963 | 5.1303 | 0.15519 | 0.12167 | 0.029407 | 0.13299 | 0.014054 | 0.010811 | 0.0025264 | 0.011892 | 0.60106 | 0.60767 | 0.66891 | 0.70884 | 0.70246 | 0.60563 | 0.57571 | 148.1 | 123.6 | 267.9 | 295.8 | 299.6 | 348.6 | 399.2 | 0.10759 | 0.096037 | 0.24262 | 0.37736 | 0.49736 | 0.76998 | 1.2216 | LOW_ETA_AND_LOW_UTI
61439 | Panasonic Carport Solar Hybrid | CO | PSCO | Public Service Co of Colorado | Public Service Co of Colorado |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, Backup Power, Excess Wind and Solar Generation | 1 | 2.2 | 2.2 | 1.5-2.5h | 2017 | 419 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 924.2424 | 0.15404 | 0.84596 | 6000 | 0 | 36 | 1 | 0.99997 | 0 | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.27826 | 0.093193 | 0.069605 | 0.0011993 | 0.027174 | 0.0081522 | 0.0062438 | 0.0001 | 0.17857 | 1 | [5 empty] | 90.9091 | 704.5455 |  | 0 | 0 | 0 | 0 | 1.5781 | 10.1614 |  | 0 | 0 | 0 | 0 | FULL_OUTAGE
61446 | RE Gaskell West 2 LLC | CA | CISO | RE Gaskell West LLC | RE Gaskell West LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage | 20 | 20 | 1 | <1.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 20 | 20
61473 | Hopewell Valley High School Hybrid | NJ | PJM | Hopewell Valley High School | Hopewell Valley High School |  |  | TRUE | colocated_firming,pv_same_plant | LIB | BL | Arbitrage, Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving, Voltage or Reactive Power Support | 1 | 1 | 1 | <1.5h | 2015 | 450 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 3266.6667 | 0.54444 | 0.45556 | 6000 | 0 | 36 | 1 | 0.893 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.10809 | 0.12644 | 0.019147 | 0.12644 | 0.0095321 | 0.011265 | 0.0016274 | 0.011265 | 0.89385 | [6 empty] | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40181 | 0 | 0 | 0 | 0 | 0 | 0 | FULL_OUTAGE
61552 | Fort Detrick Solar PV | MD | PJM | Montevue Lane Solar, LLC | Montevue Lane Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 6 | 6 | 1 | <1.5h | 2024 | 94 | C | HYBRID_ARTEFACT | 0.85035 | 0.85003 | 0.013153 | 0.023936 |  |  | insufficient_history | -0.72359 | ok | 1471.1667 | 0.24519 | 0.75481 | 6000 | 0 | 2 | 1 | 0.83874 | 896 | 6 | 6 | 0.00078915 | 0.85194 | 20 | 0.0011855 | 404.9447 | 18.0856 | 11.1362 | 12.3605 | 0.13542 | 0.11205 | 0.054941 | 0.22481 | 0.012126 | 0.009903 | 0.0048503 | 0.021221 | RTE_2024: 0.83739; RTE_2025: 0.8612; EFC_2024: 562.1667; EFC_2025: 909; UTI_2024: 0.38804; UTI_2025: 0.60702 | LOW_ETA_AND_LOW_UTI
61647 | ENO Paterson Solar | LA | MISO | Entergy New Orleans, LLC | Entergy New Orleans, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 0.5 | 0.5 | 1 | <1.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
61661 | Vista Energy Storage System | CA | CISO | Vista Energy Storage, LLC | Vista Energy Storage, LLC |  |  | FALSE |  | LIB | BL | Frequency Regulation, Ramping / Spinning Reserve | 40 | 38 | 0.95 | <1.5h | 2018 | 452 | A | UNDER_DISPATCH | 0.94202 | 0.84268 | 0.69845 | -0.031724 | 0.80819 | 16.1317 | ok | 0.055128 | ok | 4442.1547 | 0.74036 | 0.25964 | 6000 | 0 | 3 | 1 | 0.88415 | 67918.601 | 40 | 40 | 0.27938 | 0.85494 | 84 | 0.54866 | 1296.2964 | 60.258 | 11.3198 | 48.6121 | 0.15254 | 0.13124 | 0.020581 | 0.29943 | 0.013793 | 0.011724 | 0.0017519 | 0.029655 | 0.9077 | 0.881 | 0.85451 | 0.84535 | 0.83758 | 0.81126 | 0.81445 | 631.075 | 731.8 | 716.125 | 635.975 | 544.7105 | 392.3947 | 421.9474 | 0.4431 | 0.5545 | 0.70784 | 0.62144 | 0.80248 | 0.71564 | 0.81503 | PARTIAL_AVAILABILITY
61667 | Wimauma Solar and Battery Storage | FL | TEC | Tampa Electric Co | Tampa Electric Co |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 40 | 80 | 2 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.71136 |  |  |  |  | insufficient_history |  | insufficient_history | 72 | 0.012 | 0.988 | 6000 | 0 | 0 | 1 | 0.83909 | 0 | 40 | 40 |  |  |  |  | 683.485 | 18.6892 | 0.22556 | 11.9215 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2025: 0.76241; EFC_2025: 72; UTI_2025: 0.27185
61678 | Pinal Central Energy Center Hybrid | AZ | SRP | Pinal Central Energy Center, LLC | Pinal Central Energy Center, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 10 | 40 | 4 | 2.5-4.5h | 2018 | 133 | C | HYBRID_ARTEFACT | 1.0232 | 0.87284 | 2.6109 | 0.068689 | -1.5434 | -29.2106 | ok | 0.022154 | ok | 2629.6375 | 0.43827 | 0.56173 | 6000 | 16 | 14 | 1 | 0.78092 | 1155.5 | 10 | 10 | 0.26109 | 0.87523 | 84 | 0.088483 | 315.5958 | 112.1853 | 15.9018 | 0.13211 | 0.048771 | 0.27747 | 0.035322 | 0.0011993 | 0.0041667 | 0.027083 | 0.0030536 | 0.0001 | 0.85896 | 0.99381 | 0.91914 | 0.81756 | 0.85141 | 0.84914 | 0.84136 | 337.25 | 377.25 | 356.075 | 341.125 | 336.5 | 331.1 | 297.4 | 1.776 | 2.4846 | 1.7974 | 1.3068 | 1.2729 | 1.2884 | 0.88263 | PARTIAL_AVAILABILITY
61679 | Cox Battery Energy Storage | MO | SWPP | City Utilities of Springfield - (MO) | City Utilities of Springfield - (MO) |  |  | TRUE | rte_gt_1 | PBB | CS | Load Management | 1.2 | 1.5 | 1.25 | <1.5h | 2017 |  |  | HEALTHY | [8 empty] | insufficient_history | 228.8889 | 0.038148 | 0.96185 | 6000 | 0 | 0 | 0.83333 | 5.7333 | 0 | 1.2 | 1 | [16 empty] | RTE_2019: 5.45; RTE_2020: 5.7333; RTE_2021: 3; EFC_2019: 72.6667; EFC_2020: 57.3333; EFC_2021: 2; UTI_2019: 0.051238; UTI_2020: 0; UTI_2021: 0
61721 | Baldwin (CA) | CA | CISO | Sk Holdings Co. Ltd. | Electrodes |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage, System Peak Shaving | 1 | 6.9 | 6.9 | >4.5h | 2019 | 401 | C | HYBRID_ARTEFACT | 0.87837 | 0.89077 | -0.021785 | 0.00036643 | -1.3204 | -58.4017 | ok | 1.8495 | ok | 679.8551 | 0.11331 | 0.88669 | 6000 | 0 | 4 | 1 | 0.88665 | 120 | 1 | 1 | -0.00021785 | 0.88127 | 72 | 0.11163 | 2.8697 | 1.5694 | 0.008326 | 0.25027 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 |  | 0.88322 | 0.88839 | 0.87623 | 0.9147 | 0.88013 | 0.84022 |  | 200.5797 | 143.0435 | 154.9275 | 73.0435 | 40.4348 | 67.8261 |  | 0.92622 | 1.3103 | 1.1952 | 1.2534 | 0.28555 | 0.27404 | PARTIAL_AVAILABILITY
61722 | HEBT Irvine 1 | CA | CISO | Macquarie Capital | Electrodes |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5.5 | 33.5 | 6.0909 | >4.5h | 2018 | 315 | A | UNATTRIBUTED | 0.856 | 0.86473 | -0.027209 | 0.00012423 | -4.0305 | -146.158 | ok | -1.0511 | ok | 1266.8856 | 0.21115 | 0.78885 | 6000 | 0 | 0 | 1 | 0.90008 | 0.78813 | 5.5 | 5.5 | -0.0014965 | 0.85303 | 36 | 0.15379 | 79.1337 | 43.2766 | 0.2296 | 6.9013 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | 0.9039 | 0.89999 | 0.87994 | 0.87986 | 0.87989 | 0.88358 | 0.83023 | 29.7612 | 732.0299 | 117.0448 | 116.2985 | 69.1045 | 46.8955 | 135.9104 | 0.33877 | 5.0589 | 0.96635 |  | 0.80524 | 0.46365 | 1.2126 | LOW_ETA_AND_LOW_UTI
61723 | HEBT Irvine 2 | CA | CISO | Macquarie Capital | Electrodes |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5.8 | 34.8 | 6 | >4.5h | 2018 |  |  | UNATTRIBUTED | 0.86091 | 0.86364 | -0.0074115 | 0.00053881 | -2.5121 | -24.5437 | ok | 0.75307 | ok | 963.8937 | 0.16065 | 0.83935 | 6000 | 0 | 0 | 1 | 0.89999 | 439.0276 | 5.8 | 5.8 | -0.00042987 | 0.8574 | 36 | 0.020379 | 65.7419 | 35.9529 | 0.19074 | 5.7334 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | 0.87891 | 0.90001 | 0.87996 | 0.58673 | 0.87919 | 0.88137 | 0.83275 | 55.6897 | 432.1839 | 121.1207 | 99.8276 | 53.5345 | 69.5977 | 108.7356 | 0.63391 | 2.9867 | 1.0348 | 0.70413 | 0.38402 | 0.68822 | 0.93562
61730 | MA Solar Storage 1 Hybrid | MA | ISNE | Origis Energy USA, Inc | Origis Energy USA, Inc |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Excess Wind and Solar Generation | 1 | 2 | 2 | 1.5-2.5h | 2018 | 314 | C | HYBRID_ARTEFACT | 0.93197 | 0.95113 | -0.018915 | -2.6762e-05 | 1.2673 | -74.2756 | ok | 0.37047 | ok | 1055.125 | 0.17585 | 0.82415 | 6000 | 0 | 3 | 1 | 0.92243 | 0.5 | 1 | 1 | -0.00018915 | 0.94376 | 36 | 0.13613 | 22.1644 | 0.34632 | 0.0098399 | 0.55228 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 0.9726 | 0.90643 | 0.91473 | 0.9172 | 0.92453 | 0.92419 | 0.97071 | 177.5 | 155 | 177 | 144 | 24.5 | 128 | 116 | 2.9092 | 2.4559 | 0.80278 | 0.63837 | 0.13942 | 1.4585 | 1.4202 | PARTIAL_AVAILABILITY
61737 | Navy Yard Peaker Station | PA | PJM | Philadelphia Authority for Industrial Development | Philadelphia Authority for Industrial Development |  |  | TRUE | rte_gt_1 | LIB | CS | Frequency Regulation, System Peak Shaving | 6.2 | 6.2 | 1 | <1.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.91971 | 0.92878 | -0.14953 | 0.0045539 |  |  | insufficient_history | -2.5542 | ok | 2196.4516 | 0.36608 | 0.63392 | 6000 | 0 | 0 | 1 | 0.93688 | 0 | 6.2 | 6.2 | -0.0092706 | 0.92858 | 12 | 0.072616 |  |  |  |  | 0.15254 | 0.13124 | 0.023618 | 0.29943 | 0.013793 | 0.011724 | 0.0020168 | 0.029655 | RTE_2021: 4.0789; RTE_2022: 0.91571; RTE_2023: 0.92858; EFC_2021: 25; EFC_2022: 890.1613; EFC_2023: 1281.2903; UTI_2021: 0.0352; UTI_2022: 0.44367; UTI_2023: 0.77978
61739 | Lockheed Martin RMS Syracuse | NY | NYIS | Lockheed Martin RMS Syracuse | Lockheed Martin RMS Syracuse |  |  | FALSE |  | LIB | CS | Arbitrage, Load Management | 1 | 1.3 | 1.3 | <1.5h | 2017 | 321 | B | FULL_OUTAGE | [8 empty] | insufficient_history | 0.76923 | 0.00012821 | 0.99987 | 6000 | 0 | 36 | 1 | 1 | 0 | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.13116 | 0.11705 | 0.044248 | 0.25826 | 0.011716 | 0.010373 | 0.0038617 | 0.024896 | RTE_2022: 1; EFC_2022: 0.76923; EFC_2023: 0; EFC_2024: 0; EFC_2025: 0; UTI_2022: 0.012002; UTI_2023: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
61741 | Kingsberry Energy Storage System | TX | ERCO | Austin Energy | Austin Energy |  |  | TRUE | colocated_firming | LIB | CS |  | 1.5 | 3 | 2 | 1.5-2.5h | 2018 | 371 | C | HYBRID_ARTEFACT |  | 0.585 |  |  |  |  | insufficient_history | -0.040923 | ok | 275.5556 | 0.045926 | 0.95407 | 6000 | 7 | 10 | 1 | 0.60059 | 42.785 | 1.5 | 1.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | 0.61074 | 0.42587 | 0.59629 | 0.6171 | 0.57778 | 0 | 0 | 60.6667 | 45 | 85.6667 | 55.3333 | 8.6667 | 0 | 0 | 0.90253 | 0.63713 | 0.39902 | 0.22564 | 0 | 0 | 0 | FULL_OUTAGE
61763 | Sunshine Gateway Solar Energy Center | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Transmission and Distribution Deferral, Excess Wind and Solar Generation | 30 | 75 | 2.5 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.87795 | 0.79241 | 0.46666 | 0.19698 | -0.43133 | -7.0693 | ok | 0.049031 | ok | 546.6133 | 0.091102 | 0.9089 | 6000 | 0 | 0 | 1 | 0.81891 | 0 | 30 | 30 | 0.14 | 0.79913 | 45 | 0.27873 | 371.2723 | 33.8402 | 13.6192 | 0.08289 | 0.08949 | 0.14465 | 0.04759 | 0.0011993 | 0.0078125 | 0.013021 | 0.0041683 | 0.0001 | RTE_2022: 0.76836; RTE_2023: 0.82937; RTE_2024: 0.8112; RTE_2025: 0.76293; EFC_2022: 114.5067; EFC_2023: 163.5067; EFC_2024: 165.1067; EFC_2025: 103.4933; UTI_2022: 0.52073; UTI_2023: 0.60797; UTI_2024: 0.74625; UTI_2025: 0.36531
61795 | Pacific Union College BESS | CA | CISO | ENGIE Storage Services NA LLC | ENGIE Storage Services NA LLC |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage, Load Management | 1 | 2 | 2 | 1.5-2.5h | 2020 | 329 | C | HYBRID_ARTEFACT | 0.5901 | 0.37843 | 0.1929 | 0.00073501 |  |  | insufficient_history | -3.5396 | ok | 55.5 | 0.00925 | 0.99075 | 6000 | 0 | 0 | 1 | 0.57143 | 0 | 1 | 1 | 0.001929 | 0.5045 | 12 | 0.049341 | 1.5419 | 0.16865 | 0.12092 | 0.040341 | 0.095923 | 0.18264 | 0.10294 | 0.14038 | 0.0084034 | 0.016807 | 0.0095851 | 0.012605 | RTE_2020: 0.96875; RTE_2024: 0.38406; RTE_2025: 0.27551; EFC_2020: 15.5; EFC_2024: 26.5; EFC_2025: 13.5; UTI_2020: 0.39382; UTI_2024: 0.08265; UTI_2025: 0.049682 | LOW_ETA_AND_LOW_UTI
61801 | Cascade Energy Storage, LLC | CA | CISO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 25 | 100 | 4 | 2.5-4.5h | 2024 | 17 | A | UNATTRIBUTED | 0.94958 | 0.8381 | 1.6708 | -0.092414 |  |  | insufficient_history |  | insufficient_history | 315.5 | 0.052583 | 0.94742 | 6000 | 0 | 2 | 1 | 0.87522 | 7871.3737 | 25 | 25 | 0.4177 | 0.84097 | 14 | 0.35931 | 711.6227 | 129.7239 | 15.9181 | 103.4356 | 0.051638 | 0.16199 | 0.016951 | 0.35714 | 0.0044183 | 0.014728 | 0.0014375 | 0.036819 | RTE_2024: 0.82029; RTE_2025: 0.85013; EFC_2024: 94.44; EFC_2025: 221.06; UTI_2024: 0.94036; UTI_2025: 0.89794 | ELEVATED_P_AUX
61803 | Sierra Energy Storage, LLC | CA | CISO | Enel Green Power NA, Inc. | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 40 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.90196 |  |  |  |  | insufficient_history |  | insufficient_history | 69 | 0.0115 | 0.9885 | 6000 | 0 | 0 | 1 | 0.85064 | 465.5413 | 10 | 10 |  |  |  |  | 228.6143 | 41.6748 | 5.2074 | 33.2295 | 0.051638 | 0.16199 | 0.017256 | 0.35714 | 0.0044183 | 0.014728 | 0.0014638 | 0.036819 | RTE_2025: 0.8999; EFC_2025: 69; UTI_2025: 0.70188
61851 | Campbell Industrial Park BESS | HI | HECO | Hawaiian Electric Co Inc | Hawaiian Electric Co Inc |  |  | TRUE | rte_gt_1,colocated_firming | LIB | CS | Load Following, Co-Located Renewable Firming, Voltage or Reactive Power Support | 1 | 0.3 | 0.3 | <1.5h | 2016 |  |  | HEALTHY | [8 empty] | insufficient_history | 1495 | 0.24917 | 0.75083 | 6000 | 0 | 0 | 1 | 0.85925 | 0 | 1 | 1 | [16 empty] | RTE_2019: 0.96694; EFC_2019: 390; EFC_2020: 0; UTI_2019: 0.28442; UTI_2020: 0
61861 | AES ES GILBERT | AZ | SRP | AES ES GILBERT, LLC | AES ES GILBERT, LLC |  |  | TRUE | rte_gt_1 | LIB | BL |  | 10 | 40 | 4 | 2.5-4.5h | 2019 | 423 | C | FULL_OUTAGE | 0.87258 | 0.86259 | 0.17088 | -0.028232 | -6.0612 | -121.8932 | ok |  | insufficient_history | 1008.75 | 0.16812 | 0.83188 | 6000 | 21 | 44 | 1 | 0.85296 | 3203.5 | 10 | 10 | 0.017088 | 0.86369 | 39 | 0.19363 | 0 | 0 | 0 | 0 | 0.048771 | 0.27747 | 0.035322 | 0.0011993 | 0.0041667 | 0.027083 | 0.0030536 | 0.0001 | 0.85683 | 0.86265 | 0.87339 | 0.84773 |  |  |  | 233.4 | 349.35 | 329.55 | 96.45 | 0 | 0 | 0 | 1.3502 | 2.3219 | 1.6324 | 0 | 0 | 0 | 0 | FULL_OUTAGE
61891 | Stryker 22, L.L.C. | NJ | PJM | Stryker 22, L.L.C. | Stryker 22, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 19.8 | 19.8 | 1 | <1.5h | 2018 | 176 | A | PARTIAL_AVAILABILITY | 0.88438 | 0.86853 | 0.44327 | 0.033644 | 0.10758 | 10.8461 | ok | 0.015113 | ok | 13575.7989 | 2.2626 | 0 | 6000 | 0 | 9 | 1 | 0.89062 | 4142.5 | 19.8 | 19.8 | 0.087767 | 0.86897 | 83 | 0.16247 | 1916.9031 | 123.8917 | 20.8403 | 39.5141 | 0.10809 | 0.12644 | 0.01776 | 0.12644 | 0.0095321 | 0.011265 | 0.0015073 | 0.011265 | 0.87719 | 0.87272 | 0.86742 | 0.8695 | 0.86543 | 0.86512 | 0.8637 | 2078.2323 | 1989.7475 | 1744.7475 | 2112.3232 | 2061.2121 | 1827.6263 | 1572.9798 | 1.1531 | 1.0761 | 0.96672 | 1.0494 | 1.3271 | 1.1182 | 0.86697 | PARTIAL_AVAILABILITY
61892 | Plumsted 537 LLC | NJ | PJM | Plumsted 537 LLC | Plumsted 537 LLC |  |  | FALSE |  | LIB | CS |  | 19.8 | 19.8 | 1 | <1.5h | 2019 | 463 | B | UNDER_DISPATCH | 0.87781 | 0.87612 | 0.04984 | 0.034776 | -0.055184 | -17.0144 | ok | 0.015446 | ok | 12567.5253 | 2.0946 | 0 | 6000 | 0 | 3 | 1 | 0.87274 | 10233.253 | 19.8 | 19.8 | 0.0098683 | 0.87577 | 82 | 0.0065055 | 2042.1315 | 131.9854 | 22.2017 | 42.0955 | 0.10809 | 0.12644 | 0.01776 | 0.12644 | 0.0095321 | 0.011265 | 0.0015073 | 0.011265 | 0.8799 | 0.87033 | 0.86926 | 0.87248 | 0.87409 | 0.87962 | 0.88657 | 2071.7172 | 1949.899 | 1742.8283 | 1910.9091 | 1874.0404 | 1338.5354 | 1679.596 | 1.1594 | 1.0768 | 1.0703 | 0.98006 | 1.3862 | 0.84697 | 0.98734 | PARTIAL_AVAILABILITY
61901 | Redstone Arsenal Hybrid | AL | TVA | Regions Bank | MN8 Energy LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Arbitrage | 1 | 2 | 2 | 1.5-2.5h | 2017 | 260 | C | FULL_OUTAGE | 0.8678 | 0.81458 | 0.12579 | -0.00083071 |  |  | insufficient_history | 0.04498 | ok | 967.375 | 0.16123 | 0.83877 | 6000 | 0 | 25 | 1 | 0.86154 | 87.5 | 0.5 | 0.5 | 0.0012579 | 0.84808 | 10 | 0.98492 | 0 | 0 | 0 | 0 | 0.27826 | 0.093193 | 0.069605 | 0.0011993 | 0.027174 | 0.0081522 | 0.0062438 | 0.0001 | 0.86035 | 0.86093 | 1.2029 | 0.8494 | 0.84526 |  |  | 172.5 | 130 | 83 | 141 | 254 | 0 | 0 | 2.9673 | 2.0417 | 0.36682 | 0.63025 | 0.6979 | 0 | 0 | FULL_OUTAGE
61909 | Parkview Battery | MI | MISO | Consumers Energy Co - (MI) | Consumers Energy Co - (MI) |  |  | FALSE |  | LIB | CS |  | 1.1 | 1 | 0.90909 | <1.5h | 2018 |  |  | UNDER_DISPATCH |  | 0.39608 |  |  |  |  | insufficient_history | -2.3383 | ok | 402.6667 | 0.067111 | 0.93289 | 6000 | 0 | 0 | 1 | 0.67857 | 1188.9624 | 1.1 | 1.1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | 0.81679 | 0.52121 | 0.47771 | 0.073171 | 0.2 | 0.44275 | 0.22368 | 107 | 86 | 75 | 3 | 21 | 58 | 17 | 0.074648 | 0.051643 | 0.06337 | 0.0037362 | 0.008018 | 0.058299 | 0
61913 | Punkin Center Battery Storage | AZ | AZPS | Arizona Public Service Co | Arizona Public Service Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Backup Power | 2 | 8 | 4 | 2.5-4.5h | 2018 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2 | 2
61923 | ACUA | NJ | PJM | Viridity Energy Solutions, Inc. | Viridity Energy Solutions, Inc. |  |  | FALSE |  | LIB | CS |  | 1 | 1 | 1 | <1.5h | 2018 | 251 | A | UNATTRIBUTED | 0.79686 | 0.78696 | 0.30477 | 0.0029773 | 17.6598 | 5.4953 | ok | -0.055388 | ok | 10229.4167 | 1.7049 | 0 | 6000 | 0 | 3 | 1 | 0.89767 | 144.4117 | 1 | 1 | 0.0030477 | 0.86646 | 30 | 0.11268 | 88.8492 | 5.7424 | 1.0429 | 1.8315 | 0.10809 | 0.12644 | 0.019147 | 0.12644 | 0.0095321 | 0.011265 | 0.0016274 | 0.011265 | 0.93386 | 0.5284 | 0.91808 | 0.92663 | 0.606 | 0.90319 | 0.92254 | 1991 | 800 | 1782 | 1945 | 283 | 933 | 1334 | 1.0308 | 0.42123 | 0.96151 | 0.9522 | 0.16191 | 0.21572 | 0.78102 | LOW_ETA_AND_LOW_UTI
61925 | Casa Mesa Wind Energy Center Hybrid | NM | PNM | Casa Mesa Wind, LLC | Casa Mesa Wind, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 1 | 1 | 1 | <1.5h | 2018 | 237 | A | THERMAL_AUX | 0.69984 | 0.62707 | 0.31447 | 0.0020338 | 1.6812 | 33.9303 | ok | 0 | ok | 1361.1667 | 0.22686 | 0.77314 | 6000 | 0 | 6 | 1 | 0.70909 | 145.3768 | 1 | 1 | 0.0031447 | 0.64993 | 73 | 0.28412 | 4.6417 | 0.19527 | 0.23661 | 0.068506 | 0.15519 | 0.12167 | 0.1109 | 0.13299 | 0.014054 | 0.010811 | 0.01042 | 0.011892 | 0.69184 | 0.64537 | 0.69388 | 0.65937 | 0.60453 | 0.58333 | 0.41844 | 229 | 202 | 238 | 271 | 240 | 84 | 59 | 0.18465 | 0.11232 | 0.20103 | 0.32843 | 0.38603 | 0.18347 | 0.14686 | THERMAL_AUX
61956 | MCRD Parris Island PV Hybrid | SC | SCEG | MCRD Parris Island / U.S. Marine Corps | Ameresco Federal Solutions |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving, Backup Power | 4 | 8 | 2 | 1.5-2.5h | 2018 | 445 | C | HYBRID_ARTEFACT | 0.77141 | 0.70733 | 0.12559 | 0.0018315 | -2.0607 | -7.2781 | ok | 2.6732 | ok | 1846.1042 | 0.30768 | 0.69232 | 6000 | 0 | 2 | 1 | 1.0075 | 5.728 | 4 | 4 | 0.0050236 | 0.76893 | 34 | 0.22418 | 45.8715 | 0.75258 | 0.72465 | 0.0029444 | 0.27826 | 0.093193 | 0.069605 | 0.0011993 | 0.027174 | 0.0081522 | 0.0062438 | 0.0001 | 1 | 5.6631 | 5.4366 | 0.76167 | 0.75806 | 0.78417 | 0.73876 | 577.25 | 529.5 | 386 | 59.125 | 76.375 | 104 | 65.75 | 0.41432 | 0.33434 | 0.32712 | 0.25519 | 0.31983 | 0.3756 | 0.12778 | LOW_ETA_AND_LOW_UTI
61990 | TAC-Distributed Energy Resource Hybrid | IL | MISO | Bank of the West | Ameren Illinois |  |  | TRUE | pv_same_plant | LIB | CT | Load Following, Load Management, Excess Wind and Solar Generation | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2017 | 331 | C | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 74.6667 | 0.012444 | 0.98756 | 6000 | 0 | 18 | 1 | 0.18721 | 0 | 0.3 | 0.3 |  |  |  |  | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | 0.14286 | 0.11111 | 0.076923 | 0.55769 | 0.018519 |  | 0 | 4 | 2 | 2 | 58 | 2 | 0 | 0 | 0.8 | 0 | 0.067193 | 0.2534 | 0 | 0 | 0 | FULL_OUTAGE
61993 | Gavilan Community College Solar Project | CA | CISO | SolarStorage Fund C, LLC | Gavilan District College Solar Project |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.5 | 0.5 | 1 | <1.5h | 2019 |  |  | HEALTHY | [8 empty] | insufficient_history | 124 | 0.020667 | 0.97933 | 6000 | 0 | 0 | 1.5 | 0.83 | 0 | 0.2 | 0.3 | [16 empty] | RTE_2021: 0.86111; EFC_2021: 124; UTI_2021: 0.17835
61995 | UC Merced Solar Hybrid | CA | CISO | Regions Bank | MN8 Energy LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | System Peak Shaving | 0.5 | 0.9 | 1.8 | 1.5-2.5h | 2018 | 257 | C | HYBRID_ARTEFACT | 0.8232 | 0.62331 | 1.1152 | -0.00031625 |  |  | insufficient_history | -0.15376 | ok | 774.7222 | 0.12912 | 0.87088 | 6000 | 0 | 17 | 1 | 0.65593 | 35.5 | 0.5 | 0.5 | 0.005576 | 0.60927 | 19 | 0.31524 | 0 | 0 | 0 | 0 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | 0.70714 | 0.9798 | 1.575 | 0.64865 | 0.6359 | 0.56075 |  | 110 | 107.7778 | 210 | 133.3333 | 137.7778 | 66.6667 | 0 | 1.8234 | 1.6267 | 0.94097 | 0.4947 | 0.44074 | 0.20802 | 0 | LOW_ETA_AND_LOW_UTI
62027 | Caldwell Wastewater Treatment Plant Hybr | NJ | PJM | Caldwell Wastewater Treatment Plant | Caldwell Wastewater Treatment Plant |  |  | TRUE | colocated_firming,pv_same_plant | OTH | CS | Arbitrage, Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving, Voltage or Reactive Power Support | 1 | 2 | 2 | 1.5-2.5h | 2016 | 444 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 1797.625 | 0.2996 | 0.7004 | 6000 | 0 | 36 | 1 | 0.95692 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.17285 | 0.10762 | 0.027963 | 0.1884 | 0.015814 | 0.0094887 | 0.0023987 | 0.017396 | 0.93629 | 0.96042 | [5 empty] | 433.5 | 461 | 0 | 0 | 0 | 0 | 0 | 7.9359 | 7.1534 | 0 | 0 | 0 | 0 | 0 | FULL_OUTAGE
62147 | KCE NY 1 | NY | NYIS | KCE NY 1, LLC | KCE NY 1, LLC |  |  | FALSE |  | LIB | CS |  | 20 | 8.4 | 0.42 | <1.5h | 2019 | 207 | A | PARTIAL_AVAILABILITY | 0.87338 | 0.88162 | -0.12982 | -0.0020459 | -0.33473 | 29.3536 | ok | -0.039579 | ok | 14062.8571 | 2.3438 | 0 | 6000 | 0 | 5 | 1 | 0.89335 | 2854.4495 | 20 | 20 | -0.025964 | 0.88117 | 34 | 0.032545 | 1939.2844 | 86.612 | 49.809 | 59.1945 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | 0.87807 | 0.86264 | 0.86836 | 0.88124 | 0.88668 | 0.88392 | 0.87446 | 1572.381 | 1189.5238 | 1649.0476 | 1932.0238 | 2244.881 | 2600 | 2875 | 1.4865 | 0.69985 | 1.4689 | 2.5392 | 4.2968 | 6.1739 | 8.8938 | PARTIAL_AVAILABILITY
62175 | Diablo Energy Storage | CA | CISO | Diablo Energy Storage, LLC | Diablo Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve | 200 | 800 | 4 | 2.5-4.5h | 2022 | 62 | A | THERMAL_AUX | 0.86028 | 0.84536 | 0.22198 | 1.405 | -3.5545 | -40.9073 | ok | -0.27051 | ok | 891.1838 | 0.14853 | 0.85147 | 6000 | 0 | 2 | 1 | 0.87012 | 32066.805 | 200 | 200 | 0.44396 | 0.84739 | 45 | 0.043362 | 3308.1947 | 1326.7345 | 4228.6349 | 442.3839 | 0.03025 | 0.20169 | 0.36118 | 0.20982 | 0.0025597 | 0.018771 | 0.047589 | 0.019625 | RTE_2022: 0.83116; RTE_2023: 0.8481; RTE_2024: 0.84993; RTE_2025: 0.85377; EFC_2022: 146.2937; EFC_2023: 249.8363; EFC_2024: 233.11; EFC_2025: 261.9438; UTI_2022: 0.65733; UTI_2023: 0.87713; UTI_2024: 0.89054; UTI_2025: 0.90631 | THERMAL_AUX
62219 | Ashburnham Energy Storage Project | MA | ISNE | Massachusetts Mun Wholes Electric Co | Massachusetts Mun Wholes Electric Co |  |  | TRUE | rte_gt_1 | LIB | CT |  | 3 | 3 | 1 | <1.5h | 2019 |  |  | HYBRID_ARTEFACT | 0.92083 | 0.8425 | 0.11008 | 0.0050073 | -4.9584 | -116.5311 | ok | -1.3987 | ok | 522.3333 | 0.087056 | 0.91294 | 6000 | 0 | 0 | 1 | 0.98131 | 0 | 3 | 3 | 0.0033025 | 0.86486 | 36 | 0.12027 | 18.8314 | 0.34328 | 0.64953 | 0.65692 | 0.14606 | 0.051271 | 0.073289 | 0.27079 | 0.013158 | 0.004386 | 0.006601 | 0.026316 | 0.97115 | 0.97674 | 0.53465 | 0.55518 | 0.82828 | 0.88017 | 0.87671 | 33.6667 | 70 | 54 | 55.3333 | 82 | 142 | 85.3333 | 0.029036 | 0.044708 | 0.058401 | 0.082893 | 0.1555 | 0.32241 | 0.17089
62235 | Lone Star Solar | SC | SCEG | Lone Star Solar | Lone Star Solar |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 66 | 198 | 3 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.96803 | 0.92809 | 0.14628 | 0.027048 |  |  | insufficient_history |  | insufficient_history | 121.3636 | 0.020227 | 0.97977 | 6000 | 0 | 0 | 1 | 0.93457 | 0 | 66 | 66 | 0.096543 | 0.93121 | 13 | 0.38251 | 846.7583 | 46.3075 | 27.7796 | 66.462 | 0.081309 | 0.081309 | 0.038862 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033722 | 0.031802 | RTE_2024: 0.85059; RTE_2025: 0.93455; EFC_2024: 4.399; EFC_2025: 116.9646; UTI_2024: 0.19665; UTI_2025: 0.36007
62241 | NorWest Energy 9 LLC | OR | PACW | NorWest Energy 9, LLC | Radian Generation |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
62248 | Arrow Canyon Solar Hybrid | NV | NEVP | Arrow Canyon Solar LLC | Arrow Canyon Solar LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | Excess Wind and Solar Generation | 75 | 375 | 5 | >4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.82669 | 0.88182 | -1.0857 | 0.68059 | 15.6296 | 224.6737 | ok | 0.74468 | ok | 560.288 | 0.093381 | 0.90662 | 6000 | 5 | 0 | 1 | 0.89679 | 0 | 40 | 40 | -0.8143 | 0.87848 | 25 | 0.12019 | 64.0806 | 395.2372 | 4.4057 | 126.0573 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2023: 0.86358; RTE_2024: 0.88434; RTE_2025: 0.87367; EFC_2023: 15.176; EFC_2024: 269.192; EFC_2025: 275.92; UTI_2024: 2.5814; UTI_2025: 2.2481
62257 | Station 9 Energy Storage System | MA | ISNE | Braintree BESS 1 LLC | Town of Braintree - (MA) |  |  | FALSE |  | LIB | CS |  | 2 | 4.2 | 2.1 | 1.5-2.5h | 2018 |  |  | UNDER_DISPATCH | 0.93403 | 0.75908 | 0.34473 | 0.0018218 | 0.21588 | -96.2059 | ok | -0.050957 | ok | 464.0278 | 0.077338 | 0.92266 | 6000 | 0 | 0 | 1 | 0.81818 | 818.3736 | 2 | 2 | 0.0068946 | 0.78231 | 36 | 0.40427 | 30.1209 | 0.47064 | 0.013372 | 0.75054 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 0.76557 | 0.82707 | 0.70058 | 0.70349 | 0.6609 | 0.74611 | 0.9209 | 49.7619 | 78.5714 | 57.381 | 57.619 | 45.4762 | 68.5714 | 77.619 |  | 1.344 | 0.26025 | 0.25543 | 0.25244 | 0.98918 | 0.85473
62373 | I25 Battery Storage | CO | WACM | United Power, Inc | United Power, Inc |  |  | FALSE |  | LIB | CS |  | 4 | 16 | 4 | 2.5-4.5h | 2018 | 252 | A | THERMAL_AUX | 0.84071 | 0.73928 | 0.26018 | -0.0032046 | -3.2549 | 92.8285 | ok | -1.585 | ok | 2899.7188 | 0.48329 | 0.51671 | 6000 | 0 | 0 | 1 | 0.88375 | 134.1312 | 4 | 4 | 0.010407 | 0.87126 | 61 | 0.23284 | 0 | 0 | 0 | 0 | 0.048771 | 0.27747 | 0.069501 | 0.0011993 | 0.0041667 | 0.027083 | 0.0062338 | 0.0001 | 0.83115 | 0.86073 | 0.74804 | 0.70423 | 0.55631 | 0.87935 | 0.0086957 | 63.375 | 51.375 | 47.6875 | 50 | 20.375 | 2661.5625 | 0.0625 | 0.29325 | 0.32772 | 0.23907 | 0.17508 | 0.064811 | 10.0926 | 0 | THERMAL_AUX
62381 | GMP Solar/Storage-Milton Hybrid | VT | ISNE | GMP VT Microgrid LLC | Green Mountain Power Corp |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | OT | Arbitrage, Frequency Regulation | 2 | 8 | 4 | 2.5-4.5h | 2019 |  |  | HYBRID_ARTEFACT | 2.313 | 0.6203 | -0.057816 | -0.0044729 |  |  | ok | -2.3985 | ok | 671.125 | 0.11185 | 0.88815 | 6000 | 1 | 0 | 1 | 1.0498 | 0 | 2 | 2 | -0.0011563 | 2.411 | 61 | 0.00015433 | 38.4349 | 3.1529 | 0.047433 | 0.012034 | 0.064667 | 0.095415 | 0.0011985 | 0.0011993 | 0.005571 | 0.0083565 | 0.0001 | 0.0001 | 0.23529 | 0.084937 | 2.0411 | 10.8641 | 11.2805 | 4.1966 | 1 | 6 | 16 | 117.875 | 139.875 | 115.625 | 122.75 | 153 | 0.10055 | 0.042519 | 0.62509 | 0.43038 | 0.36759 | 0.58065 | 0.72864
62382 | GMP Solar/Storage-Ferrisburgh Hybrid | VT | ISNE | GMP VT Microgrid LLC | Green Mountain Power Corp |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | OT | Arbitrage, Frequency Regulation | 2 | 8 | 4 | 2.5-4.5h | 2019 | 411 | C | HYBRID_ARTEFACT | 2.158 | 0.62668 | -0.63736 | 0.0014565 |  |  | ok | -0.29872 | ok | 843.875 | 0.14065 | 0.85935 | 6000 | 1 | 2 | 1 | 0.99907 | 22 | 2 | 2 | -0.012747 | 2.2658 | 60 | 0.051875 | 37.6172 | 3.0858 | 0.046424 | 0.011777 | 0.064667 | 0.095415 | 0.0011985 | 0.0011993 | 0.005571 | 0.0083565 | 0.0001 | 0.0001 | 5 | 0.069153 | 1.6837 | 16.197 | 13.2987 | 4.2459 | 1 | 25.625 | 12.75 | 264.125 | 133.625 | 128 | 129.5 | 150.25 | 0.42943 | 0.039627 | 0.72267 | 0.33249 | 0.40499 | 0.60815 | 0.74073 | PARTIAL_AVAILABILITY
62383 | GMP Solar/Storage-Essex Hybrid | VT | ISNE | GMP VT Microgrid LLC | Green Mountain Power Corp |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | OT | Arbitrage, Frequency Regulation | 2 | 8 | 4 | 2.5-4.5h | 2019 |  |  | HYBRID_ARTEFACT | 1.5696 | 0.62226 | -0.8625 | -0.0034224 |  |  | ok | -1.6325 | ok | 813.375 | 0.13556 | 0.86444 | 6000 | 1 | 0 | 1 | 6.0055 | 0 | 2 | 2 | -0.01725 | 2.4102 | 60 | 0.031913 | 43.1371 | 3.5386 | 0.053236 | 0.013506 | 0.064667 | 0.095415 | 0.0011985 | 0.0011993 | 0.005571 | 0.0083565 | 0.0001 | 0.0001 | 5.8 | 0.08522 | 3.5018 | 4.2576 | 12.2338 | 2.3387 | 1 | 29 | 16 | 243.375 | 121.875 | 117.75 | 126 | 159.375 | 0.48599 | 0.065767 | 0.63169 | 0.37284 | 0.35624 | 0.5524 | 0.79426
62441 | Kearny Mesa Storage LLC | CA | CISO | Kearny Mesa Storage LLC | Kearny Mesa Storage LLC |  |  | TRUE | colocated_firming | LIB | CS | Backup Power | 1 | 1 | 1 | <1.5h | 2020 | 250 | C | HYBRID_ARTEFACT | 0.93928 | 0.9231 | 0.13094 | 0.0022839 | 6.004 | 291.7564 | ok | -0.11662 | ok | 1871 | 0.31183 | 0.68817 | 6000 | 0 | 2 | 1 | 0.96 | 38.5 | 1 | 1 | 0.0013094 | 0.92285 | 24 | 0.022855 | 106.7888 | 2.4334 | 0.024474 | 0.15522 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 | RTE_2020: 0.96526; RTE_2024: 0.92135; RTE_2025: 0.92456; EFC_2020: 639; EFC_2024: 656; EFC_2025: 576; UTI_2020: 1.0046; UTI_2024: 0.82525; UTI_2025: 1.0025 | PARTIAL_AVAILABILITY
62444 | Meyersdale Battery | PA | PJM | GlidePath Power Operations LLC | GlidePath Power Operations LLC |  |  | TRUE | rte_gt_1 | LIB | CT |  | 18 | 12.1 | 0.67222 | <1.5h | 2015 | 79 | C | HYBRID_ARTEFACT | 0.86145 | 0.82431 | 0.28079 | 0.17117 | 0.27323 | 18.7212 | ok | 0.016999 | ok | 20044.9656 | 3.3408 | 0 | 6000 | 0 | 2 | 1 | 0.86503 | 1232.5 | 18 | 18 | 0.050541 | 0.85542 | 79 | 0.1682 | 1381.0098 | 89.2563 | 14.9906 | 28.4675 | 0.10809 | 0.12644 | 0.017732 | 0.12644 | 0.0095321 | 0.011265 | 0.0015049 | 0.011265 | 0.86053 | 0.85644 | 0.86687 | 0.8864 | 0.81878 | 0.83911 | 0.84001 | 1694.9587 | 2114.1322 | 2356.9421 | 2658.7603 | 2167.6033 | 1916.281 | 1910.1653 | 1.1246 | 1.1985 | 1.3784 | 1.2672 | 1.4062 | 1.0574 | 0.8249 | PARTIAL_AVAILABILITY
62460 | DESI-2 Battery Storage Facility | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS |  | 1.4 | 3.7 | 2.6429 | 2.5-4.5h | 2019 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.4 | 1.4
62490 | Echo River Solar | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Transmission and Distribution Deferral, Excess Wind and Solar Generation | 30 | 75 | 2.5 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.88945 | 0.7778 | 0.31601 | -0.029388 | -4.544 | -79.562 | ok | 145.8866 | ok | 400.4267 | 0.066738 | 0.93326 | 6000 | 0 | 0 | 1 | 0.85175 | 0 | 30 | 30 | 0.094802 | 0.82913 | 33 | 0.57156 | 319.9536 | 29.1627 | 11.7367 | 0.071433 | 0.08949 | 0.14465 | 0.04759 | 0.0011993 | 0.0078125 | 0.013021 | 0.0041683 | 0.0001 | RTE_2022: 0.58824; RTE_2023: 0.83523; RTE_2024: 0.83859; RTE_2025: 0.79508; EFC_2022: 0.13333; EFC_2023: 145.1067; EFC_2024: 163.4133; EFC_2025: 91.7733; UTI_2022: 0.00058794; UTI_2023: 0.6246; UTI_2024: 0.69717; UTI_2025: 0.30482
62494 | Skeleton Creek Energy Center Hybrid | OK | SWPP | Skeleton Creek Energy Center | Skeleton Creek Energy Center |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Excess Wind and Solar Generation | 252 | 1008 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.82854 |  |  |  |  | insufficient_history |  | insufficient_history | 17.5863 | 0.0029311 | 0.99707 | 6000 | 0 | 0 | 1 | 0.86491 | 0 | 252 | 252 |  |  |  |  | 4597.392 | 251.4219 | 156.8876 | 360.8492 | 0.081309 | 0.081309 | 0.040359 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035078 | 0.031802 | RTE_2025: 0.85932; EFC_2025: 17.5863; UTI_2025: 0.37916
62497 | Orange County Energy Storage 2 | CA | CISO | Orange County Energy Storage 2, LLC | Convergent Energy and Power LP |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 9 | 36 | 4 | 2.5-4.5h | 2021 | 376 | B | FULL_OUTAGE |  | 0.80933 |  |  |  |  | insufficient_history |  | insufficient_history | 312.1806 | 0.05203 | 0.94797 | 6000 | 0 | 12 | 1 | 0.86011 | 5607.834 | 9 | 9 |  |  |  |  | 0 | 0 | 0 | 0 | 0.080762 | 0.20113 | 0.075292 | 0.25527 | 0.0070175 | 0.018713 | 0.0067964 | 0.024561 | RTE_2024: 0.8138; EFC_2024: 98.5833; EFC_2025: 0; UTI_2024: 0.35893; UTI_2025: 0 | FULL_OUTAGE
62499 | Orange County Energy Storage 3 | CA | CISO | Orange County Energy Storage 3, LLC | Convergent Energy and Power LP |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 6 | 24 | 4 | 2.5-4.5h | 2021 | 395 | B | FULL_OUTAGE |  | 0.84485 |  |  |  |  | insufficient_history |  | insufficient_history | 568.5486 | 0.094758 | 0.90524 | 6000 | 0 | 13 | 1 | 0.86872 | 2356.469 | 6 | 6 |  |  |  |  | 0 | 0 | 0 | 0 | 0.080762 | 0.20113 | 0.075292 | 0.25527 | 0.0070175 | 0.018713 | 0.0067964 | 0.024561 | RTE_2024: 0.84557; EFC_2024: 179.5417; EFC_2025: 0; UTI_2024: 0.90705; UTI_2025: 0 | FULL_OUTAGE
62529 | Hale Kuawehi Solar Hybrid | HI | HECO | Hale Kuawehi Solar LLC | Hale Kuawehi Solar LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Following | 30 | 30 | 1 | <1.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 30 | 30
62541 | Lake Placid Solar Power Plant | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Ramping / Spinning Reserve, Co-Located Renewable Firming | 17.3 | 36 | 2.0809 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.93299 | 0.90009 | 0.042065 | -0.0021738 | -1.4998 | -86.4219 | ok | 0.36734 | ok | 217.25 | 0.036208 | 0.96379 | 6000 | 0 | 1 | 1 | 0.96393 | 354 | 17.3 | 17.3 | 0.0072773 | 0.91912 | 32 | 0.36261 | 67.1034 | 22.0185 | 0.080737 | 3.5113 | 0.066273 | 0.3373 | 0.0011985 | 0.18593 | 0.0057143 | 0.034286 | 0.0001 | 0.017143 | RTE_2023: 0.9284; RTE_2024: 0.91835; RTE_2025: 0.90432; EFC_2023: 85; EFC_2024: 83.4167; EFC_2025: 48.8333; UTI_2023: 0.57685; UTI_2024: 0.27365; UTI_2025: 0.19106
62561 | Roadrunner, LLC Hybrid | TX | ERCO | Roadrunner Solar, LLC | Roadrunner Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 63.3 | 108.6 | 1.7156 | 1.5-2.5h | 2023 | 39 | C | FULL_OUTAGE |  | 0.7522 |  |  |  |  | insufficient_history |  | insufficient_history | 94.6685 | 0.015778 | 0.98422 | 6000 | 3 | 21 | 1 | 0.8203 | 4124.5 | 50 | 50 |  |  |  |  | 0 | 0 | 0 | 0 | 0.031828 | 0.092476 | 0.10197 | 0.404 | 0.0026954 | 0.0080863 | 0.0094837 | 0.043127 | RTE_2023: 0.73423; RTE_2024: 0.80197; EFC_2023: 59.5028; EFC_2024: 35.1657; EFC_2025: 0; UTI_2023: 0.61588; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
62562 | High Lonesome Wind Power, LLC Hybrid | TX | ERCO | High Lonesome Wind Power, LLC | High Lonesome Wind Power, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 63.3 | 81 | 1.2796 | <1.5h | 2023 | 28 | A | FULL_OUTAGE | 0.86398 | 0.76907 | 0.40314 | 0.20481 |  |  | insufficient_history |  | insufficient_history | 223.2222 | 0.037204 | 0.9628 | 6000 | 3 | 18 | 1 | 0.79686 | 6489.9194 | 51.1 | 51.1 | 0.25519 | 0.77521 | 13 | 0.29777 | 0 | 0 | 0 | 0 | 0.010638 | 0.052071 | 0.19005 | 0.46223 | 0.00089127 | 0.0044563 | 0.019642 | 0.051693 | RTE_2023: 0.74151; RTE_2024: 0.80628; EFC_2023: 102.4198; EFC_2024: 120.8025; EFC_2025: 0; UTI_2023: 1.0022; UTI_2024: 0.3209; UTI_2025: 0 | FULL_OUTAGE
62564 | Elkhorn Battery Energy Storage System | CA | CISO | Pacific Gas & Electric Co. | Pacific Gas & Electric Co. |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 182.5 | 730 | 4 | 2.5-4.5h | 2022 |  |  | UNDER_DISPATCH | 0.87699 | 0.83198 | 0.21031 | -0.1686 | -1.8848 | -97.4309 | ok | -0.45289 | ok | 443.0589 | 0.073843 | 0.92616 | 6000 | 0 | 0 | 1 | 0.87691 | 396299.5196 | 182.5 | 182.5 | 0.38381 | 0.85657 | 32 | 0.80241 | 0 | 0 | 0 | 0 | 0.03025 | 0.20169 | 0.099346 | 0.20982 | 0.0025597 | 0.018771 | 0.0092124 | 0.019625 | RTE_2022: 0.85185; RTE_2023: 0.85159; RTE_2024: 0.86011; RTE_2025: 0.77773; EFC_2022: 95.5397; EFC_2023: 152.3397; EFC_2024: 184.5096; EFC_2025: 10.6699; UTI_2022: 0.41191; UTI_2023: 0.52237; UTI_2024: 0.70462; UTI_2025: 0
62569 | Knoxville Battery Energy Storage | IA | MISO | MidAmerican Energy Co | MidAmerican Energy Co |  |  | FALSE |  | LIB | CS |  | 1.1 | 4 | 3.6364 | 2.5-4.5h | 2018 |  |  | CAPACITY_FADE | [7 empty] | -8.3853 | ok | 343.75 | 0.057292 | 0.94271 | 6000 | 1 | 0 | 1 | 0.86438 | 80.6747 | 1.1 | 1.1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.12376 | 0.14367 | 0.0056108 | 0.12376 | 0.01101 | 0.012925 | 0.00047026 | 0.01101 | 0.87123 | 0.87553 | 0.79139 | 0.37975 | 0.058824 | 0 | 0 | 159 | 103.75 | 59.75 | 7.5 | 0.5 | 0 | 0 | 0.71558 | 0.6265 | 0.2771 | 0.029431 | 0 | 0 | 0
62579 | Plainfield Community Solar LLC | MA | ISNE | Plainfield Solar LLC | Plainfield Solar LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CT | Co-Located Renewable Firming, Excess Wind and Solar Generation | 1 | 1 | 1 | <1.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
62585 | Beebe Substation Battery Storage | MA | ISNE | Massachusetts Mun Wholes Electric Co | Massachusetts Mun Wholes Electric Co |  |  | FALSE |  | LIB | CT |  | 3 | 3 | 1 | <1.5h | 2019 |  |  | UNDER_DISPATCH | 0.9757 | 0.83197 | 0.16971 | 0.0012548 |  |  | ok | 2.1722 | ok | 427 | 0.071167 | 0.92883 | 6000 | 0 | 0 | 1 | 0.98182 | 3935.4699 | 3 | 3 | 0.0050912 | 0.86313 | 34 | 0.28897 | 15.9343 | 0.29047 | 0.5496 | 0.55586 | 0.14606 | 0.051271 | 0.073289 | 0.27079 | 0.013158 | 0.004386 | 0.006601 | 0.026316 | 0.72222 | 0.66667 | 0.70732 | 0.69507 | 0.79937 | 0.91241 | 0.85317 | 30.3333 | 5.3333 | 58 | 51.6667 | 85 | 125 | 71.6667 | 0.026163 | 0.0034038 | 0.062726 | 0.077403 | 0.13781 | 0.24035 | 0.13447
62604 | Outer Cape Community Battery | MA | ISNE | Eversource | Eversource |  |  | FALSE |  | LIB | BL | System Peak Shaving, Voltage or Reactive Power Support | 25 | 38 | 1.52 | 1.5-2.5h | 2022 |  |  | UNDER_DISPATCH | 0.88863 | 0.79606 | 0.0081636 | -5.989e-05 |  |  | ok | 5.0417 | ok | 45.4211 | 0.0075702 | 0.99243 | 6000 | 0 | 1 | 2.5 | 0.80833 | 22030.3011 | 10 | 25 | 0.0020409 | 0.88883 | 31 | 0.082616 | 73.639 | 1.7259 | 0.66059 | 0.55047 | 0.17028 | 0.076884 | 0.023765 | 0.076884 | 0.015556 | 0.0066667 | 0.0020296 | 0.0066667 | RTE_2022: 0.60204; RTE_2023: 0.58416; RTE_2024: 0.93218; RTE_2025: 0.92481; EFC_2022: 3.1053; EFC_2023: 1.5526; EFC_2024: 21.3421; EFC_2025: 19.4211; UTI_2022: 0.011574; UTI_2023: 0.0054814; UTI_2024: 0.11632; UTI_2025: 0.12391
62609 | Commerce ESS | TX | ERCO | City of San Antonio - (TX) | City of San Antonio - (TX) |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 10 | 10 | 1 | <1.5h | 2019 | 428 | B | UNDER_DISPATCH | 0.96341 | 0.64967 | 0.94758 | 0.01083 | -2.6406 | -28.707 | ok | -0.13678 | ok | 1076.1 | 0.17935 | 0.82065 | 6000 | 8 | 4 | 1 | 0.78063 | 31287.0529 | 10 | 10 | 0.094758 | 0.66804 | 71 | 0.77061 | 111.5167 | 9.1479 | 0.078971 | 7.7804 | 0.10997 | 0.16034 | 0.0011985 | 0.3725 | 0.0097087 | 0.014563 | 0.0001 | 0.038835 | 0.68817 | 0.6286 | 0.62955 | 0.64429 | 0.65274 | 0.67848 | 0.72663 | 12.8 | 135.4 | 171.3 | 176.6 | 181.2 | 181.9 | 216.9 | 0 | 0.11957 | 0.25545 | 0.38187 | 0.29203 | 0.29268 | 0.36626 | FULL_OUTAGE
62617 | Searcy Solar Hybrid | AR | MISO | Searcy Solar, LLC | Searcy Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving | 10 | 30 | 3 | 2.5-4.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
62644 | Minuteman Energy Storage | MA | ISNE | Minuteman Energy Storage, LLC | Minuteman Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Load Management | 5 | 10 | 2 | 1.5-2.5h | 2019 |  |  | UNDER_DISPATCH | 0.86724 | 0.75967 | 0.20169 | -0.00048613 | -3.2729 | -16.0083 | ok | 0.077902 | ok | 391.2 | 0.0652 | 0.9348 | 6000 | 0 | 0 | 1 | 0.65625 | 4716.0112 | 5 | 5 | 0.010084 | 0.76481 | 80 | 0.29365 | 48.3071 | 0.7548 | 0.021446 | 1.2037 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 0.82618 | 0.79765 | 0.78756 | 0.79152 | 0.75425 | 0.67702 | 0.76 | 40.4 | 61.1 | 60.8 | 65.3 | 48.8 | 65.4 | 49.4 |  | 0.91083 | 0.19706 | 0.23487 | 0.27657 | 0.92283 | 0.58623
62652 | Happy Hollow CSG Hybrid | MA | ISNE | Happy Hollow Solar Holdings, LLC | REA Investments, LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | Ramping / Spinning Reserve, Excess Wind and Solar Generation | 3.3 | 6.6 | 2 | 1.5-2.5h | 2019 | 282 | C | HYBRID_ARTEFACT | 0.92772 | 0.84169 | 0.45531 | 0.0012837 | 0.66435 | 6.3046 | ok |  | insufficient_history | 390.4545 | 0.065076 | 0.93492 | 6000 | 0 | 2 | 1 | 0.86982 | 11.5 | 3.3 | 3.3 | 0.015025 | 0.84714 | 24 | 0.90546 | 111.9589 | 1.7494 | 0.049704 | 2.7897 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | RTE_2024: 0.85484; RTE_2025: 0.83772; EFC_2024: 216.8182; EFC_2025: 173.6364; UTI_2024: 2.6143; UTI_2025: 2.1691 | PARTIAL_AVAILABILITY
62682 | Noland Wastewater Treatment Plant Hybrid | AR | SWPP | Today's Power, Inc. | Today's Power, Inc. |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | BL | Excess Wind and Solar Generation | 6 | 13.1 | 2.1833 | 1.5-2.5h | 2019 | 348 | C | HYBRID_ARTEFACT | 0.64232 | 0.56556 | 0.020818 | 0.0013534 | 2.4601 | -286.0648 | ok |  | insufficient_history | 151.2977 | 0.025216 | 0.97478 | 6000 | 0 | 4 | 1 | 0.79221 | 0 | 6 | 6 | 0.0012491 | 0.67287 | 35 | 0.042184 | 0 | 0 | 0 | 0 | 0.27826 | 0.093193 | 0.055787 | 0.0011993 | 0.027174 | 0.0081522 | 0.0049295 | 0.0001 | 0.72603 | 0.51852 | 0.5838 | 0.68333 | 0.63382 | 0.4632 | 0.16427 | 24.2748 | 21.374 | 23.6641 | 25.0382 | 32.9008 | 19.6947 | 4.3511 | 0.088972 | 0.04283 | 0.020517 | 0.017218 | 0.02664 | 0.012037 | 0 | LOW_ETA_AND_LOW_UTI
62683 | Westside Wastewater Treatment Plant Hybr | AR | SWPP | Today's Power, Inc. | Today's Power, Inc. |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | BL | Excess Wind and Solar Generation | 6 | 13.1 | 2.1833 | 1.5-2.5h | 2019 | 266 | C | HYBRID_ARTEFACT | 0.69519 | 0.62122 | 0.038321 | 0.0021971 |  |  | ok |  | insufficient_history | 158.855 | 0.026476 | 0.97352 | 6000 | 0 | 5 | 1 | 0.80102 | 28.5 | 6 | 6 | 0.0022993 | 0.70425 | 31 | 0.049259 | 0 | 0 | 0 | 0 | 0.27826 | 0.093193 | 0.055787 | 0.0011993 | 0.027174 | 0.0081522 | 0.0049295 | 0.0001 | 0.76509 | 0.5175 | 0.59199 | 0.69489 | 0.67473 | 0.47007 | 0.048 | 27.0992 | 21.4504 | 24.8092 | 30.0763 | 38.3206 | 16.1832 | 0.91603 | 0.36318 | 0.056549 | 0.017952 | 0.020754 | 0 | 0.0087658 | 0 | LOW_ETA_AND_LOW_UTI
62695 | CED Northampton Solar LLC Hybrid | MA | ISNE | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 2.3 | 4.9 | 2.1304 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.8787 | 0.87434 | 0.03786 | -0.0068834 | -4.0579 | -100.5053 | ok |  | insufficient_history | 297.3469 | 0.049558 | 0.95044 | 6000 | 0 | 0 | 1 | 0.90099 | 0 | 2 | 2 | 0.00087079 | 0.88903 | 24 | 0.089652 | 18.0582 | 0.54865 | 0.19144 | 0.052496 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  | 0.625 |  |  | 0.87902 | 0.87324 | 0.87736 |  | 3.0612 | 0 | 0 | 117.1429 | 101.2245 | 75.9184 |  | 0.77385 | 0 | 0 | 0.64481 | 0.96481 | 0.46987
62714 | Eyak Service Center BESS | AK |  | Cordova Electric Coop, Inc | Cordova Electric Coop, Inc |  |  | FALSE |  | LIB | CS | Load Following, Ramping / Spinning Reserve, System Peak Shaving, Load Management, Voltage or Reactive Power Support | 1 | 0.9 | 0.9 | <1.5h | 2019 | 213 | A | UNATTRIBUTED | 0.58822 | 0.48518 | 0.10686 | -0.00036725 | -10.1328 | -137.0129 | ok | 1.2019 | ok | 481.1111 | 0.080185 | 0.91981 | 6000 | 0 | 0 | 1 | 0.8 | 152.8483 | 1 | 1 | 0.0010686 | 0.60628 | 28 | 0.12882 | 11.3464 | 0.47732 | 0.16051 | 0.16746 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 |  | 0.44961 | 0.46203 | 0.35537 | 0.50658 | 0.48718 | 0.60504 |  | 64.4444 | 81.1111 | 47.7778 | 85.5556 | 42.2222 | 160 |  | 0.040452 | 0.06745 | 0.058121 | 0.12177 | 0.10042 | 0.45163 | LOW_ETA_AND_LOW_UTI
62733 | East Hampton Energy Storage Center | NY | NYIS | East Hampton Energy Storage Center, LLC | East Hampton Energy Storage Center, LLC |  |  | FALSE |  | LIB | BL | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 5 | 40 | 8 | >4.5h | 2018 | 412 | A | UNDER_DISPATCH | 0.94622 | 0.83592 | 0.32832 | -0.0005403 |  |  | ok | 1.8166 | ok | 848.9354 | 0.14149 | 0.85851 | 6000 | 0 | 10 | 1 | 0.93407 | 4150.1366 | 5 | 5 | 0.016416 | 0.93002 | 11 | 0.80375 | 22.2407 | 1.3379 | 0.012615 | 0.31034 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | 0.91318 | 0.954 | 0.95034 | 0.90258 | 0.92907 | 0.9264 | 0.9198 | 125.425 | 151.925 | 150.225 | 147.775 | 26.525 | 88.425 | 106.375 | 2.4093 | 1.0355 | 1.2487 |  | 0 | 0 | 0.04214 | FULL_OUTAGE
62734 | Montauk Energy Storage Center | NY | NYIS | Montauk Energy Storage Center, LLC | Montauk Energy Storage Center, LLC |  |  | FALSE |  | LIB | BL | System Peak Shaving | 5 | 40 | 8 | >4.5h | 2019 | 34 | A | UNATTRIBUTED | 0.9171 | 0.79063 | 1.2182 |  |  |  | ok | -0.78921 | ok | 698.95 | 0.11649 | 0.88351 | 6000 | 0 | 2 | 1 | 0.88174 | 5206.6208 | 5 | 5 | 0.060909 | 0.87088 | 14 | 0.094964 | 0 | 0 | 0 | 0 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | 0.8082 | 0.88593 | 0.8486 | 0.92149 | 0.84509 | 0.83288 | 0.83516 | 75.425 | 105.625 | 106.775 | 139.675 | 87.15 | 106.4 | 77.9 | 1.5775 | 0.65969 | 0.85766 |  | 3.0337 | 0.011244 | 0 | ELEVATED_P_AUX
62745 | Wheatridge Hybrid | OR | BPAT | Wheatridge Wind Holdings, LLC | Wheatridge Wind Holdings, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 30 | 120 | 4 | 2.5-4.5h | 2022 | 407 | C | HYBRID_ARTEFACT | 0.74406 | 0.77943 | 0.081141 | -0.47896 | -10.5602 | 22.3372 | ok | 0.58097 | ok | 773.3083 | 0.12888 | 0.87112 | 6000 | 0 | 2 | 1 | 0.91176 | 1175 | 30 | 30 | 0.024342 | 0.74859 | 45 | 0.00022064 | 13.4752 | 234.165 | 29.4708 | 17.5729 | 0.0011993 | 0.31703 | 0.036741 | 0.085813 | 0.0001 | 0.031776 | 0.003181 | 0.0074766 | RTE_2022: 0.95698; RTE_2023: 0.84179; RTE_2024: 0.70181; RTE_2025: 0.6212; EFC_2022: 148.5; EFC_2023: 200.15; EFC_2024: 235.45; EFC_2025: 189.2083; UTI_2022: 0.72352; UTI_2023: 0.79563; UTI_2024: 0.9707; UTI_2025: 0.63828 | LOW_ETA_AND_LOW_UTI
62753 | Prospect Storage | TX | ERCO | GlidePath Power Operations LLC | GlidePath Power Operations LLC |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage, Frequency Regulation | 9.9 | 10 | 1.0101 | <1.5h | 2020 | 350 | C | HYBRID_ARTEFACT | 1.294 | 0.48047 | 0.38447 | -0.00028034 | -1.1118 | 11.1889 | ok | 1.0199 | ok | 161.1 | 0.02685 | 0.97315 | 6000 | 3 | 6 | 1 | 0.7037 | 88 | 9.9 | 9.9 | 0.038063 | 0.54501 | 54 | 0.74736 | 4.6847 | 0.9394 | 0.41806 | 0.13619 | 0.053242 | 0.18177 | 0.066215 | 0.087152 | 0.0045593 | 0.016717 | 0.0059177 | 0.0075988 |  | 0.60082 | 0.58575 | 0.53311 | 0.54778 | 0.42048 | 0.32018 |  | 29.2 | 22.2 | 31.4 | 40.7 | 23 | 14.6 |  | 0.01875 | 0.026708 | 0.073031 | 0.050941 | 0.036469 | 0.037973 | FULL_OUTAGE
62754 | San Diego International Airport BESS | CA | CISO | Critical Loop, Inc. | Critical Loop, Inc. |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 2 | 4 | 2 | 1.5-2.5h | 2021 | 340 | B | FULL_OUTAGE |  | 0.86271 |  |  |  |  | insufficient_history |  | insufficient_history | 97.7292 | 0.016288 | 0.98371 | 6000 | 0 | 12 | 1 | 0.824 | 447.8573 | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.095923 | 0.18264 | 0.10676 | 0.14038 | 0.0084034 | 0.016807 | 0.0099838 | 0.012605 | RTE_2024: 0.68; RTE_2025: 0.87766; EFC_2024: 4.25; EFC_2025: 82.5; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
62801 | Vallecito | CA | CISO | Viridity Energy Solutions, Inc. | Viridity Energy Solutions, Inc. |  |  | FALSE |  | LIB | CS | Frequency Regulation | 10 | 10 | 1 | <1.5h | 2021 |  |  | CELL_DEGRADATION | 0.88121 | 0.84809 | 0.51598 | 0.0062962 | -4.1007 | -70.5698 | ok | 0.021551 | ok | 5684.1917 | 0.94737 | 0.052635 | 6000 | 0 | 0 | 1 | 0.85103 | 23.5961 | 10 | 10 | 0.051598 | 0.8504 | 24 | 0.472 | 1999.2625 | 45.5565 | 0.45818 | 2.906 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 | RTE_2024: 0.85231; RTE_2025: 0.84817; EFC_2024: 1191.7; EFC_2025: 1016.7; UTI_2024: 1.709; UTI_2025: 1.6836
62835 | Acushnet Ball Plant 2 | MA | ISNE | Acushnet Company | Acushnet |  |  | FALSE |  | LIB | CS | Frequency Regulation | 1.5 | 3 | 2 | 1.5-2.5h | 2019 | 182 | A | UNATTRIBUTED | 0.75316 | 0.81051 | -0.082435 | 0.00033876 | 6.1225 | -110.5905 | ok | 1.8445 | ok | 1747.6667 | 0.29128 | 0.70872 | 6000 | 0 | 14 | 1 | 0.67041 | 225.0616 | 1.5 | 1.5 | -0.0012365 | 0.7543 | 22 | 0.34893 | 6.8198 | 0.10656 | 0.0030277 | 0.16993 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | 0.67022 | 0.66819 | 0.85714 | 0.68196 | 0.7331 |  | 0.89313 | 1088.6667 | 195.3333 | 2 | 213 | 209.6667 | 0 | 39 | 30.9466 | 3.095 | 0.040217 | 0.94425 | 1.443 | 0 | 0.29345 | FULL_OUTAGE
62839 | 98th Street Battery Storage Station | NY | NYIS | Consolidated Edison Co-NY Inc | Consolidated Edison Co-NY Inc |  |  | TRUE | rte_gt_1 | LIB | CS |  | 2 | 10 | 5 | >4.5h | 2021 | 338 | C | HYBRID_ARTEFACT | 0.78195 | 0.46421 | 0.4773 |  |  |  | ok |  | insufficient_history | 93.5667 | 0.015594 | 0.98441 | 6000 | 0 | 0 | 1.5 | 0.63636 | 0 | 1 | 1.5 | 0.0095459 | 0.71466 | 10 | 0.67767 | 0 | 0 | 0 | 0 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 |  |  | 13.5455 | 10.1667 | 0.45517 | 0.63722 | 0.45988 |  |  | 12.4167 | 10.1667 | 11 | 45.0833 | 14.9 |  |  | 0.17545 | 0.072788 | 0.16422 | 0.0082994 | 0 | LOW_ETA_AND_LOW_UTI
62844 | Cranberry Point Energy Storage | MA | ISNE | Cranberry Point Energy Storage LLC | Cranberry Point Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 150 | 300 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.84369 |  |  |  |  | insufficient_history |  | insufficient_history | 177.91 | 0.029652 | 0.97035 | 6000 | 0 | 0 | 1 | 0.85497 | 0 | 150 | 150 |  |  |  |  | 7801.5851 | 255.9915 | 87.4761 | 149.6846 | 0.17285 | 0.10762 | 0.030002 | 0.1884 | 0.015814 | 0.0094887 | 0.0025791 | 0.017396 | RTE_2025: 0.84698; EFC_2025: 177.91; UTI_2025: 3.1379
62856 | Marengo Battery Storage LLC | IL | PJM | Marengo Battery Storage LLC | Marengo Battery Storage LLC |  |  | TRUE | rte_gt_1 | LIB | CS |  | 20 | 20 | 1 | <1.5h | 2018 | 447 | C | HYBRID_ARTEFACT | 0.83514 | 0.85532 | -0.35864 | 0.016309 |  |  | ok |  | insufficient_history | 2173.7458 | 0.36229 | 0.63771 | 6000 | 0 | 8 | 1 | 0.85347 | 0 | 20 | 20 | -0.071729 | 0.85791 | 21 | 0.96289 | 0 | 0 | 0 | 0 | 0.10809 | 0.12644 | 0.01776 | 0.12644 | 0.0095321 | 0.011265 | 0.0015073 | 0.011265 | 0.83267 | 0 | 0.857 | 0.83386 | 0 | 0 | 0 | 377.95 | 0 | 1325.4 | 438.9 | 0 | 0 | 0 | 0 | 0 | 0.7916 | 0 | 0 | 0 | 0 | LOW_ETA_AND_LOW_UTI
62862 | Nabb Battery Energy Storage System | IN | MISO | Duke Energy Indiana, LLC | Duke Energy Indiana, LLC |  |  | FALSE |  | LIB | CS |  | 5 | 5 | 1 | <1.5h | 2020 | 115 | A | UNDER_DISPATCH | 0.86897 | 0.83464 | -0.018605 | -0.0052413 |  |  | insufficient_history |  | insufficient_history | 261.2 | 0.043533 | 0.95647 | 6000 | 0 | 8 | 1 | 0.92593 | 1588.2067 | 5 | 5 | -0.00093027 | 0.88148 | 15 | 0.053483 | 65.8591 | 2.9414 | 1.7931 | 2.0103 | 0.13542 | 0.11205 | 0.054422 | 0.22481 | 0.012126 | 0.009903 | 0.0048018 | 0.021221 | RTE_2020: 0.81818; RTE_2024: 0.88866; RTE_2025: 0.87327; EFC_2020: 12.6; EFC_2024: 84.6; EFC_2025: 164; UTI_2020: 0.12109; UTI_2024: 0.002297; UTI_2025: 0.507 | FULL_OUTAGE
62874 | Acorn I Energy Storage LLC | CA | CISO | Acorn I Energy Storage LLC | Acorn I Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 2 | 6 | 3 | 2.5-4.5h | 2021 | 156 | A | PARTIAL_AVAILABILITY | 0.89439 | 0.90023 | -0.018982 | 0.0045012 | -5.5586 | -123.0232 | ok | 0.67698 | ok | 1205.7917 | 0.20097 | 0.79903 | 6000 | 0 | 7 | 1 | 0.92766 | 747.9714 | 2 | 2 | -0.00037965 | 0.90682 | 36 | 0.005039 | 43.0065 | 6.2718 | 2.6394 | 2.6255 | 0.080762 | 0.20113 | 0.069817 | 0.25527 | 0.0070175 | 0.018713 | 0.0062643 | 0.024561 | RTE_2022: 0.92263; RTE_2023: 0.92585; RTE_2024: 0.92244; RTE_2025: 0.84776; EFC_2022: 294.1667; EFC_2023: 320.5; EFC_2024: 222; EFC_2025: 148.5; UTI_2022: 1.2034; UTI_2023: 1.1482; UTI_2024: 0.82642; UTI_2025: 0.59957 | PARTIAL_AVAILABILITY
62875 | Wildcat I Energy Storage LLC | CA | CISO | Wildcat I Energy Storage LLC | Wildcat I Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 3 | 12 | 4 | 2.5-4.5h | 2021 | 150 | A | THERMAL_AUX | 0.99712 | 0.89369 | 0.6577 | -0.0040945 | 0.34951 | 102.7453 | ok | 0.73841 | ok | 699.75 | 0.11663 | 0.88338 | 6000 | 7 | 2 | 1 | 0.92954 | 409.8294 | 3 | 3 | 0.019731 | 0.90504 | 36 | 0.7226 | 44.2941 | 6.4596 | 8.3808 | 2.7041 | 0.080762 | 0.20113 | 0.18747 | 0.25527 | 0.0070175 | 0.018713 | 0.019312 | 0.024561 | RTE_2022: 0.92446; RTE_2023: 0.92852; RTE_2024: 0.91702; RTE_2025: 0.83753; EFC_2022: 231.5; EFC_2023: 199.1667; EFC_2024: 144.5833; EFC_2025: 85.9167; UTI_2022: 0.80913; UTI_2023: 0.64319; UTI_2024: 0.53522; UTI_2025: 0.2978 | THERMAL_AUX
62889 | Hecate Energy Johanna Facility | CA | CISO | Hecate Energy Johanna Facility LLC | Hecate Energy Johanna Facility LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, System Peak Shaving | 20 | 80 | 4 | 2.5-4.5h | 2021 | 114 | A | UNATTRIBUTED | 0.95564 | 0.85703 | 1.4063 | 0.05323 |  |  | ok | -0.74058 | ok | 1073.5687 | 0.17893 | 0.82107 | 6000 | 0 | 0 | 1 | 0.86829 | 477.7154 | 20 | 20 | 0.28125 | 0.85773 | 24 | 0.2584 | 935.07 | 136.3655 | 62.2625 | 57.0839 | 0.080762 | 0.20113 | 0.075292 | 0.25527 | 0.0070175 | 0.018713 | 0.0067964 | 0.024561 | RTE_2024: 0.85797; RTE_2025: 0.85751; EFC_2024: 247.675; EFC_2025: 268.625; UTI_2024: 0.91859; UTI_2025: 0.92579 | ELEVATED_P_AUX
62907 | Hinesburg | VT | ISNE | Viridity Energy Solutions, Inc. | Viridity Energy Solutions, Inc. |  |  | FALSE |  | LIB | CS |  | 1.9 | 1.9 | 1 | <1.5h | 2019 |  |  | FULL_OUTAGE | 0.87893 | 0.87243 | 0.1435 | -0.0051097 | 5.0569 | 143.9647 | ok | 0.052994 | ok | 8280.5263 | 1.3801 | 0 | 6000 | 1 | 2 | 1 | 0.90765 | 347 | 1.9 | 1.9 | 0.0027265 | 0.87312 | 34 | 0.013308 | 149.6859 | 2.7287 | 15.9168 | 5.2217 | 0.14606 | 0.051271 | 0.19554 | 0.27079 | 0.013158 | 0.004386 | 0.02035 | 0.026316 | 0.92428 | 0.90794 | 0.90978 | 0.88373 | 0.88129 | 0.85927 | 0.87867 | 218.4211 | 2185.2632 | 1714.2105 | 1352.1053 | 922.1053 | 912.6316 | 975.7895 | 0.47427 | 1.4761 | 1.6283 | 1.7318 | 2.1334 | 2.4992 | 2.4772
62908 | Anoka BESS | MN | MISO | Gopher Energy Storage, LLC | Gopher Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 6 | 12 | 2 | 1.5-2.5h | 2018 | 95 | A | UNATTRIBUTED | 0.53603 | 0.34262 | 0.17431 | -0.0073808 | -11.9115 | -56.7825 | ok | 2.7182 | ok | 140.6458 | 0.023441 | 0.97656 | 6000 | 5 | 3 | 1 | 0.43662 | 2652.2043 | 6 | 6 | 0.010459 | 0.48677 | 35 | 0.28936 | 11.72 | 0.31538 | 0.10393 | 0.19144 | 0.18267 | 0.094486 | 0.025344 | 0.17213 | 0.016809 | 0.0082711 | 0.0021681 | 0.015742 | 0.35581 | 0.40985 | 0.43466 | 0.38162 | 0.16461 | 0.26812 | 0.22672 | 23.75 | 30.5 | 25.5 | 22.8333 | 6.6667 | 15.4167 | 14 | 0.45238 | 0.42132 | 0.046729 | 0.092464 | 0.015965 | 0.042568 | 0.039672 | LOW_ETA_AND_LOW_UTI
62937 | Athens BESS | MN | MISO | Gopher Energy Storage, LLC | Gopher Energy Storage, LLC |  |  | TRUE | colocated_firming | LIB | CS |  | 6 | 12 | 2 | 1.5-2.5h | 2018 | 342 | C | HYBRID_ARTEFACT | 0.50827 | 0.33472 | 0.066435 | -0.0074076 | -7.9067 | -43.6672 | ok | -10.14 | ok | 111.7986 | 0.018633 | 0.98137 | 6000 | 6 | 0 | 1 | 0.62887 | 0 | 6 | 6 | 0.0039861 | 0.49652 | 30 | 0.03301 | 4.9347 | 0.13279 | 0.043761 | 0.080608 | 0.18267 | 0.094486 | 0.025344 | 0.17213 | 0.016809 | 0.0082711 | 0.0021681 | 0.015742 | 0.39439 | 0.4284 | 0.43277 | 0.34985 | 0.10586 | 0.20779 | 0.20426 | 24.5833 | 29.1667 | 23.3333 | 19.4167 | 3.9167 | 5.3333 | 4 | 0.35088 | 0.47857 | 0.065289 | 0.074529 | 0.0022157 | 0.0199 | 0.015139 | LOW_ETA_AND_LOW_UTI
62964 | El Sol BESS | AZ | AZPS | Invenergy Services LLC | Invenergy Services LLC |  |  | FALSE |  | LIB | CS | System Peak Shaving | 50 | 50 | 1 | <1.5h | 2023 | 122 | B | PARTIAL_AVAILABILITY | 0.89498 | 0.88028 | 0.20615 | 0.020247 |  |  | insufficient_history |  | insufficient_history | 2450.465 | 0.40841 | 0.59159 | 6000 | 4 | 2 | 1 | 0.87051 | 441 | 50 | 50 | 0.10307 | 0.88103 | 16 | 0.18948 | 2909.0141 | 201.5114 | 87.4106 | 175.8975 | 0.099307 | 0.12408 | 0.043674 | 0.30412 | 0.0087159 | 0.01104 | 0.0038092 | 0.030215 | RTE_2024: 0.88354; RTE_2025: 0.88008; EFC_2024: 383.26; EFC_2025: 1013.24; UTI_2024: 2.9051; UTI_2025: 3.1071 | PARTIAL_AVAILABILITY
62968 | Syncarpha Tewksbury Hybrid CSG | MA | ISNE | Syncarpha Tewksbury, LLC | Syncarpha Tewksbury, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving | 2 | 4 | 2 | 1.5-2.5h | 2022 | 387 | C | HYBRID_ARTEFACT | 0.87589 | 0.84094 | 0.12472 | -0.0019799 | 1.7372 | 59.9847 | ok | 0.5163 | ok | 458.5 | 0.076417 | 0.92358 | 6000 | 0 | 3 | 1 | 0.87342 | 123.5 | 2 | 2 | 0.0024944 | 0.84885 | 32 | 0.47728 | 60.5096 | 1.4182 | 0.54861 | 0.45232 | 0.17028 | 0.076884 | 0.024013 | 0.076884 | 0.015556 | 0.0066667 | 0.0020513 | 0.0066667 | RTE_2022: 0.85801; RTE_2023: 0.85514; RTE_2024: 0.84692; RTE_2025: 0.84571; EFC_2022: 71; EFC_2023: 91.5; EFC_2024: 148; EFC_2025: 148; UTI_2022: 0.36677; UTI_2023: 0.4333; UTI_2024: 1.3369; UTI_2025: 1.5134 | FULL_OUTAGE
62969 | Syncarpha Puddon I Hybrid CSG | MA | ISNE | Syncarpha Puddon I, LLC | Syncarpha Puddon I, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving, Excess Wind and Solar Generation | 4 | 8 | 2 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.87987 | 0.88429 | -0.0087511 | 0.0020584 | -0.77618 | -9.9378 | ok | 3.2233 | ok | 350.625 | 0.058438 | 0.94156 | 6000 | 0 | 0 | 1 | 0.89041 | 0 | 4 | 4 | -0.00035005 | 0.88384 | 24 | 0.0032544 | 70.8071 | 2.1513 | 0.76984 | 0.20584 | 0.14392 | 0.082709 | 0.023972 | 0.025567 | 0.01295 | 0.0071942 | 0.0020478 | 0.0021583 | RTE_2021: 0.77778; RTE_2022: 0.83465; RTE_2024: 0.88626; RTE_2025: 0.8812; EFC_2021: 7.875; EFC_2022: 119.25; EFC_2024: 116.875; EFC_2025: 106.625; UTI_2021: 0.042712; UTI_2022: 0.52864; UTI_2024: 1.0646; UTI_2025: 0.96547
62970 | Syncarpha Puddon II Hybrid CSG | MA | ISNE | Syncarpha Puddon II, LLC | Syncarpha Puddon II, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving, Excess Wind and Solar Generation | 4 | 8 | 2 | 1.5-2.5h | 2021 | 220 | C | HYBRID_ARTEFACT | 0.79998 | 0.81058 | 0.029436 | -0.015963 |  |  | insufficient_history | -3.2499 | ok | 318.375 | 0.053062 | 0.94694 | 6000 | 0 | 1 | 1 | 0.90728 | 71.5335 | 4 | 4 | 0.0011774 | 0.84013 | 23 | 0.19494 | 61.3028 | 1.8625 | 0.6665 | 0.17821 | 0.14392 | 0.082709 | 0.023972 | 0.025567 | 0.01295 | 0.0071942 | 0.0020478 | 0.0021583 | RTE_2021: 0.89238; RTE_2022: 0.8408; RTE_2024: 0.79732; RTE_2025: 0.87069; EFC_2021: 24.875; EFC_2022: 105.625; EFC_2024: 74.25; EFC_2025: 113.625; UTI_2021: 0.13491; UTI_2022: 0.46824; UTI_2024: 0.56909; UTI_2025: 1.1344 | LOW_ETA_AND_LOW_UTI
62971 | Syncarpha Westminster Hybrid CSG | MA | ISNE | Syncarpha Westminster, LLC | Syncarpha Westminster, LLC |  |  | TRUE | pv_same_plant | NIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving | 2.9 | 6 | 2.069 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.9531 | 0.85805 | 0.20992 | -0.0012075 |  |  | insufficient_history |  | insufficient_history | 130.6667 | 0.021778 | 0.97822 | 6000 | 0 | 0 | 1 | 0.92481 | 0 | 2.9 | 2.9 | 0.0060876 | 0.89192 | 12 | 0.41676 | 71.3556 | 1.6724 | 0.68191 | 0.5334 | 0.17028 | 0.076884 | 0.025277 | 0.076884 | 0.015556 | 0.0066667 | 0.0021622 | 0.0066667 | RTE_2025: 0.89192; EFC_2025: 130.6667; UTI_2025: 1.2806
62972 | Syncarpha Leicester Hybrid CSG | MA | ISNE | Syncarpha Leicester, LLC | Syncarpha Leicester, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | NIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving | 2 | 4.2 | 2.1 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.99352 | 0.98465 | 0.017806 | -0.0011697 | 1.1468 | 225.1189 | ok | -7.6336 | ok | 663.8095 | 0.11063 | 0.88937 | 6000 | 0 | 0 | 1 | 1.0189 | 0 | 2 | 2 | 0.00035611 | 0.98958 | 36 | 0.0041352 | 54.1745 | 1.6459 | 0.57431 | 0.15749 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.95238 | 0.96623 | 1.0314 | 0.96588 | 0.97227 |  |  | 9.5238 | 156.6667 | 172.1429 | 175.2381 | 150.2381 |  |  | 0.018623 | 0.69452 | 1.1078 | 1.6842 | 1.6761
62973 | Syncarpha Halifax Hybrid CSG | MA | ISNE | Syncarpha Halifax, LLC | Syncarpha Halifax, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | NIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving | 1.6 | 3.2 | 2 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 1.0152 | 0.8974 | 0.3824 | -0.0040774 | 2.3701 | 51.9221 | ok | -0.15833 | ok | 729.375 | 0.12156 | 0.87844 | 6000 | 0 | 0 | 1 | 0.88889 | 0 | 1.6 | 1.6 | 0.0061183 | 0.91212 | 36 | 0.32427 | 34.6907 | 1.054 | 0.36776 | 0.10085 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.9587 | 0.90407 | 0.99079 | 0.88793 | 0.85106 |  |  | 101.5625 | 173.75 | 168.125 | 160.9375 | 125 |  |  | 0.46063 | 0.77024 | 0.8722 | 1.4559 | 1.4094
62974 | Syncarpha Millbury Hybrid (CSG) | MA | ISNE | Syncarpha Millbury, LLC | Syncarpha Millbury, LLC |  |  | TRUE | pv_same_plant | NIB | CT | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving | 3.8 | 7.9 | 2.0789 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.96517 | 0.88181 | 0.40736 | -0.0027292 |  |  | insufficient_history |  | insufficient_history | 207.5949 | 0.034599 | 0.9654 | 6000 | 0 | 0 | 1 | 0.90594 | 0 | 3.8 | 3.8 | 0.01548 | 0.89617 | 12 | 0.88901 | 175.8203 | 4.1208 | 1.6802 | 1.3143 | 0.17028 | 0.076884 | 0.025277 | 0.076884 | 0.015556 | 0.0066667 | 0.0021622 | 0.0066667 | RTE_2025: 0.89617; EFC_2025: 207.5949; UTI_2025: 1.6456
62975 | Syncarpha Blandford Hybrid CSG | MA | ISNE | Syncarpha Blandford, LLC | Syncarpha Blandford, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | NIB | CT | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving | 3.9 | 7.9 | 2.0256 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.94598 | 0.88709 | 0.19203 | -0.0083526 | 4.0723 | 120.7982 | ok | -0.57825 | ok | 671.8987 | 0.11198 | 0.88802 | 6000 | 0 | 1 | 1 | 0.90503 | 91.5 | 3.9 | 3.9 | 0.0074893 | 0.89894 | 35 | 0.51194 | 108.3491 | 3.2919 | 1.1486 | 0.31497 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  | 0.83777 | 0.79287 | 0.86511 | 0.89045 | 0.90383 | 0.90044 |  | 39.8734 | 59.1139 | 131.519 | 120.3797 | 164.1772 | 156.8354 |  | 0.86475 | 0.26811 | 0.58303 | 0.74083 | 1.4392 | 1.6381
62976 | Syncarpha Northampton Hybrid CSG | MA | ISNE | Syncarpha Northampton, LLC | Syncarpha Northampton, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving, Excess Wind and Solar Generation | 2 | 4 | 2 | 1.5-2.5h | 2020 | 290 | C | HYBRID_ARTEFACT | 0.94786 | 0.73519 | 0.36844 | -0.0011112 | -7.1633 | 28.7753 | ok | -7.1281 | ok | 292.75 | 0.048792 | 0.95121 | 6000 | 0 | 14 | 1 | 0.856 | 175.7185 | 2 | 2 | 0.0073688 | 0.75921 | 24 | 0.71901 | 15.2069 | 0.46202 | 0.16121 | 0.044207 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.84211 | 0.85097 |  | 0.8057 | 0.70312 |  |  | 16 | 142.75 | 0 | 77.75 | 56.25 |  |  | 0.07257 | 0.63282 | 0 | 0.67063 | 0.82165 | FULL_OUTAGE
62977 | Syncarpha Northbridge I Hybrid(CSG) | MA | ISNE | Syncarpha Northbridge I, LLC | Syncarpha Northbridge I, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving | 4 | 8 | 2 | 1.5-2.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.87668 | 0.79914 | 0.17217 | -0.0023883 |  |  | insufficient_history |  | insufficient_history | 86.125 | 0.014354 | 0.98565 | 6000 | 0 | 0 | 1 | 0.85906 | 0 | 4 | 4 | 0.0068867 | 0.81635 | 12 | 0.8072 | 58.797 | 1.3781 | 0.56189 | 0.43952 | 0.17028 | 0.076884 | 0.025277 | 0.076884 | 0.015556 | 0.0066667 | 0.0021622 | 0.0066667 | RTE_2025: 0.81635; EFC_2025: 86.125; UTI_2025: 0.78169
62978 | Syncarpha Northbridge II Hybrid CSG | MA | ISNE | Syncarpha Northbridge II, LLC | Syncarpha Northbridge II, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving | 3 | 6 | 2 | 1.5-2.5h | 2021 | 279 | C | HYBRID_ARTEFACT | 0.83908 | 0.83904 | 0.0041375 | -0.0034027 | 2.7626 | 117.4722 | ok | -0.1582 | ok | 471.6667 | 0.078611 | 0.92139 | 6000 | 0 | 3 | 1 | 0.87395 | 78 | 3 | 3 | 0.00012412 | 0.84318 | 34 | 0.0020706 | 61.778 | 1.877 | 0.65491 | 0.17959 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.84082 | 0.82123 | 0.86232 | 0.83667 | 0.83403 |  |  | 34.3333 | 73.5 | 99.1667 | 132.3333 | 132.3333 |  |  | 0.20745 | 0.32583 | 0.52124 | 1.2716 | 1.4294 | LOW_ETA_AND_LOW_UTI
62981 | East Pulaski BESS | NY | NYIS | National Grid | National Grid |  |  | FALSE |  | LIB | CS | Load Following, Transmission and Distribution Deferral | 2 | 4.2 | 2.1 | 1.5-2.5h | 2018 |  |  | UNDER_DISPATCH | 0.4105 | 0.60609 | -1.2628 | -0.011625 | -16.2101 | 75.0577 | ok | 0.27611 | ok | 290.2183 | 0.04837 | 0.95163 | 6000 | 0 | 0 | 1 | 0.46512 | 2312.4145 | 2 | 2 | -0.025257 | 0.54118 | 24 | 0.26286 | 43.7958 | 1.1785 | 0.43449 | 0.71539 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | 0.29529 | 0.5 | 0.065 | 0.02381 | 0.95671 | 0.43913 | 0.38942 | 28.3333 | 58.5714 | 3.0952 | 0.71429 | 52.619 | 48.0952 | 96.4286 | 0.50924 | 0.90342 | 0.012547 | 0.0031047 | 0.24711 | 0.031971 | 0.37801
62999 | Finchville Solar, LLC Hybrid CSG | NY | NYIS | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 3 | 4.4 | 1.4667 | <1.5h | 2020 | 232 | C | HYBRID_ARTEFACT | 0.9681 | 0.90699 | -0.00023673 | 0.0021428 |  |  | ok | 12.8256 | ok | 287.7273 | 0.047955 | 0.95205 | 6000 | 0 | 12 | 1 | 0.95575 | 55.5 | 1.9 | 1.9 | -7.1018e-06 | 1.0063 | 23 | 5.7999e-05 | 0 | 0 | 0 | 0 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 |  |  | 0.68421 | 1.0403 | 1.0561 | 0.92593 | 0.66667 |  |  | 5.9091 | 64.5455 | 141.1364 | 73.8636 | 2.2727 |  |  | 0.0049507 | 0.080419 | 0.23324 | 0.14568 | 0 | FULL_OUTAGE
63000 | RT 52 Walden Solar 1, LLC Hybrid | NY | NYIS | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CT | System Peak Shaving | 4 | 8.8 | 2.2 | 1.5-2.5h | 2020 | 242 | C | HYBRID_ARTEFACT | 0.73823 | 0.76323 | -0.00053251 | 0.0008052 |  |  | ok | 2.0679 | ok | 303.75 | 0.050625 | 0.94937 | 6000 | 0 | 16 | 1 | 0.91275 | 131.4675 | 3.9 | 3.9 | -2.13e-05 | 0.87518 | 15 | 0.00010255 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 |  | 0.96622 | 0.89855 | 2.6169 | 0.88057 | 0.76667 | 0.5 |  | 146.25 | 42.2727 | 45.7955 | 56.1364 | 13.0682 | 0.22727 |  | 2.2557 | 0.17138 | 0.19888 | 0.03606 | 0.0061592 | 0 | FULL_OUTAGE
63011 | Cronin Road Solar 1, LLC CSG Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 1.5 | 7.7 | 5.1333 | >4.5h | 2020 | 189 | C | HYBRID_ARTEFACT | 0.98201 | 0.96953 | 0.094792 | 0.00085486 | -0.57911 | -26.8994 | ok | -1.0991 | ok | 460.9091 | 0.076818 | 0.92318 | 6000 | 0 | 3 | 1 | 0.9726 | 126.5 | 1.5 | 1.5 | 0.0014219 | 0.9716 | 32 | 0.026922 | 190.7621 | 1.7387 | 3.304 | 1.6637 | 0.26681 | 0.050409 | 0.072405 | 0.14373 | 0.025862 | 0.0043103 | 0.006515 | 0.012931 |  |  | 0.88722 | 1.0912 | 0.98202 | 0.92475 | 0.98324 |  |  | 76.6234 | 46.6234 | 113.5065 | 71.8182 | 152.3377 |  |  | 0.63592 | 0.33432 | 1.5924 | 0.67624 | 1.4543 | FULL_OUTAGE
63022 | Fort Carson Battery Energy Storage Syste | CO | WACM | Department of the Army, Fort Carson | Department of the Army, Fort Carson |  |  | FALSE |  | LIB | CS |  | 4.2 | 8.5 | 2.0238 | 1.5-2.5h | 2018 | 146 | A | THERMAL_AUX | 0.50472 | 0.49727 | -0.16851 | 0.0013682 | 17.7593 | 135.6206 | ok | -5.4104 | ok | 902.6569 | 0.15044 | 0.84956 | 6000 | 0 | 4 | 1 | 0.66697 | 298.4837 | 4.2 | 4.2 | -0.0070776 | 0.5375 | 31 | 0.056834 | 474.6701 | 7.7876 | 30.927 | 0.030468 | 0.27826 | 0.093193 | 0.23502 | 0.0011993 | 0.027174 | 0.0081522 | 0.025752 | 0.0001 |  | 0.875 | 0.28571 | 0.49038 | 0.55724 | 0.5444 | 0.45625 |  | 0.82353 | 0.23529 | 30 | 47.5294 | 479.6471 | 343.5294 |  | 0.12106 | 0.0079051 | 0.13226 | 0.21891 | 1.7833 | 1.2897 | THERMAL_AUX
63044 | Ryan Road Solar LLC Hybrid(CSG) | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 4.3 | 14 | 3.2558 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.9518 | 0.90262 | 0.061199 | -0.004964 | 1.6636 | 32.2313 | ok | -12.7268 | ok | 364.2857 | 0.060714 | 0.93929 | 6000 | 0 | 0 | 1 | 0.96454 | 0 | 4.3 | 4.3 | 0.0026316 | 0.94444 | 35 | 0.94085 | 149.8468 | 8.1948 | 0.098903 | 0.025091 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 | RTE_2022: 0.9112; RTE_2023: 0.93131; RTE_2024: 0.93208; RTE_2025: 0.95927; EFC_2022: 16.8571; EFC_2023: 116.2143; EFC_2024: 88.2143; EFC_2025: 143; UTI_2022: 0.066288; UTI_2023: 0.40039; UTI_2024: 0.46327; UTI_2025: 0.71969
63064 | Asheville-Rock Hill Battery | NC | CPLW | Duke Energy Progress - (NC) | Duke Energy Progress - (NC) |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 8.8 | 8.8 | 1 | <1.5h | 2020 | 246 | B | UNDER_DISPATCH | 0.86318 | 0.58221 | 0.20554 | -0.0071971 | -0.93322 | -2.4556 | ok | 2.6079 | ok | 216.9318 | 0.036155 | 0.96384 | 6000 | 0 | 2 | 1 | 0.80412 | 31179.1005 | 8.8 | 8.8 | 0.018088 | 0.65074 | 58 | 0.69743 | 31.8957 | 1.1629 | 0.015643 | 0.37089 | 0.15484 | 0.10609 | 0.0011985 | 0.10609 | 0.014019 | 0.0093458 | 0.0001 | 0.0093458 |  | 0.64 | 0.64223 | 0.64275 | 0.60512 | 0.6088 | 0.68429 |  | 10.9091 | 41.8182 | 46.8182 | 37.6136 | 28.2955 | 51.4773 |  | 0.015022 | 0.035237 | 0.056445 | 0.039604 | 0.055627 | 0.11907 | FULL_OUTAGE
63090 | Athens - Coopers Corner BESS | MN | MISO | Gopher Energy Storage, LLC | Gopher Energy Storage, LLC |  |  | TRUE | colocated_firming | LIB | CS |  | 3 | 6 | 2 | 1.5-2.5h | 2018 | 345 | C | HYBRID_ARTEFACT |  | 0.23598 |  |  |  |  | insufficient_history | -0.21065 | ok | 141.3611 | 0.02356 | 0.97644 | 6000 | 7 | 2 | 1 | 0.41538 | 0 | 3 | 3 |  |  |  |  | 11.1031 | 0.29879 | 0.11015 | 0.18137 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | 0.34845 | 0.45455 | 0.41554 | 0.3805 | 0.1133 | 0.23505 | 0.23242 | 24.3333 | 31.6667 | 20.5 | 20.1667 | 3.8333 | 19 | 19.8333 | 0.40234 | 0.51142 | 0.097202 | 0.082123 | 0.014642 | 0.06572 | 0.07327 | PARTIAL_AVAILABILITY
63091 | UC Santa Cruz Solar | CA | CISO | Forefront Power, LLC | Forefront Power, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 1 | 1 | 1 | <1.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
63150 | Pohatcong Solar Farm | NJ | PJM | NJR Clean Energy Ventures III Corporation | NJR Clean Energy Ventures Corporation |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
63172 | Arroyo Solar Energy Storage Hybrid | NM | PNM | Arroyo Solar LLC | Arroyo Solar LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 150 | 600 | 4 | 2.5-4.5h | 2023 | 15 | C | HYBRID_ARTEFACT | 0.96594 | 0.9033 | 0.96542 | -0.045038 | 1.2852 | 18.9747 | ok | 0.17755 | ok | 745.405 | 0.12423 | 0.87577 | 6000 | 0 | 6 | 1 | 0.91008 | 8531 | 150 | 150 | 1.4481 | 0.90386 | 30 | 0.28875 | 105.5007 | 1833.3363 | 242.8 | 137.5825 | 0.0011993 | 0.31703 | 0.038587 | 0.085813 | 0.0001 | 0.031776 | 0.0033474 | 0.0074766 | RTE_2023: 0.90768; RTE_2024: 0.90432; RTE_2025: 0.90115; EFC_2023: 158.4383; EFC_2024: 311.4083; EFC_2025: 275.5583; UTI_2023: 1.2032; UTI_2024: 1.1884; UTI_2025: 0.99466 | PARTIAL_AVAILABILITY
63186 | Imeson Solar | FL | JEA | Imeson Solar Farm LLC | Imeson Solar Farm LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 5 | 3.8 | 0.76 | <1.5h | 2019 | 271 | C | FULL_OUTAGE | 0.98801 | 0.92399 | 0.026091 | -0.0002371 |  |  | insufficient_history |  | insufficient_history | 522.8947 | 0.087149 | 0.91285 | 6000 | 0 | 24 | 1 | 0.97368 | 229.912 | 1.5 | 1.5 | 0.0013046 | 0.96095 | 12 | 0.99024 | 0 | 0 | 0 | 0 | 0.15519 | 0.12167 | 0.033513 | 0.13299 | 0.014054 | 0.010811 | 0.0028916 | 0.011892 |  |  | 0.97352 | 0.97352 |  | 0.96095 |  |  |  | 203.1579 | 203.1579 | 0 | 116.5789 | 0 |  |  | 0.16826 | 0.23946 | 0 | 0.30771 | 0 | FULL_OUTAGE
63214 | Middleton Solar Park | MA | ISNE | Novis Renewables, LLC | Novis Renewables, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 3 | 6.6 | 2.2 | 1.5-2.5h | 2019 | 211 | C | HYBRID_ARTEFACT | 0.96937 | 0.66701 | 0.49081 | 0.0038953 |  |  | ok | 1.0984 | ok | 285.9848 | 0.047664 | 0.95234 | 6000 | 0 | 12 | 0.9 | 0.84932 | 83.5 | 3 | 2.7 | 0.014724 | 0.69957 | 24 | 0.81987 | 0 | 0 | 0 | 0 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 |  | 0.89394 | 0.89195 | 0.8456 | 0.72009 | 0.68058 |  |  | 53.6364 | 58.7879 | 71.3636 | 48.3333 | 49.3939 | 0 |  | 0.84985 | 0.26663 | 0.31636 | 0.21542 | 1.088 | 0 | FULL_OUTAGE
63238 | Willis Battery Storage | NY | NYIS | New York Power Authority | New York Power Authority |  |  | FALSE |  | LIB | CS | Arbitrage | 20 | 20 | 1 | <1.5h | 2023 | 138 | B | CAPACITY_FADE |  | 0.34329 |  |  |  |  | insufficient_history | -8.6677 | ok | 64.225 | 0.010704 | 0.9893 | 6000 | 0 | 9 | 1 | 0.57348 | 1613.1344 | 20 | 20 |  |  |  |  | 0 | 0 | 0 | 0 | 0.13542 | 0.11205 | 0.054422 | 0.22481 | 0.012126 | 0.009903 | 0.0048018 | 0.021221 | RTE_2024: 0.36157; RTE_2025: 0.48059; EFC_2024: 34.15; EFC_2025: 13; UTI_2024: 0.063813; UTI_2025: 0 | FULL_OUTAGE
63255 | 2W Permian Solar Project Hybrid | TX | ERCO | 2W Permian Solar, LLC | 2W Permian Solar, LLC |  |  | TRUE | pv_same_plant | LIB | BL | Arbitrage, Frequency Regulation, Excess Wind and Solar Generation | 40 | 40 | 1 | <1.5h | 2021 | 184 | C | HYBRID_ARTEFACT | 0.45877 | 0.4508 | -0.0077424 | 0.022464 | -2.6302 | 16.2808 | ok | 0.33915 | ok | 251.225 | 0.041871 | 0.95813 | 6000 | 1 | 2 | 1 | 0.66029 | 117 | 40 | 40 | -0.003097 | 0.49708 | 45 | 0.0015451 | 41.8281 | 8.3875 | 4.1129 | 1.216 | 0.053242 | 0.18177 | 0.072461 | 0.087152 | 0.0045593 | 0.016717 | 0.0065205 | 0.0075988 |  |  | 0.6425 | 0.38462 | 0.44197 | 0.43123 | 0.4102 |  |  | 57.375 | 36.875 | 66.45 | 53.925 | 36.6 |  |  | 0.075052 | 0.15617 | 0.12634 | 0.23465 | 0.16099 | PARTIAL_AVAILABILITY
63264 | Partridge Hill Solar Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 1.3 | 1.5 | 1.1538 | <1.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.92058 | 0.83664 | 0.25622 | -0.0016047 | 2.78 | 8.3906 | ok | 0.063744 | ok | 887.3333 | 0.14789 | 0.85211 | 6000 | 0 | 1 | 1 | 0.9 | 34.5 | 1.3 | 1.3 | 0.0033308 | 0.86097 | 35 | 0.6738 | 8.8963 | 2.4326 | 0.016147 | 1.7069 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 |  | 1 |  | 0.82418 | 0.84434 | 0.88366 | 0.85819 |  | 2 | 0 | 200 | 238.6667 | 212.6667 | 234 |  | 0.019665 | 0 | 0.29961 | 0.54785 | 0.5601 | 0.58107
63280 | AES Kekaha Solar, LLC Hybrid | HI |  | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Load Management, Voltage or Reactive Power Support, Backup Power, Excess Wind and Solar Generation | 14 | 70 | 5 | >4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.96814 | 0.96153 | -0.0072085 | 0.014712 |  |  | ok | 0.34418 | ok | 1167.0286 | 0.1945 | 0.8055 | 6000 | 0 | 0 | 1 | 0.97835 | 0 | 8 | 8 | -0.0010092 | 0.9709 | 36 | 0.0080843 | 1203.6676 | 72.4087 | 0.68274 | 16.7957 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 |  |  | 0.97952 | 0.95817 | 0.99231 | 0.96652 | 0.95189 |  |  | 211.1143 | 254.2286 | 243.2714 | 253.2143 | 205.2 |  |  | 2.3778 | 1.7757 | 6.7648 | 2.5267 | 1.8612
63324 | Camp Atterbury Microgrid Hybrid | IN | MISO | Duke Energy Indiana, LLC | Duke Energy Indiana, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | BL | System Peak Shaving, Voltage or Reactive Power Support, Backup Power, Excess Wind and Solar Generation | 5 | 5 | 1 | <1.5h | 2019 | 425 | C | HYBRID_ARTEFACT | 0.89809 | 0.80749 | 0.074217 | 0.0021307 | -4.5142 | -37.6726 | ok | -0.9286 | ok | 1011.8 | 0.16863 | 0.83137 | 6000 | 0 | 12 | 1 | 0.90769 | 457.6195 | 5 | 5 | 0.0037108 | 0.88723 | 22 | 0.50752 | 57.4042 | 2.5638 | 1.4744 | 1.7522 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | 1 | 0.93846 | 0.94582 | 0.80554 | 0.61765 | 0.89822 | 0.87154 | 17.6 | 12.2 | 251.4 | 267.6 | 4.2 | 282.4 | 176.4 | 0.083126 | 0.0073258 | 0.20991 | 0.33888 | 0 | 0.76405 | 0.42547 | FULL_OUTAGE
63325 | Yorktown Battery Energy Storage Facility | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS | Arbitrage | 3.5 | 9 | 2.5714 | 2.5-4.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 3 | 3
63326 | Cadillac Battery Energy Storage Facility | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS | Arbitrage | 3.5 | 8.8 | 2.5143 | 2.5-4.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 3.5 | 3.5
63337 | Lansing Renewables, LLC | NY | NYIS | Lansing Renewables, LLC | Lansing Renewables, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CT |  | 3 | 3 | 1 | <1.5h | 2022 | 171 | C | HYBRID_ARTEFACT | 0.91175 | 0.88942 | 0.035651 | -0.0019217 | 2.0358 | 114.0044 | ok | -8.1431 | ok | 874.3333 | 0.14572 | 0.85428 | 6000 | 0 | 4 | 1 | 0.9205 | 168 | 3 | 3 | 0.0010695 | 0.9181 | 36 | 0.20802 | 48.9494 | 2.1862 | 1.2572 | 1.4941 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | RTE_2023: 0.90279; RTE_2024: 0.89934; RTE_2025: 0.94707; EFC_2023: 269.3333; EFC_2024: 271; EFC_2025: 334; UTI_2023: 0.29473; UTI_2024: 0.37318; UTI_2025: 0.66647 | PARTIAL_AVAILABILITY
63338 | Granby Solar, LLC CSG | MA | ISNE | Granby Solar, LLC | Granby Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CT |  | 2 | 2 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.88598 | 0.88803 | -0.0062818 | -0.00096633 | 1.3743 | 87.689 | ok | 0.10396 | ok | 1076 | 0.17933 | 0.82067 | 6000 | 0 | 0 | 1 | 0.89362 | 0 | 2 | 2 | -0.00012564 | 0.88889 | 36 | 0.0019094 | 46.7055 | 2.5542 | 0.03179 | 0.27155 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2023: 0.89133; RTE_2024: 0.9017; RTE_2025: 0.87379; EFC_2023: 344.5; EFC_2024: 371.5; EFC_2025: 360; UTI_2023: 0.94839; UTI_2024: 0.72045; UTI_2025: 0.7083
63339 | Hales Mills Solar, LLC | NY | NYIS | Hales Mills Solar, LLC | Hales Mills Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 3 | 12.8 | 4.2667 | 2.5-4.5h | 2024 | 269 | C | HYBRID_ARTEFACT | 0.91669 | 0.85358 | 0.022355 | -0.00043633 |  |  | insufficient_history |  | insufficient_history | 23.9062 | 0.0039844 | 0.99602 | 6000 | 0 | 5 | 1 | 0.89873 | 27.5 | 3 | 3 | 0.00067064 | 0.89971 | 11 | 0.2761 | 13.211 | 0.0018062 | 0.0022707 | 0.15362 | 0.38122 | 0.0011993 | 0.0011985 | 0.27385 | 0.04 | 0.0001 | 0.0001 | 0.026667 | RTE_2024: 0.89394; RTE_2025: 0.89818; EFC_2024: 4.6094; EFC_2025: 19.2969; UTI_2024: 0.040997; UTI_2025: 0.015271 | FULL_OUTAGE
63340 | Owlville Creek Solar 2, LLC | NY | NYIS | Owlville Creek Solar 2, LLC | Owlville Creek Solar 2, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 3 | 12.8 | 4.2667 | 2.5-4.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.90468 | 0.88261 | 0.0335 | -0.0017957 | -0.7857 | 56.4682 | ok | 0.064374 | ok | 150 | 0.025 | 0.975 | 6000 | 0 | 0 | 1 | 0.90674 | 0 | 3 | 3 | 0.001005 | 0.89013 | 33 | 0.2139 | 92.8084 | 0.019668 | 0.024726 | 1.2141 | 0.26632 | 0.0011993 | 0.0011985 | 0.20726 | 0.025806 | 0.0001 | 0.0001 | 0.019355 | RTE_2023: 0.89848; RTE_2024: 0.90269; RTE_2025: 0.87334; EFC_2023: 46.3281; EFC_2024: 47.1094; EFC_2025: 56.5625; UTI_2023: 0.14383; UTI_2024: 0.11113; UTI_2025: 0.16951
63341 | Owlville Creek Solar, LLC | NY | NYIS | Owlville Creek Solar, LLC | Owlville Creek Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 3 | 12.8 | 4.2667 | 2.5-4.5h | 2022 | 249 | C | HYBRID_ARTEFACT | 0.90149 | 0.9059 | -0.003048 | -0.00041746 | 4.6436 | 119.6162 | ok | -2.896 | ok | 145.3906 | 0.024232 | 0.97577 | 6000 | 0 | 3 | 1 | 0.92537 | 39 | 3 | 3 | -9.1441e-05 | 0.9078 | 33 | 0.0086898 | 99.4375 | 0.021072 | 0.026492 | 1.3008 | 0.26632 | 0.0011993 | 0.0011985 | 0.20726 | 0.025806 | 0.0001 | 0.0001 | 0.019355 | RTE_2023: 0.88156; RTE_2024: 0.89744; RTE_2025: 0.93082; EFC_2023: 45.9375; EFC_2024: 30.0781; EFC_2025: 69.375; UTI_2023: 0.062074; UTI_2024: 0.056295; UTI_2025: 0.18124 | FULL_OUTAGE
63352 | Gemini Solar Hybrid | NV | NEVP | Solar Partners XI LLC | Gemini Solar |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 380 | 380 | 1 | <1.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.92882 | 0.87728 | 0.80384 | 1.6779 |  |  | insufficient_history | -0.10673 | ok | 1952.5868 | 0.32543 | 0.67457 | 6000 | 5 | 0 | 1 | 0.89065 | 0 | 380 | 380 | 3.0546 | 0.87717 | 21 | 0.065689 | 24721.6619 | 1712.5038 | 728.3933 | 1494.8287 | 0.099307 | 0.12408 | 0.042861 | 0.30412 | 0.0087159 | 0.01104 | 0.0037351 | 0.030215 | RTE_2024: 0.87784; RTE_2025: 0.87675; EFC_2024: 739.8763; EFC_2025: 1212.7105; UTI_2024: 2.4049; UTI_2025: 3.552
63398 | Kearsarge Amesbury Hybrid | MA | ISNE | Kearsarge Amesbury LLC | Kearsarge Amesbury LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming | 1.6 | 3.8 | 2.375 | 1.5-2.5h | 2019 |  |  | HYBRID_ARTEFACT | 0.89396 | 0.8641 | 0.26842 | 0.0012604 | -2.64 | -62.7479 | ok | -0.017092 | ok | 1322.8947 | 0.22048 | 0.77952 | 6000 | 0 | 0 | 1 | 0.8869 | 0 | 1.5 | 1.5 | 0.0042947 | 0.86887 | 36 | 0.66222 | 118.2104 | 1.8471 | 0.052479 | 2.9455 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 |  | 0.89629 |  | 0.8714 | 0.87454 | 0.86973 | 0.8618 |  | 184.2105 | 0 | 238.9474 | 315.5263 | 298.6842 | 285.5263 |  | 2.9188 | 0 | 1.0593 | 1.8841 | 4.5646 | 5.1369
63415 | Middletown Solar 1, LLC Hybrid CSG | NY | NYIS | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 1.6 | 6.6 | 4.125 | 2.5-4.5h | 2020 | 335 | C | FULL_OUTAGE |  | 1.0137 |  |  |  |  | insufficient_history |  | insufficient_history | 90 | 0.015 | 0.985 | 6000 | 0 | 32 | 1 | 1.0109 | 141 | 1.6 | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.8318; RTE_2023: 1.0175; EFC_2022: 54.697; EFC_2023: 35.303; EFC_2024: 0; EFC_2025: 0; UTI_2022: 0.21941; UTI_2023: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
63420 | Fresno Bullard High School Hybrid | CA | CISO | Forefront Power, LLC | Forefront Power, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.4 | 0.4 | 1 | <1.5h | 2020 | 418 | C | HYBRID_ARTEFACT | 1.0297 | 0.80246 | 0.34362 | 3.7674e-05 |  |  | ok | 3.3736 | ok | 917.5 | 0.15292 | 0.84708 | 6000 | 0 | 3 | 1 | 1.1818 | 29 | 0.4 | 0.4 | 0.0013745 | 0.87027 | 27 | 0.92416 | 11.0092 | 0.25086 | 0.002523 | 0.016002 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  | 0.84211 | 0.86 | 0.87129 | 0.91753 | 0.36842 | 0.86667 |  | 80 | 215 | 220 | 222.5 | 17.5 | 162.5 |  | 0.11288 | 0.31977 | 0.27484 | 0.3902 | 0.013376 | 0.21729 | FULL_OUTAGE
63421 | Fresno Hoover High School Hybrid | CA | CISO | Forefront Power, LLC | Forefront Power, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.2 | 0.2 | 1 | <1.5h | 2020 | 294 | C | HYBRID_ARTEFACT | 1.2561 | 1.0887 | 0.25578 | 0.00044518 |  |  | insufficient_history | -2.426 | ok | 940 | 0.15667 | 0.84333 | 6000 | 0 | 5 | 1 | 1.1667 | 6 | 0.2 | 0.2 | 0.00051157 | 1.1685 | 12 | 0.40124 | 0 | 0 | 0 | 0 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  | 0.9 | 0.86842 | 0.85714 | 1.1685 | 0 | 0 |  | 45 | 165 | 210 | 520 | 0 | 0 |  | 0.063517 | 0.24541 | 0.26235 | 0.41873 | 0 | 0 | FULL_OUTAGE
63422 | Fresno Sunnyside High School Hybrid | CA | CISO | Forefront Power, LLC | Forefront Power, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.3 | 0.3 | 1 | <1.5h | 2020 | 292 | C | HYBRID_ARTEFACT | 0.7655 | 0.87351 | -0.39721 | -2.9364e-05 |  |  | insufficient_history |  | insufficient_history | 596.6667 | 0.099444 | 0.90056 | 6000 | 0 | 7 | 1 | 0.875 | 6 | 0.3 | 0.3 | -0.0011916 | 0.8642 | 12 | 0.27015 | 0 | 0 | 0 | 0 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  | 0 | 0.86957 | 0.87342 | 0.8642 | 0 | 0 |  | 0 | 133.3333 | 230 | 233.3333 | 0 | 0 |  | 0 | 0.19831 | 0.28733 | 0.34553 | 0 | 0 | LOW_ETA_AND_LOW_UTI
63435 | Partridge Solar Project CSG Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 1.3 | 1.5 | 1.1538 | <1.5h | 2020 |  |  | HEALTHY | [8 empty] | insufficient_history | 2 | 0.00033333 | 0.99967 | 6000 | 0 | 0 | 1 | 1 | 0 | 1.3 | 1.3 | [16 empty] | RTE_2020: 1; EFC_2020: 2; UTI_2020: 0.019665
63458 | Rush Springs Energy Storage (BA) | OK | SWPP | Rush Springs Energy Storage | Rush Springs Energy Storage |  |  | FALSE |  | FLB | CS | Arbitrage | 10 | 20 | 2 | 1.5-2.5h | 2020 | 47 | A | FULL_OUTAGE | 0.90277 | 0.86291 | 0.50926 | -0.0013355 | 0.026554 | 19.91 | ok | -0.0026933 | ok | 1086.25 | 0.18104 | 0.81896 | 6000 | 0 | 4 | 1 | 0.87881 | 2868 | 10 | 10 | 0.050926 | 0.86882 | 20 | 0.67133 | 614.0662 | 39.179 | 0.18999 | 3.5702 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 | RTE_2020: 0.8583; RTE_2024: 0.87472; RTE_2025: 0.85418; EFC_2020: 233.2; EFC_2024: 612; EFC_2025: 241.05; UTI_2020: 4.7832; UTI_2024: 2.7708; UTI_2025: 0.96076 | FULL_OUTAGE
63468 | Hurteau Solar Project Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 1.3 | 1.5 | 1.1538 | <1.5h | 2020 | 409 | C | HYBRID_ARTEFACT | 0.71176 | 0.38701 | 0.42612 | 0.00088667 |  |  | ok | 0.12011 | ok | 800.6667 | 0.13344 | 0.86656 | 6000 | 0 | 0 | 1 | 0.61224 | 0 | 1.3 | 1.3 | 0.0055396 | 0.62837 | 23 | 0.016958 | 4.1701 | 1.1403 | 0.0075691 | 0.8001 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 |  | 0.97516 | 0.80352 | 0.94463 | 0.71204 | 0.48601 | 0.42265 |  | 104.6667 | 182.6667 | 193.3333 | 90.6667 | 127.3333 | 102 |  | 0.080537 | 0.19755 | 0.28963 | 0.14065 | 0.25839 | 0.20417 | LOW_ETA_AND_LOW_UTI
63469 | Alicea Solar Project Hybrid CSG | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 1.5 | 3 | 2 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.94598 | 0.88929 | 0.09364 | -0.0018789 | 7.2098 | 44.1074 | ok | -0.83714 | ok | 573.6667 | 0.095611 | 0.90439 | 6000 | 0 | 1 | 1 | 0.90667 | 29 | 1.5 | 1.5 | 0.0014046 | 0.92647 | 32 | 0.58101 | 40.3933 | 1.2272 | 0.42821 | 0.11742 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.87554 | 0.96739 | 0.85285 | 0.92398 | 0.9692 |  |  | 68 | 148.3333 | 94.6667 | 105.3333 | 157.3333 |  |  | 0.30842 | 0.65757 | 0.28295 | 1.0664 | 1.7241
63470 | McDougle-Mitchell Solar Project Hybrid C | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 2.9 | 5.7 | 1.9655 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 1.0146 | 0.89984 | 0.18979 | -0.00040459 | 5.6214 | -80.5994 | ok | 1.8141 | ok | 459.2982 | 0.07655 | 0.92345 | 6000 | 0 | 0 | 1 | 0.9 | 0 | 2.9 | 2.9 | 0.0055038 | 0.92334 | 36 | 0.5571 | 47.5215 | 1.4438 | 0.50378 | 0.13815 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  | 0.95 | 0.861 | 0.83879 | 0.85605 | 0.95043 | 0.97411 |  | 3.3333 | 111.9298 | 62.9825 | 98.0702 | 77.3684 | 105.614 |  | 0.12346 | 0.50766 | 0.2792 | 0.66006 | 0.65863 | 1.2344
63472 | Cycz Solar Project CSG Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 1.3 | 2.5 | 1.9231 | 1.5-2.5h | 2020 | 393 | C | HYBRID_ARTEFACT | 0.7645 | 0.79899 | -0.025979 | -0.00020407 | -6.9254 | -11.7978 | ok | -2.0621 | ok | 550.8 | 0.0918 | 0.9082 | 6000 | 0 | 0 | 1 | 0.75 | 0 | 1.3 | 1.3 | -0.00033773 | 0.78614 | 36 | 0.034365 | 21.3847 | 0.64971 | 0.2267 | 0.062166 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  | 0.76923 | 0.88385 | 0.85902 | 0.8543 | 0.68132 | 0.83939 |  | 8 | 124.8 | 104.8 | 103.2 | 99.2 | 110.8 |  | 0.21915 | 0.56602 | 0.46459 | 0.58183 | 0.94059 | 1.1009 | LOW_ETA_AND_LOW_UTI
63473 | West A&B Solar Project Hybrid CSG | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 1.8 | 3.5 | 1.9444 | 1.5-2.5h | 2020 | 240 | C | HYBRID_ARTEFACT | 0.93143 | 0.9119 | 0.062861 | -0.00048334 | 4.113 | 110.8715 | ok | -1.4871 | ok | 590.5714 | 0.098429 | 0.90157 | 6000 | 0 | 4 | 1 | 0.92683 | 89.5 | 1.8 | 1.8 | 0.0011315 | 0.9189 | 34 | 0.1408 | 49.4224 | 1.5016 | 0.52393 | 0.14367 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.92632 | 0.9022 | 0.90408 | 0.89002 | 0.95556 |  |  | 50.2857 | 129.1429 | 126.5714 | 124.8571 | 159.7143 |  |  | 0.22807 | 0.5725 | 0.67765 | 1.1322 | 1.7789 | FULL_OUTAGE
63474 | Annese Solar Project Hybrid CSG | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 3.5 | 6.7 | 1.9143 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.92816 | 0.83801 | 0.18869 | -0.0084202 | 5.7129 | -3.2516 | ok | 0.50703 | ok | 479.8507 | 0.079975 | 0.92002 | 6000 | 0 | 0 | 1 | 0.87121 | 0 | 3.5 | 3.5 | 0.0066041 | 0.86631 | 36 | 0.49965 | 61.778 | 1.877 | 0.65491 | 0.17959 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.81152 | 0.81165 | 0.77809 | 0.89947 | 0.91166 |  |  | 69.403 | 116.4179 | 81.6418 | 101.4925 | 110.8955 |  |  | 0.31478 | 0.51609 | 0.32801 | 0.88775 | 1.3353
63475 | Randall Solar Project Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 3.3 | 6 | 1.8182 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.95998 | 0.89712 | 0.12361 | 0.00058122 | 4.6659 | -25.8584 | ok | -2.356 | ok | 369.8333 | 0.061639 | 0.93836 | 6000 | 0 | 0 | 1 | 0.90435 | 0 | 3.2 | 3.2 | 0.0040793 | 0.91043 | 36 | 0.39999 | 59.8771 | 1.8192 | 0.63476 | 0.17406 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.5 | 1.1565 | 0.85849 | 0.91196 | 0.96026 |  |  | 0.83333 | 50.5 | 106.1667 | 91.5 | 120.8333 |  |  | 0.055994 | 0.22387 | 0.42091 | 0.75 | 1.3491
63486 | D'Arrigo Brothers - Phase 4 | CA | CISO | D'Arrigo Brothers | CalCom Energy |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage | 0.5 | 0.8 | 1.6 | 1.5-2.5h | 2019 | 410 | C | HYBRID_ARTEFACT | 1.2724 | 0.84153 | 1.9926 | -0.00017159 |  |  | ok | 0.88899 | ok | 810 | 0.135 | 0.865 | 6000 | 0 | 2 | 1 | 0.83333 | 1.5 | 0.1 | 0.1 | 0.0099631 | 0.84047 | 36 | 0.11993 | 35.4657 | 1.2122 | 0.009083 | 0.3093 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | RTE_2023: 0.83774; RTE_2024: 0.83465; RTE_2025: 0.84921; EFC_2023: 277.5; EFC_2024: 265; EFC_2025: 267.5; UTI_2023: 0.9292; UTI_2024: 0.8663; UTI_2025: 0.93855 | PARTIAL_AVAILABILITY
63510 | Walnut Unified School District Walnut HS | CA | CISO | Solar Integrated Fund VI, LLC | Tesla Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Backup Power | 0.5 | 0.5 | 1 | <1.5h | 2020 | 254 | C | HYBRID_ARTEFACT | 0.95797 | 0.85407 | 0.23364 | 1.4155e-06 | 3.1803 | 11.4844 | ok | -0.6503 | ok | 1130 | 0.18833 | 0.81167 | 6000 | 0 | 13 | 1 | 0.89655 | 74.5 | 0.1 | 0.1 | 0.0011682 | 0.88131 | 23 | 0.75119 | 1.1009 | 0.025086 | 0.0002523 | 0.0016002 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  |  | 0.90805 | 0.88732 | 0.87234 | 0.89764 | 0.86957 |  |  | 158 | 378 | 246 | 228 | 120 |  |  | 0.235 | 0.47222 | 0.33737 | 0.19177 | 0.020197 | FULL_OUTAGE
63522 | Hickory Park Solar Hybrid | GA | SOCO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | LIB | OT | Excess Wind and Solar Generation | 40 | 80 | 2 | 1.5-2.5h | 2022 | 152 | C | HYBRID_ARTEFACT | 0.94086 | 0.83382 | 0.62394 | 0.061503 | -3.3197 | -2.1648 | ok | -0.25952 | ok | 842.4875 | 0.14041 | 0.85959 | 6000 | 0 | 6 | 1 | 0.95652 | 491.5 | 40 | 40 | 0.24958 | 0.8496 | 43 | 0.024488 | 646.0801 | 211.9967 | 0.77735 | 33.8072 | 0.066273 | 0.3373 | 0.0011985 | 0.18593 | 0.0057143 | 0.034286 | 0.0001 | 0.017143 | RTE_2022: 0.92143; RTE_2023: 0.8089; RTE_2024: 0.88694; RTE_2025: 0.81487; EFC_2022: 149.9625; EFC_2023: 238.6875; EFC_2024: 232.1; EFC_2025: 221.7375; UTI_2022: 1.3793; UTI_2023: 1.0914; UTI_2024: 0.94454; UTI_2025: 0.84342 | PARTIAL_AVAILABILITY
63535 | Solar BESS Hybrid | GA | SOCO | Gas South | Cobb Electric Membership Corporation |  |  | TRUE | pv_same_plant | LIB | BL | Arbitrage, Backup Power, Excess Wind and Solar Generation | 1 | 4 | 4 | 2.5-4.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.95822 | 0.86588 | 0.56134 | 0.0035032 | -6.0242 | -149.8016 | ok | -0.064908 | ok | 938.25 | 0.15637 | 0.84363 | 6000 | 0 | 0 | 1 | 0.90265 | 0 | 1 | 1 | 0.0056134 | 0.88893 | 36 | 0.85891 | 53.3256 | 4.8604 | 2.0449 | 0.011905 | 0.08949 | 0.14465 | 0.049641 | 0.0011993 | 0.0078125 | 0.013021 | 0.0043574 | 0.0001 |  | 0.72222 | 0.88138 | 0.85943 | 0.88416 | 0.88561 | 0.8944 |  | 3.25 | 172.75 | 188 | 150.75 | 180 | 243.5 |  | 0.069935 | 0.85306 | 0.78515 | 0.49588 | 0.6297 | 0.94738
63554 | Mohave Electric Cooperative at Joy Lane | AZ | WALC | Sierra Southwest Cooperative | Mohave Electric Cooperative, Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 15 | 60 | 4 | 2.5-4.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 15 | 15
63585 | NY3 Battery | NY | NYIS | Orange & Rockland Utils Inc | Orange & Rockland Utils Inc |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage, Ramping / Spinning Reserve, System Peak Shaving, Load Management | 3 | 12 | 4 | 2.5-4.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.98465 | 0.75097 | 0.51585 | -0.013313 | -2.1452 | -19.6158 | ok | -4.8026 | ok | 219.75 | 0.036625 | 0.96337 | 6000 | 0 | 0 | 1 | 0.905 | 0 | 3 | 3 | 0.015476 | 0.864 | 30 | 0.79503 | 221.3122 | 0.039335 | 0.049452 | 0.012546 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 |  | 0.89474 |  | 0.78571 | 0.69855 | 0.86662 | 0.88034 |  | 1.4167 |  | 1.8333 | 20.0833 | 100.1667 | 96.25 |  | 0.084661 |  | 0 | 0.029114 | 0.46976 | 0.35252
63609 | Allergan | CA | CISO | Sk Holdings Co. Ltd. | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 1.5 | 9 | 6 | >4.5h | 2019 | 193 | A | PARTIAL_AVAILABILITY | 0.8658 | 0.86527 | 0.010984 | -0.00030107 | -9.7856 | -217.013 | ok | -0.68302 | ok | 370.4444 | 0.061741 | 0.93826 | 6000 | 0 | 3 | 1 | 0.83951 | 111.5 | 1.5 | 1.5 | 0.00016476 | 0.86405 | 24 | 0.00071913 | 15.8267 | 8.6553 | 0.045919 | 1.3803 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.90052; RTE_2024: 0.89409; RTE_2025: 0.83687; EFC_2020: 114.6667; EFC_2024: 97.5556; EFC_2025: 100.8889; UTI_2020: 0.68971; UTI_2024: 0.96734; UTI_2025: 0.86658 | PARTIAL_AVAILABILITY
63610 | Baker | CA | CISO | Sk Holdings Co. Ltd. | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 1.2 | 6.3 | 5.25 | >4.5h | 2019 | 158 | A | CELL_DEGRADATION | 0.819 | 0.84023 | -0.14309 | -0.0024871 | -13.0107 | -230.8643 | ok | 0.33503 | ok | 500.2778 | 0.08338 | 0.91662 | 6000 | 0 | 4 | 1 | 0.80147 | 228.6773 | 1.2 | 1.2 | -0.0017171 | 0.83397 | 24 | 0.068364 | 12.6962 | 6.9433 | 0.036836 | 1.1072 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.90043; RTE_2024: 0.87779; RTE_2025: 0.80154; EFC_2020: 166.5079; EFC_2024: 93.4921; EFC_2025: 115.3968; UTI_2020: 1.1507; UTI_2024: 0.92651; UTI_2025: 1.0226 | PARTIAL_AVAILABILITY
63611 | CSU Long Beach | CA | CISO | SUSI Partners AG | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 2.5 | 15 | 6 | >4.5h | 2017 | 110 | A | CELL_DEGRADATION | 0.8125 | 0.83942 | -0.24302 | -0.0077268 | -14.6603 | -275.0669 | ok | 0.10548 | ok | 925.5889 | 0.15426 | 0.84574 | 6000 | 0 | 3 | 1 | 0.79951 | 590.3911 | 2.5 | 2.5 | -0.0060754 | 0.82986 | 24 | 0.12458 | 37.9146 | 20.7347 | 0.11 | 3.3066 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.89973; RTE_2024: 0.88002; RTE_2025: 0.79875; EFC_2020: 177.6667; EFC_2024: 99.2667; EFC_2025: 145.2667; UTI_2020: 1.2278; UTI_2024: 0.98273; UTI_2025: 1.2948 | PARTIAL_AVAILABILITY
63612 | DATS | CA | CISO | Sk Holdings Co. Ltd. | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 1 | 6 | 6 | >4.5h | 2017 | 143 | A | UNDER_DISPATCH | 0.86012 | 0.82779 | 0.20414 | 0.0025677 | -11.9537 | -108.0091 | ok | 0.33932 | ok | 783 | 0.1305 | 0.8695 | 6000 | 0 | 6 | 1 | 0.90357 | 609.1789 | 1 | 1 | 0.0020414 | 0.83812 | 24 | 0.19736 | 6.0872 | 3.329 | 0.017661 | 0.53087 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.89973; RTE_2024: 0.87411; RTE_2025: 0.78222; EFC_2020: 166; EFC_2024: 101.8333; EFC_2025: 58.6667; UTI_2020: 1.1452; UTI_2024: 1.0161; UTI_2025: 0.49885 | PARTIAL_AVAILABILITY
63613 | Downey | CA | CISO | SUSI Partners AG | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 2 | 13 | 6.5 | >4.5h | 2019 |  |  | UNDER_DISPATCH | 0.87656 | 0.84344 | 0.18977 | 0.0024259 | -7.5485 | -55.2288 | ok | 1.7974 | ok | 229.8269 | 0.038304 | 0.9617 | 6000 | 0 | 0 | 1 | 0.87892 | 768.5619 | 2 | 2 | 0.0037954 | 0.85466 | 24 | 0.39077 | 11.4787 | 6.2775 | 0.033304 | 1.0011 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.9; RTE_2024: 0.87844; RTE_2025: 0.81088; EFC_2020: 72.6923; EFC_2024: 100.6154; EFC_2025: 50.4615; UTI_2020: 0.43724; UTI_2024: 1.0041; UTI_2025: 0.43416
63614 | LAWRP | CA | CISO | Sk Holdings Co. Ltd. | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 1 | 5 | 5 | >4.5h | 2019 | 169 | A | CELL_DEGRADATION | 0.84181 | 0.85122 | -0.050064 | -0.0011784 | -14.6083 | -172.2932 | ok | 0.34565 | ok | 541.2 | 0.0902 | 0.9098 | 6000 | 0 | 3 | 1 | 0.8156 | 190.432 | 1 | 1 | -0.00050064 | 0.84651 | 24 | 0.0069857 | 10.2613 | 5.6117 | 0.029772 | 0.8949 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.8998; RTE_2024: 0.89619; RTE_2025: 0.8069; EFC_2020: 183.2; EFC_2024: 103.6; EFC_2025: 117; UTI_2020: 1.266; UTI_2024: 1.0395; UTI_2025: 1.05 | PARTIAL_AVAILABILITY
63615 | Long Beach Convention Center | CA | CISO | Sk Holdings Co. Ltd. | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 1.5 | 8.6 | 5.7333 | >4.5h | 2019 |  |  | CELL_DEGRADATION | 0.80681 | 0.83988 | -0.34121 | -0.0047197 | -12.5422 | -187.5423 | ok | -0.97183 | ok | 470.5233 | 0.078421 | 0.92158 | 6000 | 0 | 0 | 1 | 0.8 | 45.9992 | 1.5 | 1.5 | -0.0051181 | 0.82387 | 24 | 0.29696 | 31.6535 | 17.3106 | 0.091839 | 2.7605 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.90058; RTE_2024: 0.87888; RTE_2025: 0.79974; EFC_2020: 89.5349; EFC_2024: 102.093; EFC_2025: 211.7442; UTI_2020: 0.53854; UTI_2024: 1.0227; UTI_2025: 1.8854
63616 | OCSD | CA | CISO | SUSI Partners AG | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 4.9 | 32.6 | 6.6531 | >4.5h | 2019 | 120 | A | PARTIAL_AVAILABILITY | 0.88272 | 0.87967 | 0.024582 | 0.0012104 | -0.15345 | 11.1561 | ok | -0.54695 | ok | 376.112 | 0.062685 | 0.93731 | 6000 | 0 | 3 | 1 | 0.88277 | 446 | 4.9 | 4.9 | 0.0012045 | 0.8801 | 24 | 0.33851 | 56.698 | 31.007 | 0.1645 | 4.9447 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.9002; RTE_2024: 0.88105; RTE_2025: 0.87912; EFC_2020: 123.4049; EFC_2024: 101.5644; EFC_2025: 99.7239; UTI_2020: 0.74227; UTI_2024: 1.0148; UTI_2025: 0.85516 | PARTIAL_AVAILABILITY
63617 | SOCCD | CA | CISO | SUSI Partners AG | Hybrid-Electric Building Technologies West Los Angeles 1, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving | 1.3 | 7.2 | 5.5385 | >4.5h | 2019 |  |  | CELL_DEGRADATION | 0.8073 | 0.83737 | -0.29831 | -0.002965 | -10.4276 | -198.6628 | ok | -0.91941 | ok | 445.3241 | 0.074221 | 0.92578 | 6000 | 0 | 0 | 1 | 0.80292 | 35.6256 | 1.3 | 1.3 | -0.003878 | 0.82444 | 24 | 0.32013 | 25.3924 | 13.8866 | 0.073673 | 2.2145 | 0.028036 | 0.2475 | 0.0011985 | 0.13253 | 0.0023697 | 0.023697 | 0.0001 | 0.011848 | RTE_2020: 0.90014; RTE_2024: 0.87024; RTE_2025: 0.8033; EFC_2020: 88.8889; EFC_2024: 101.5278; EFC_2025: 203.0556; UTI_2020: 0.53466; UTI_2024: 1.0134; UTI_2025: 1.8065
63685 | Luna Storage | CA | CISO | AES Distributed Energy | AES Distributed Energy |  |  | FALSE |  | LIB | CT | Frequency Regulation, Voltage or Reactive Power Support | 100 | 400 | 4 | 2.5-4.5h | 2022 | 32 | B | PARTIAL_AVAILABILITY | 0.88704 | 0.84873 | 0.54806 | 0.037229 | -4.3194 | -71.0164 | ok | -0.080306 | ok | 1072.15 | 0.17869 | 0.82131 | 6000 | 0 | 2 | 1 | 0.8699 | 13364 | 100 | 100 | 0.54806 | 0.858 | 41 | 0.9698 | 1794.4359 | 719.6493 | 461.735 | 239.9585 | 0.03025 | 0.20169 | 0.1029 | 0.20982 | 0.0025597 | 0.018771 | 0.00958 | 0.019625 | RTE_2022: 0.8676; RTE_2023: 0.86169; RTE_2024: 0.85356; RTE_2025: 0.8536; EFC_2022: 133.0675; EFC_2023: 358.225; EFC_2024: 299.61; EFC_2025: 281.2475; UTI_2022: 1.1027; UTI_2023: 1.2534; UTI_2024: 1.0907; UTI_2025: 0.94027 | PARTIAL_AVAILABILITY
63721 | Cool Springs Solar (Hybrid) | GA | SOCO | Cool Springs Solar, LLC | Cool Springs Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Load Following, System Peak Shaving, Excess Wind and Solar Generation | 40 | 80 | 2 | 1.5-2.5h | 2021 | 59 | C | HYBRID_ARTEFACT | 1.0376 | 0.95389 | 0.5912 | 0.05251 | -0.74943 | -36.933 | ok | 0.20119 | ok | 1377.7875 | 0.22963 | 0.77037 | 6000 | 0 | 6 | 1 | 0.99354 | 2177.5 | 40 | 40 | 0.23648 | 0.96175 | 49 | 0.20391 | 3817.3225 | 243.5551 | 1.181 | 22.1942 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 |  |  | 0.82143 | 0.9226 | 0.99916 | 0.96086 | 0.95849 |  |  | 12.075 | 254.7875 | 384.7625 | 378.375 | 347.7875 |  |  | 0.81136 | 1.2227 | 1.8455 | 1.5403 | 1.3527 | PARTIAL_AVAILABILITY
63722 | Rawhide Prairie Solar Hybrid | CO | PSCO | Greenbacker Renewable Energy Corporation | Greenbacker Renewable Energy Corporation |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 1 | 2 | 2 | 1.5-2.5h | 2021 | 167 | C | HYBRID_ARTEFACT | 0.82907 | 0.83207 | 0.0036514 | -0.0036054 |  |  | ok | 0.39597 | ok | 1104.5 | 0.18408 | 0.81592 | 6000 | 0 | 12 | 1 | 0.84496 | 195.013 | 1 | 1 | 3.6514e-05 | 0.8362 | 26 | 0.00012402 | 61.162 | 3.9023 | 0.018923 | 0.3556 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 |  |  | 0.87573 | 0.84993 | 0.84276 | 0.78519 | 0.84067 |  |  | 225.5 | 320 | 305.5 | 53 | 200.5 |  |  | 1.2957 | 1.4108 | 1.3481 | 0 | 0.76468 | FULL_OUTAGE
63723 | Ho'Ohana Solar 1 | HI | HECO | Ho'Ohana Solar 1 LLC | Ho'Ohana Solar 1 LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving, Excess Wind and Solar Generation | 52 | 208 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.93927 |  |  |  |  | insufficient_history |  | insufficient_history | 156.0962 | 0.026016 | 0.97398 | 6000 | 0 | 0 | 1 | 0.99978 | 0 | 52 | 52 |  |  |  |  | 2240.9919 | 122.5552 | 75.3732 | 175.8954 | 0.081309 | 0.081309 | 0.039802 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034572 | 0.031802 | RTE_2025: 0.95317; EFC_2025: 156.0962; UTI_2025: 0.89849
63727 | Slate Hybrid | CA | CISO | RE Slate 1 LLC | MN8 Energy LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 140.3 | 561 | 3.9986 | 2.5-4.5h | 2022 | 38 | C | HYBRID_ARTEFACT | 0.87239 | 0.84894 | 0.33661 | 0.13038 | -2.6583 | -45.6324 | ok | 0.19401 | ok | 826.5045 | 0.13775 | 0.86225 | 6000 | 1 | 13 | 1 | 0.86159 | 19185.3144 | 140.3 | 140.3 | 0.47226 | 0.85262 | 38 | 0.45419 | 2861.8167 | 1147.7169 | 694.7954 | 382.6926 | 0.03025 | 0.20169 | 0.097662 | 0.20982 | 0.0025597 | 0.018771 | 0.0090389 | 0.019625 | RTE_2022: 0.81125; RTE_2023: 0.84342; RTE_2024: 0.8516; RTE_2025: 0.8637; EFC_2022: 15.6292; EFC_2023: 247.0873; EFC_2024: 266.9358; EFC_2025: 296.852; UTI_2022: 0; UTI_2023: 0.85179; UTI_2024: 0.98382; UTI_2025: 1.1173 | FULL_OUTAGE
63728 | Taos Mesa Energy Facility Hybrid | NM | PNM | Taos Mesa Energy Facility, LLC | Taos Mesa Energy Facility, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 12.5 | 25 | 2 | 1.5-2.5h | 2022 | 261 | C | HYBRID_ARTEFACT | 0.86069 | 0.84841 | 0.10072 | 0.0099219 | -4.191 | -74.985 | ok | 0.13572 | ok | 863.56 | 0.14393 | 0.85607 | 6000 | 0 | 2 | 1 | 0.8469 | 30 | 12.5 | 12.5 | 0.01259 | 0.84943 | 38 | 0.058362 | 226.6837 | 74.3812 | 0.27274 | 11.8616 | 0.066273 | 0.3373 | 0.0011985 | 0.18593 | 0.0057143 | 0.034286 | 0.0001 | 0.017143 | RTE_2022: 0.86898; RTE_2023: 0.862; RTE_2024: 0.83488; RTE_2025: 0.84644; EFC_2022: 44.04; EFC_2023: 304.32; EFC_2024: 259.88; EFC_2025: 255.32; UTI_2022: 1.1568; UTI_2023: 1.4419; UTI_2024: 1.1655; UTI_2025: 0.93011 | PARTIAL_AVAILABILITY
63731 | Neptune Energy Center Hybrid | CO | PSCO | Neptune Energy Center, LLC | Neptune Energy Center, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, System Peak Shaving | 125 | 500 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.8846 | 0.8397 | 0.543 | 0.33728 | -10.1527 | -176.1761 | ok | 0.23799 | ok | 534.914 | 0.089152 | 0.91085 | 6000 | 0 | 0 | 1 | 0.8897 | 0 | 125 | 125 | 0.67875 | 0.84248 | 31 | 0.21144 | 49.6403 | 862.6227 | 113.8456 | 64.7354 | 0.0011993 | 0.31703 | 0.038458 | 0.085813 | 0.0001 | 0.031776 | 0.0033357 | 0.0074766 | RTE_2023: 0.85461; RTE_2024: 0.84615; RTE_2025: 0.82754; EFC_2023: 140.208; EFC_2024: 229.346; EFC_2025: 165.36; UTI_2023: 0.93168; UTI_2024: 0.91677; UTI_2025: 0.54515
63735 | Silverstrand Grid Energy Storage System | CA | CISO | Silverstrand Grid, LLC | Silverstrand Grid, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 11 | 44 | 4 | 2.5-4.5h | 2021 | 60 | B | UNATTRIBUTED | 0.85423 | 0.86319 | -0.15393 | -0.013098 |  |  | insufficient_history | 0.34126 | ok | 1310.9091 | 0.21848 | 0.78152 | 6000 | 0 | 2 | 1 | 0.87154 | 2349.3292 | 11 | 11 | -0.016932 | 0.86269 | 21 | 0.0083627 | 542.6033 | 79.1303 | 36.3873 | 33.1247 | 0.080762 | 0.20113 | 0.075787 | 0.25527 | 0.0070175 | 0.018713 | 0.0068448 | 0.024561 | RTE_2024: 0.85814; RTE_2025: 0.86797; EFC_2024: 283.6364; EFC_2025: 247.2727; UTI_2024: 1.2481; UTI_2025: 1.0049 | FULL_OUTAGE
63737 | Chisholm Grid Energy Storage System | TX | ERCO | Chisholm Grid, LLC | Chisholm Grid, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 100 | 125 | 1.25 | <1.5h | 2021 | 19 | A | THERMAL_AUX | 0.9422 | 0.89922 | 0.2945 | 0.010926 | -0.064721 | 32.6787 | ok | 0.25922 | ok | 2070.704 | 0.34512 | 0.65488 | 6000 | 4 | 4 | 1 | 0.92763 | 7608.4851 | 100 | 100 | 0.2945 | 0.90812 | 49 | 0.74332 | 1121.6622 | 224.9184 | 593.9413 | 32.6071 | 0.053242 | 0.18177 | 0.29486 | 0.087152 | 0.0045593 | 0.016717 | 0.035114 | 0.0075988 |  |  | 0.85817 | 0.92264 | 0.91308 | 0.91152 | 0.87411 |  |  | 56.584 | 636.88 | 531.68 | 546.32 | 299.24 |  |  | 0.36182 | 2.0279 | 1.0427 | 2.5593 | 1.3829 | THERMAL_AUX
63757 | Madero Grid | TX | ERCO | Madero Grid, LLC | Madero Grid, LLC |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 100 | 100 | 1 | <1.5h | 2023 | 439 | A | THERMAL_AUX | 0.87641 | 0.83133 | 0.36863 | 0.29219 | 4.6381 | 135.9276 | ok | -0.45926 | ok | 1637.38 | 0.2729 | 0.7271 | 6000 | 11 | 0 | 1 | 0.85655 | 1493.6822 | 100 | 100 | 0.36863 | 0.8388 | 31 | 0.43544 | 431.6007 | 118.0168 | 653.9759 | 436.6283 | 0.010638 | 0.052071 | 0.19005 | 0.46223 | 0.00089127 | 0.0044563 | 0.019642 | 0.051693 | RTE_2023: 0.82257; RTE_2024: 0.84688; RTE_2025: 0.83562; EFC_2023: 188.59; EFC_2024: 691.7; EFC_2025: 757.09; UTI_2023: 0.51685; UTI_2024: 3.2477; UTI_2025: 3.5351 | THERMAL_AUX
63763 | CES Agawam Tuckahoe Solar Hybrid | MA | ISNE | CES Agawam Tuckahoe Solar LLC | CES Agawam Tuckahoe Solar LLC |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, System Peak Shaving | 2.6 | 5.2 | 2 | 1.5-2.5h | 2021 | 377 | C | HYBRID_ARTEFACT | 1 | 1 | -1.2275e-16 | -1.09e-17 | -2.109e-14 | -19.9571 | ok | -0.10539 | ok | 317.1154 | 0.052853 | 0.94715 | 6000 | 0 | 2 | 1 | 1 | 0 | 2.6 | 2.6 | -3.1915e-18 | 1 | 36 |  | 28.9881 | 0.88072 | 0.3073 | 0.08427 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 1; RTE_2023: 1; RTE_2024: 1; RTE_2025: 1; EFC_2022: 75; EFC_2023: 78.0769; EFC_2024: 79.6154; EFC_2025: 84.4231; UTI_2022: 0.33248; UTI_2023: 0.50846; UTI_2024: 0.82988; UTI_2025: 0.78534 | PARTIAL_AVAILABILITY
63774 | Mount Kisco Landfill Solar & Storage CSG | NY | NYIS | BQ Energy LLC | BQ Energy LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Load Following, Co-Located Renewable Firming, Excess Wind and Solar Generation | 0.7 | 2.1 | 3 | 2.5-4.5h | 2020 | 212 | C | HYBRID_ARTEFACT |  | 0.85397 |  |  |  |  | insufficient_history |  | insufficient_history | 151.9048 | 0.025317 | 0.97468 | 6000 | 0 | 2 | 1.4 | 0.86957 | 83 | 0.5 | 0.7 |  |  |  |  | 11.2914 | 0.0020069 | 0.002523 | 0.00064008 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2025: 0.88611; EFC_2025: 151.9048; UTI_2025: 0.10084 | FULL_OUTAGE
63775 | Tech Square Microgrid | GA | SOCO | Georgia Power Co | Georgia Power Co |  |  | FALSE |  | LIB | BL |  | 0.2 | 0.4 | 2 | 1.5-2.5h | 2020 | 324 | B | FULL_OUTAGE | [8 empty] | insufficient_history | 10 | 0.0016667 | 0.99833 | 6000 | 0 | 34 | 1 | 0.085106 | 51.4179 | 0.2 | 0.2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 |  |  | 0 | 0 | 0 | 0.085106 |  |  |  | 0 | 0 | 0 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | FULL_OUTAGE
63776 | Thunder Wolf Energy Center Hybrid | CO | PSCO | Thunder Wolf Energy Center, LLC | Thunder Wolf Energy Center, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, System Peak Shaving | 100 | 400 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.90489 | 0.84154 | 0.83382 | 0.14507 | 0.91062 | 47.0278 | ok | 0.85627 | ok | 578.6525 | 0.096442 | 0.90356 | 6000 | 0 | 0 | 1 | 0.86289 | 0 | 100 | 100 | 0.83382 | 0.84269 | 31 | 0.19518 | 49.6476 | 862.7502 | 113.8624 | 64.745 | 0.0011993 | 0.31703 | 0.038458 | 0.085813 | 0.0001 | 0.031776 | 0.0033357 | 0.0074766 | RTE_2023: 0.8536; RTE_2024: 0.84487; RTE_2025: 0.83292; EFC_2023: 139.035; EFC_2024: 236.265; EFC_2025: 203.3525; UTI_2023: 0.91131; UTI_2024: 0.94031; UTI_2025: 0.71247
63804 | Partridgeville Hybrid CSG | MA | ISNE | Partridgeville Road Solar 1, LLC | Partridgeville Road Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 2 | 3.9 | 1.95 | 1.5-2.5h | 2020 | 381 | C | HYBRID_ARTEFACT | 0.85026 | 0.81116 | 0.042268 | 0.00054633 | -10.2197 | -124.9275 | ok | -0.2453 | ok | 343.0769 | 0.057179 | 0.94282 | 6000 | 0 | 0 | 1 | 0.74194 | 0 | 2 | 2 | 0.00084537 | 0.85924 | 36 | 0.35957 | 16.6325 | 0.50533 | 0.17632 | 0.048351 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  | 0.70994 |  | 0.77353 | 0.88434 | 0.86692 | 0.81387 |  | 65.8974 | 0 | 67.4359 | 94.1026 | 58.4615 | 57.1795 |  | 1.0441 | 0 | 0.29895 | 0.46686 | 0.55723 | 0.58666 | LOW_ETA_AND_LOW_UTI
63805 | Williamsville Hybrid CSG | MA | ISNE | 147 Williamsville Solar 1, LLC | 147 Williamsville Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 3.3 | 6.7 | 2.0303 | 1.5-2.5h | 2021 | 362 | C | HYBRID_ARTEFACT | 0.83948 | 0.81636 | 0.060767 | -0.0012595 | -2.3483 | -98.889 | ok | 20.2774 | ok | 202.9851 | 0.033831 | 0.96617 | 6000 | 0 | 0 | 1 | 0.93827 | 0 | 3.3 | 3.3 | 0.0020053 | 0.8327 | 36 | 0.23273 | 41.8189 | 1.2706 | 0.44332 | 0.12157 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.5942; RTE_2023: 0.6996; RTE_2024: 0.90859; RTE_2025: 0.88136; EFC_2022: 6.1194; EFC_2023: 52.8358; EFC_2024: 74.1791; EFC_2025: 69.8507; UTI_2022: 0.027126; UTI_2023: 0.27004; UTI_2024: 0.57855; UTI_2025: 0.68107 | LOW_ETA_AND_LOW_UTI
63834 | Gateway Energy Storage System | CA | CISO | Gateway Energy Storage, LLC | Gateway Energy Storage, LLC |  |  | FALSE |  | LIB | BL | Load Following, Ramping / Spinning Reserve | 250 | 1000 | 4 | 2.5-4.5h | 2020 | 4 | B | UNDER_DISPATCH | 0.86801 | 0.83184 | 0.16018 | -0.57365 | -1.7726 | -23.1259 | ok | 0.076275 | ok | 1994.9877 | 0.3325 | 0.6675 | 6000 | 0 | 4 | 1 | 0.88041 | 401413.4059 | 250 | 250 | 0.40044 | 0.87239 | 63 | 0.50423 | 6221.0095 | 907.2378 | 319.3079 | 379.7787 | 0.080762 | 0.20113 | 0.059078 | 0.25527 | 0.0070175 | 0.018713 | 0.0052389 | 0.024561 |  | 0.73147 | 0.85633 | 0.89207 | 0.88544 | 0.85667 | 0.86145 |  | 61.648 | 406.772 | 911.976 | 322.5186 | 173.7471 | 118.326 |  | 0.17312 | 0.38727 | 1.1601 | 1.1303 | 0.86528 | 0.55212 | PARTIAL_AVAILABILITY
63843 | Johanna Energy Center, LLC | CA | CISO | Johanna Energy Center, LLC | Johanna Energy Center, LLC |  |  | TRUE | colocated_firming | LIB | CS | Frequency Regulation | 80 | 320 | 4 | 2.5-4.5h | 2021.75 |  |  | HYBRID_ARTEFACT | 0.91242 | 0.88276 | 0.49972 | 0.086707 | -1.6256 | -45.4648 | ok | 0.69009 | ok | 2792.7257 | 0.46545 | 0.53455 | 6000 | 0 | 0 | 1 | 0.88377 | 0 | 80 | 80 | 0.39978 | 0.88274 | 24 | 0.054775 | 1473.6487 | 590.9992 | 456.6439 | 197.0617 | 0.03025 | 0.20169 | 0.12131 | 0.20982 | 0.0025597 | 0.018771 | 0.011537 | 0.019625 | RTE_2024: 0.87803; RTE_2025: 0.88774; EFC_2024: 698.0714; EFC_2025: 291.3031; UTI_2024: 2.191; UTI_2025: 1.0624
63848 | Solar Blue | CA | CISO | Westlands Solar Blue | Westlands Solar Blue |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation | 225 | 900 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.89726 | 0.89035 | 0.13411 | 0.15735 |  |  | insufficient_history | -0.19052 | ok | 662.6033 | 0.11043 | 0.88957 | 6000 | 1 | 0 | 1 | 0.91987 | 0 | 225 | 225 | 0.30176 | 0.8907 | 23 | 0.022033 | 4974.5036 | 1994.9991 | 1560.2102 | 665.2088 | 0.03025 | 0.20169 | 0.1226 | 0.20982 | 0.0025597 | 0.018771 | 0.011677 | 0.019625 | RTE_2024: 0.8964; RTE_2025: 0.88523; EFC_2024: 326.7844; EFC_2025: 335.8189; UTI_2024: 1.3592; UTI_2025: 1.1759
63849 | Chestnut | CA | CISO | Chestnut Westside LLC | Chestnut Westside LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation | 135 | 540 | 4 | 2.5-4.5h | 2023 | 25 | C | HYBRID_ARTEFACT | 0.95066 | 0.89023 | 1.2075 | 0.040286 |  |  | insufficient_history | -0.52086 | ok | 743.7838 | 0.12396 | 0.87604 | 6000 | 1 | 4 | 1 | 0.89833 | 6090.5 | 135 | 135 | 1.6301 | 0.89057 | 23 | 0.52044 | 3054.4769 | 1224.9823 | 958.0104 | 408.4558 | 0.03025 | 0.20169 | 0.1226 | 0.20982 | 0.0025597 | 0.018771 | 0.011677 | 0.019625 | RTE_2024: 0.89539; RTE_2025: 0.88591; EFC_2024: 352.5833; EFC_2025: 361.8185; UTI_2024: 1.4426; UTI_2025: 1.1976 | ELEVATED_P_AUX
63859 | Golden Field Solar III, LLC | CA | CISO | Golden Fields Solar III, LLC | Golden Fields Solar III, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 147 | 147 | 1 | <1.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.87827 | 0.89583 | -0.066612 | -0.35693 |  |  | insufficient_history | 0.16696 | ok | 1937.3265 | 0.32289 | 0.67711 | 6000 | 1 | 0 | 1 | 0.92155 | 0 | 147 | 147 | -0.09792 | 0.89552 | 22 | 0.026146 | 16323.4942 | 446.3491 | 7.0143 | 782.9743 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.95541; RTE_2025: 0.85185; EFC_2024: 871.4966; EFC_2025: 1065.8299; UTI_2024: 1.495; UTI_2025: 1.4803
63891 | Saticoy | CA | CISO | Ventura Energy Storage, LLC | Ventura Energy Storage, LLC |  |  | TRUE | rte_gt_1 | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 100 | 400 | 4 | 2.5-4.5h | 2021 | 89 | C | HYBRID_ARTEFACT | 0.89344 | 0.86475 | 0.45391 | 0.53383 | 0.5843 | 21.8534 | ok | 0.45473 | ok | 1348.8675 | 0.22481 | 0.77519 | 6000 | 0 | 2 | 1 | 0.86234 | 1006.5 | 100 | 100 | 0.45391 | 0.86599 | 57 | 0.11245 | 4852.0114 | 707.5906 | 261.9015 | 296.2044 | 0.080762 | 0.20113 | 0.061936 | 0.25527 | 0.0070175 | 0.018713 | 0.0055095 | 0.024561 |  |  | 0.88265 | 0.87259 | 0.85642 | 0.85698 | 0.86259 |  |  | 232.5175 | 318.055 | 253.045 | 276.1325 | 269.1175 |  |  | 1.4959 | 1.1362 | 0.95133 | 1.1906 | 1.0657 | PARTIAL_AVAILABILITY
63892 | Lily Solar Hybrid | TX | ERCO | Lily Solar, LLC | Lily Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 55.2 | 80.5 | 1.4583 | <1.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.91371 | 0.7779 | 0.25259 | -0.037691 | -0.60966 | 1.7831 | ok | -2.1465 | ok | 451.8907 | 0.075315 | 0.92468 | 6000 | 2 | 0 | 1 | 0.90236 | 0 | 50 | 50 | 0.13943 | 0.80875 | 51 | 0.78627 | 339.8115 | 68.1398 | 34.5873 | 9.8784 | 0.053242 | 0.18177 | 0.074814 | 0.087152 | 0.0045593 | 0.016717 | 0.0067497 | 0.0075988 |  |  | 0.73297 | 0.73697 | 0.84401 | 0.79483 | 0.82445 |  |  | 21.0921 | 65.8421 | 121.7888 | 101.6894 | 141.4783 |  |  | 0.29963 | 0.27043 | 0.57148 | 0.44145 | 0.6995
63900 | AES Waikoloa Solar Hybrid | HI | HECO | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 30 | 120 | 4 | 2.5-4.5h | 2023 | 80 | C | HYBRID_ARTEFACT | 1.2168 | 0.97376 | 2.8114 | 0.0020378 |  |  | ok | -0.31148 | ok | 591.0917 | 0.098515 | 0.90148 | 6000 | 0 | 2 | 1 | 0.98594 | 1206 | 30 | 30 | 0.84342 | 0.97001 | 24 | 0.089809 | 22.6055 | 392.8259 | 53.1358 | 29.4796 | 0.0011993 | 0.31703 | 0.039378 | 0.085813 | 0.0001 | 0.031776 | 0.0034189 | 0.0074766 | RTE_2024: 1.0055; RTE_2025: 0.93901; EFC_2024: 285.4667; EFC_2025: 305.625; UTI_2024: 1.0586; UTI_2025: 1.0422 | PARTIAL_AVAILABILITY
63905 | Azure Sky Solar | TX | ERCO | Azure Sky Solar Project, LLC | Azure Sky Solar Project, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 91.2 | 80.5 | 0.88268 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.9299 | 0.65298 | 0.68055 | 0.036881 | -1.2279 | -3.1597 | ok | 0.75026 | ok | 717.1789 | 0.11953 | 0.88047 | 6000 | 4 | 0 | 1 | 0.80488 | 0 | 51.7 | 51.7 | 0.62066 | 0.71329 | 41 | 0.97354 | 146.7233 | 40.12 | 66.7951 | 148.4324 | 0.010638 | 0.052071 | 0.066046 | 0.46223 | 0.00089127 | 0.0044563 | 0.0059015 | 0.051693 | RTE_2022: 0.49118; RTE_2023: 0.67021; RTE_2024: 0.68349; RTE_2025: 0.77856; EFC_2022: 43.4149; EFC_2023: 155.9627; EFC_2024: 174.472; EFC_2025: 343.3292; UTI_2022: 0.32577; UTI_2023: 0.28775; UTI_2024: 0.79741; UTI_2025: 1.5321
63913 | Dodge Flat | NV | NEVP | Dodge Flat Solar, LLC | Dodge Flat Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 50 | 200 | 4 | 2.5-4.5h | 2022 | 91 | C | HYBRID_ARTEFACT | 0.9346 | 0.90165 | 0.32688 | 0.058461 | 0.57722 | 4.5797 | ok | -0.18998 | ok | 1065.06 | 0.17751 | 0.82249 | 6000 | 0 | 6 | 1 | 0.98942 | 3274 | 50 | 50 | 0.16344 | 0.91356 | 45 | 0.29134 | 36.8256 | 639.9363 | 80.2732 | 48.024 | 0.0011993 | 0.31703 | 0.036624 | 0.085813 | 0.0001 | 0.031776 | 0.0031705 | 0.0074766 | RTE_2022: 0.92329; RTE_2023: 0.91553; RTE_2024: 0.9059; RTE_2025: 0.91125; EFC_2022: 226.29; EFC_2023: 295.775; EFC_2024: 278.31; EFC_2025: 264.685; UTI_2022: 1.1027; UTI_2023: 1.1077; UTI_2024: 1.1622; UTI_2025: 1.0613 | PARTIAL_AVAILABILITY
63930 | Cal Flats BESS | CA | CISO | Arevon Energy, Inc. | Arevon Energy, Inc. |  |  | TRUE | rte_gt_1,colocated_firming | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Co-Located Renewable Firming, Load Management, Voltage or Reactive Power Support | 60 | 242 | 4.0333 | 2.5-4.5h | 2021 | 427 | C | HYBRID_ARTEFACT | 0.89865 | 0.83936 | 0.39703 | 0.047816 | -3.1229 | -57.0042 | ok | -0.051025 | ok | 1053.7686 | 0.17563 | 0.82437 | 6000 | 0 | 2 | 1 | 0.84356 | 2346 | 60 | 60 | 0.23822 | 0.87008 | 50 | 0.0072056 | 2795.9391 | 407.7444 | 157.2343 | 170.6858 | 0.080762 | 0.20113 | 0.064357 | 0.25527 | 0.0070175 | 0.018713 | 0.00574 | 0.024561 |  |  | 2.3814 | 0.91292 | 0.84043 | 0.83374 | 0.83786 |  |  | 26.186 | 272.624 | 275.7231 | 244.4587 | 234.7769 |  |  | 0.50164 | 1.0783 | 0.96031 | 0.94949 | 0.93686 | PARTIAL_AVAILABILITY
63933 | Dry Lake Solar Energy Center | NV | NEVP | Nevada Power Co | Nevada Power Co |  |  | TRUE | pv_same_plant | LIB | CS |  | 100 | 150 | 1.5 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.91803 | 0.88895 | 0.53381 | 0.24872 |  |  | insufficient_history | 0.30721 | ok | 1457.7067 | 0.24295 | 0.75705 | 6000 | 5 | 0 | 1 | 0.89458 | 0 | 100 | 100 | 0.53381 | 0.88891 | 20 | 0.017222 | 16801.9582 | 459.4322 | 5.5449 | 293.0634 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2024: 0.89261; RTE_2025: 0.88639; EFC_2024: 594.0467; EFC_2025: 863.66; UTI_2024: 3.4993; UTI_2025: 3.2175
63943 | Coso Battery Storage | CA | CISO | John Hancock | Arevon Asset Management |  |  | FALSE |  | LIB | CS | Frequency Regulation, System Peak Shaving | 60 | 240 | 4 | 2.5-4.5h | 2022 | 52 | A | CELL_DEGRADATION | 0.946 | 0.85862 | 1.5606 | 0.13115 | -1.6376 | -9.0035 | ok | -0.020273 | ok | 1262.5542 | 0.21043 | 0.78957 | 6000 | 1 | 2 | 1 | 0.91732 | 5206.002 | 60 | 60 | 0.93635 | 0.86278 | 45 | 0.4073 | 1230.3576 | 493.4286 | 304.4395 | 164.5279 | 0.03025 | 0.20169 | 0.099346 | 0.20982 | 0.0025597 | 0.018771 | 0.0092124 | 0.019625 | RTE_2022: 0.85824; RTE_2023: 0.86607; RTE_2024: 0.8474; RTE_2025: 0.87416; EFC_2022: 230.2833; EFC_2023: 325.0833; EFC_2024: 295.8083; EFC_2025: 411.3792; UTI_2022: 1.1121; UTI_2023: 1.1419; UTI_2024: 1.1251; UTI_2025: 1.0936 | ELEVATED_P_AUX
63995 | Trenton | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | FALSE |  | LIB | CS | Load Management | 11 | 10.1 | 0.91818 | <1.5h | 2021 | 161 | A | UNATTRIBUTED | 0.67784 | 0.52735 | 0.037079 | 0.0048012 |  |  | insufficient_history |  | insufficient_history | 64.1997 | 0.0107 | 0.9893 | 6000 | 0 | 4 | 1 | 0.74242 | 206.0711 | 11 | 11 | 0.0040787 | 0.65359 | 13 | 0.21867 | 5.1445 | 0.18756 | 0.002523 | 0.059821 | 0.15484 | 0.10609 | 0.0011985 | 0.10609 | 0.014019 | 0.0093458 | 0.0001 | 0.0093458 | RTE_2024: 0.60755; RTE_2025: 0.53521; EFC_2024: 15.9406; EFC_2025: 15.0495; UTI_2024: 0.021425; UTI_2025: 0.015513 | LOW_ETA_AND_LOW_UTI
63996 | Cape San Blas | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 5.5 | 14.3 | 2.6 | 2.5-4.5h | 2022 | 206 | A | THERMAL_AUX | 0.82172 | 0.78838 | 0.00080398 | 0.0052007 | -11.67 | 260.4586 | ok | 3.345 | ok | 138.4266 | 0.023071 | 0.97693 | 6000 | 0 | 0 | 1 | 0.92222 | 91.2418 | 5.5 | 5.5 | 4.4219e-05 | 0.84536 | 22 | 6.2572e-05 | 0.28624 | 4.9741 | 1.3735 | 0.37328 | 0.0011993 | 0.31703 | 0.077161 | 0.085813 | 0.0001 | 0.031776 | 0.0069795 | 0.0074766 | RTE_2024: 0.87945; RTE_2025: 0.78676; EFC_2024: 44.8951; EFC_2025: 29.9301; UTI_2024: 0.12146; UTI_2025: 0.11427 | THERMAL_AUX
63998 | Jennings Energy Storage Facility | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 5.5 | 5.5 | 1 | <1.5h | 2022 | 177 | A | CAPACITY_FADE | 0.59505 | 0.57126 | -0.0055796 | -0.011851 | -40.5547 | -297.4297 | ok | -14.1361 | ok | 141.6364 | 0.023606 | 0.97639 | 6000 | 0 | 0 | 1 | 0.76786 | 145.3104 | 5.5 | 5.5 | -0.00030688 | 0.6737 | 20 | 0.010826 | 15.1376 | 0.0044152 | 0.52866 | 0.26403 | 0.20148 | 0.0011993 | 0.10236 | 0.20148 | 0.01875 | 0.0001 | 0.0095243 | 0.01875 | RTE_2024: 0.6738; RTE_2025: 0.61818; EFC_2024: 45.8182; EFC_2025: 30.9091; UTI_2024: 0.1047; UTI_2025: 0.075997 | LOW_ETA_AND_LOW_UTI
63999 | Micanopy Energy Storage Facility | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 8.3 | 11.7 | 1.4096 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.93355 | 0.66454 | 0.20038 | -0.0022891 | -8.5505 | -11.8579 | ok | 7.5502 | ok | 129.4444 | 0.021574 | 0.97843 | 6000 | 0 | 1 | 1 | 0.84375 | 7655.9013 | 8.3 | 8.3 | 0.016632 | 0.72663 | 21 | 0.72681 | 24.7706 | 0.0072248 | 0.86509 | 0.43205 | 0.20148 | 0.0011993 | 0.10236 | 0.20148 | 0.01875 | 0.0001 | 0.0095243 | 0.01875 | RTE_2024: 0.76944; RTE_2025: 0.60225; EFC_2024: 47.3504; EFC_2025: 22.906; UTI_2024: 0.10538; UTI_2025: 0.052114
64000 | Amaterasu LLC | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 3.2 | 6 | 1.875 | 1.5-2.5h | 2021 | 378 | C | HYBRID_ARTEFACT | 0.86535 | 0.85116 | 0.0064016 | -0.014114 | 4.578 | 136.4041 | ok | 2.5608 | ok | 324 | 0.054 | 0.946 | 6000 | 0 | 2 | 1 | 0.95935 | 0 | 3.2 | 3.2 | 0.00020485 | 0.90749 | 34 | 0.0088797 | 45.6207 | 1.3861 | 0.48363 | 0.13262 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.39706; RTE_2023: 0.89636; RTE_2024: 0.91497; RTE_2025: 0.90014; EFC_2022: 22.5; EFC_2023: 106.6667; EFC_2024: 89.6667; EFC_2025: 105.1667; UTI_2022: 0.099744; UTI_2023: 0.65468; UTI_2024: 0.8748; UTI_2025: 1.1732 | PARTIAL_AVAILABILITY
64042 | Montague Road Solar | MA | ISNE | Montague Road Solar, LLC | Montague Road Solar, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CT | Co-Located Renewable Firming, Excess Wind and Solar Generation | 2 | 2 | 1 | <1.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2 | 2
64050 | Fort Bragg - Camp Mackall PV BESS System | NC | CPLE | US Army Fort Bragg | Ameresco Federal Solutions |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 2 | 2 | 1 | <1.5h | 2023 | 325 | C | HYBRID_ARTEFACT |  | 0.55208 |  |  |  |  | insufficient_history |  | insufficient_history | 13.5 | 0.00225 | 0.99775 | 6000 | 0 | 3 | 1 | 0.83333 | 0.5 | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.13542 | 0.11205 | 0.051734 | 0.22481 | 0.012126 | 0.009903 | 0.0045514 | 0.021221 | RTE_2023: 0.30233; RTE_2024: 0.2449; RTE_2025: 0.18182; EFC_2023: 6.5; EFC_2024: 6; EFC_2025: 1; UTI_2023: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
64084 | Blanchard Road 1 Community Solar | NY | NYIS | OYA Blanchard Road LLC | OYA Blanchard Road LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 5 | 15 | 3 | 2.5-4.5h | 2019 | 224 | C | FULL_OUTAGE |  | 1 |  |  |  |  | insufficient_history |  | insufficient_history | 27.7333 | 0.0046222 | 0.99538 | 6000 | 0 | 12 | 1 | 1 | 66.5 | 3.8 | 3.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0.12376 | 0.14367 | 0.0056521 | 0.12376 | 0.01101 | 0.012925 | 0.00047374 | 0.01101 | RTE_2024: 1; EFC_2024: 27.7333; EFC_2025: 0; UTI_2024: 0.044491; UTI_2025: 0 | FULL_OUTAGE
64087 | Blanchard Road 2 Community Solar | NY | NYIS | OYA Blanchard Road 2 LLC | OYA Blanchard Road 2 LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 5 | 15 | 3 | 2.5-4.5h | 2019 | 238 | C | FULL_OUTAGE |  | 1 |  |  |  |  | insufficient_history |  | insufficient_history | 21.3333 | 0.0035556 | 0.99644 | 6000 | 0 | 12 | 1 | 1 | 49.5 | 3.8 | 3.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0.12376 | 0.14367 | 0.0056493 | 0.12376 | 0.01101 | 0.012925 | 0.0004735 | 0.01101 | RTE_2024: 1; EFC_2024: 21.3333; EFC_2025: 0; UTI_2024: 0.045847; UTI_2025: 0 | FULL_OUTAGE
64089 | Ignacio Grid Energy Storage System | TX | ERCO | Ignacio Grid, LLC | Ignacio Grid, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 100 | 100 | 1 | <1.5h | 2023 |  |  | THERMAL_AUX | 0.87735 | 0.83431 | 0.41668 | 0.1835 | 6.2439 | 156.2702 | ok | -0.11627 | ok | 1735.89 | 0.28931 | 0.71069 | 6000 | 11 | 0 | 1 | 0.85707 | 309.1047 | 100 | 100 | 0.41668 | 0.83808 | 31 | 0.35629 | 433.7921 | 118.616 | 657.2964 | 438.8452 | 0.010638 | 0.052071 | 0.19005 | 0.46223 | 0.00089127 | 0.0044563 | 0.019642 | 0.051693 | RTE_2023: 0.81728; RTE_2024: 0.84769; RTE_2025: 0.83763; EFC_2023: 288.45; EFC_2024: 683.89; EFC_2025: 763.55; UTI_2023: 1.0823; UTI_2024: 3.153; UTI_2025: 3.5718
64090 | NYS Rte 12 Community Solar | NY | NYIS | OYA NYS Rte 12 LLC | OYA NYS Rte 12 LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 5 | 15 | 3 | 2.5-4.5h | 2019 | 256 | C | FULL_OUTAGE |  | 1 |  |  |  |  | insufficient_history |  | insufficient_history | 13.4667 | 0.0022444 | 0.99776 | 6000 | 0 | 12 | 1 | 1 | 35.5 | 3.8 | 3.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0.12376 | 0.14367 | 0.0056521 | 0.12376 | 0.01101 | 0.012925 | 0.00047374 | 0.01101 | RTE_2024: 1; EFC_2024: 13.4667; EFC_2025: 0; UTI_2024: 0.013903; UTI_2025: 0 | FULL_OUTAGE
64092 | Great Lakes Seaway Community Solar | NY | NYIS | OYA Great Lakes Seaway LLC | OYA Great Lakes Seaway LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 5 | 15 | 3 | 2.5-4.5h | 2019 | 216 | C | FULL_OUTAGE |  | 1 |  |  |  |  | insufficient_history |  | insufficient_history | 30.0667 | 0.0050111 | 0.99499 | 6000 | 0 | 12 | 1 | 1 | 77 | 3.8 | 3.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0.12376 | 0.14367 | 0.0056521 | 0.12376 | 0.01101 | 0.012925 | 0.00047374 | 0.01101 | RTE_2024: 1; EFC_2024: 30.0667; EFC_2025: 0; UTI_2024: 0.044103; UTI_2025: 0 | FULL_OUTAGE
64103 | Desert Harvest II LLC | CA | CISO | Desert Harvest II LLC | Desert Harvest II LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 35 | 140 | 4 | 2.5-4.5h | 2021 | 402 | C | HYBRID_ARTEFACT | 0.94985 | 0.77789 | 1.0404 | -0.036494 | 3.5857 | 11.326 | ok | 0.35708 | ok | 714.8714 | 0.11915 | 0.88085 | 6000 | 9 | 0 | 1 | 0.84571 | 0 | 35 | 35 | 0.36413 | 0.8299 | 55 | 0.69797 | 988.635 | 144.1771 | 53.06 | 60.3539 | 0.080762 | 0.20113 | 0.061605 | 0.25527 | 0.0070175 | 0.018713 | 0.005478 | 0.024561 |  |  | 0.77931 | 0.83773 | 0.72553 | 0.84404 | 0.87516 |  |  | 100.7143 | 222.7214 | 82.5857 | 149.8714 | 158.9786 |  |  | 0.61581 | 0.81653 | 0.29385 | 0.5273 | 0.59334 | ELEVATED_P_AUX
64105 | Maverick Solar 6, LLC | CA | CISO | Maverick Solar 6, LLC | Maverick Solar 6, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 50 | 200 | 4 | 2.5-4.5h | 2022 | 408 | C | HYBRID_ARTEFACT | 0.86791 | 0.88705 | -0.14875 | 0.20127 | -9.2272 | -119.3714 | ok | 0.20074 | ok | 777.205 | 0.12953 | 0.87047 | 6000 | 7 | 3 | 1 | 0.82207 | 5831.75 | 50 | 50 | -0.074377 | 0.88077 | 42 | 0.34466 | 750.4449 | 300.9621 | 189.3228 | 100.3522 | 0.03025 | 0.20169 | 0.10109 | 0.20982 | 0.0025597 | 0.018771 | 0.0093926 | 0.019625 | RTE_2022: 0.86475; RTE_2023: 0.94072; RTE_2024: 0.86593; RTE_2025: 0.84883; EFC_2022: 108.63; EFC_2023: 224.455; EFC_2024: 215.725; EFC_2025: 228.395; UTI_2022: 0.71558; UTI_2023: 0.84204; UTI_2024: 0.84437; UTI_2025: 0.83495 | PARTIAL_AVAILABILITY
64128 | Ware Palmer Road Solar LLC CSG | MA | ISNE | Ware Palmer Road Solar LLC | Ware Palmer Road Solar LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 2 | 4.5 | 2.25 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 1.0047 | 0.55504 | 0.19813 | -0.0003129 | -33.1872 | -11.5973 | ok |  | insufficient_history | 378.4444 | 0.063074 | 0.93693 | 6000 | 0 | 0 | 1 | 0.99213 | 0 | 2 | 2 | 0.0039627 | 0.91867 | 28 | 0.96596 | 1.9009 | 0.057752 | 0.020151 | 0.0055259 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.94647; RTE_2023: 0.96187; RTE_2024: 0.34426; RTE_2025: 0.34426; EFC_2022: 172.8889; EFC_2023: 196.2222; EFC_2024: 4.6667; EFC_2025: 4.6667; UTI_2022: 0.76643; UTI_2023: 1.2512; UTI_2024: 0.046348; UTI_2025: 0.046298
64129 | East Brookfield Adams Road Solar LLC CSG | MA | ISNE | East Brookfield Adams Road Solar LLC | East Brookfield Adams Road Solar LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 3.1 | 6.3 | 2.0323 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.97088 | 0.95569 | 0.078566 | 0.0023719 | -2.4105 | -105.3243 | ok | -0.52656 | ok | 557.9365 | 0.092989 | 0.90701 | 6000 | 0 | 0 | 1 | 0.99408 | 0 | 3 | 3 | 0.0024355 | 0.95804 | 24 | 0.043096 | 103.1217 | 3.1331 | 1.1212 | 0.29978 | 0.14392 | 0.082709 | 0.023972 | 0.025567 | 0.01295 | 0.0071942 | 0.0020478 | 0.0021583 | RTE_2022: 0.96362; RTE_2023: 0.96752; RTE_2025: 0.94753; EFC_2022: 130.3175; EFC_2023: 226.9841; EFC_2025: 200.6349; UTI_2022: 0.5777; UTI_2023: 1.1881; UTI_2025: 1.9947
64140 | BWC Stony Brook, LLC Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 0.7 | 1.4 | 2 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.93082 | 0.81579 | 0.27729 | 0.0010579 | 0.27518 | -144.6866 | ok | 2.1744 | ok | 492.1429 | 0.082024 | 0.91798 | 6000 | 0 | 0 | 1 | 0.88889 | 0 | 0.7 | 0.7 | 0.001941 | 0.8527 | 35 | 0.52687 | 12.8308 | 0.38983 | 0.13602 | 0.0373 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.7381 | 0.91489 | 0.82979 | 0.83085 | 0.89888 |  |  | 88.5714 | 30.7143 | 139.2857 | 119.2857 | 114.2857 |  |  | 0.78788 | 0.13616 | 0.80524 | 0.99309 | 1.3367
64147 | ZPD-PT Solar Project 2017-038 Hybrid LLC | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 3.5 | 6.7 | 1.9143 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.98358 | 0.88871 | 0.18436 | 0.00019695 | -0.2909 | 23.9847 | ok | 4.3765 | ok | 389.1045 | 0.064851 | 0.93515 | 6000 | 0 | 0 | 1 | 0.97714 | 0 | 3.5 | 3.5 | 0.0064526 | 0.91573 | 36 | 0.21223 | 47.5215 | 1.4438 | 0.50378 | 0.13815 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.96226 | 0.92946 | 0.89882 | 0.90068 | 0.96354 |  |  | 7.6119 | 66.8657 | 114.0299 | 117.7612 | 82.8358 |  |  | 0.045997 | 0.29642 | 0.63271 | 0.75858 | 0.74972
64148 | Fish Springs | NV | NEVP | Fish Springs Ranch Solar, LLC | Fish Springs Ranch Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 25 | 100 | 4 | 2.5-4.5h | 2022 | 424 | C | HYBRID_ARTEFACT | 0.88043 | 0.87831 | -0.093461 | 0.30113 | -0.47258 | -5.9027 | ok | 0.048124 | ok | 1011.16 | 0.16853 | 0.83147 | 6000 | 0 | 4 | 1 | 0.76215 | 1944 | 25 | 25 | -0.023365 | 0.88981 | 44 | 0.0021968 | 17.211 | 299.0834 | 37.5168 | 22.4447 | 0.0011993 | 0.31703 | 0.036624 | 0.085813 | 0.0001 | 0.031776 | 0.0031705 | 0.0074766 | RTE_2022: 0.91049; RTE_2023: 0.72753; RTE_2024: 0.89744; RTE_2025: 0.88708; EFC_2022: 233.34; EFC_2023: 262.1; EFC_2024: 287.35; EFC_2025: 228.37; UTI_2022: 1.008; UTI_2023: 0.99201; UTI_2024: 1.1405; UTI_2025: 0.97832 | PARTIAL_AVAILABILITY
64164 | Azure Sky Wind Project, LLC Hybrid | TX | ERCO | Azure Sky Wind Project, LLC | Azure Sky Wind Project, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 120 | 190 | 1.5833 | 1.5-2.5h | 2023 | 31 | A | UNATTRIBUTED | 0.9122 | 0.76329 | 1.0928 | -0.071258 |  |  | insufficient_history |  | insufficient_history | 304.7053 | 0.050784 | 0.94922 | 6000 | 0 | 0 | 1 | 0.82142 | 5173.0428 | 121.8 | 121.8 | 1.3114 | 0.77246 | 12 | 0.98205 | 982.5151 | 161.1952 | 289.0671 | 274.1959 | 0.031828 | 0.092476 | 0.12129 | 0.404 | 0.0026954 | 0.0080863 | 0.011534 | 0.043127 | RTE_2025: 0.77246; EFC_2025: 304.7053; UTI_2025: 1.1087 | ELEVATED_P_AUX
64170 | BWC Muddy Brook, LLC Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 0.9 | 1.8 | 2 | 1.5-2.5h | 2021 | 258 | C | HYBRID_ARTEFACT | 0.88556 | 0.87609 | 0.010026 | -0.00033919 | 4.8739 | 67.2248 | ok | 1.9542 | ok | 458.8889 | 0.076481 | 0.92352 | 6000 | 0 | 3 | 1 | 0.93878 | 34.5 | 0.9 | 0.9 | 9.0235e-05 | 0.90835 | 35 | 0.010603 | 13.7812 | 0.4187 | 0.1461 | 0.040063 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.76923 | 0.88339 | 0.87129 | 0.8964 | 0.95263 |  |  | 11.1111 | 138.8889 | 97.7778 | 110.5556 | 100.5556 |  |  | 0.14789 | 0.61571 | 0.48692 | 0.79348 | 1.0208 | PARTIAL_AVAILABILITY
64182 | BWC Lake Lashaway, LLC Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 3.7 | 9 | 2.4324 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.97252 | 0.93659 | 0.085974 | 0.00084501 | -0.48126 | -39.174 | ok | 1.9505 | ok | 397.8889 | 0.066315 | 0.93369 | 6000 | 0 | 2 | 1 | 0.94521 | 138.5 | 3.7 | 3.7 | 0.003181 | 0.94699 | 34 | 0.30757 | 80.3114 | 2.44 | 0.85138 | 0.23347 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.93382 | 0.93454 | 0.93085 | 0.97254 | 0.93927 |  |  | 14.1111 | 92 | 94.2222 | 94.4444 | 103.1111 |  |  | 0.094667 | 0.40784 | 0.68407 | 0.74461 | 1.1869
64185 | ZPD-PT Solar Project 2017-023 LLC Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 1.9 | 3.5 | 1.8421 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.93051 | 0.89464 | 0.10825 | 0.0013092 | 5.9842 | 32.1905 | ok | -0.42602 | ok | 514.5714 | 0.085762 | 0.91424 | 6000 | 0 | 1 | 1 | 0.98958 | 20 | 1.9 | 1.9 | 0.0020567 | 0.90196 | 35 | 0.1096 | 47.5215 | 1.4438 | 0.50378 | 0.13815 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.87552 | 1.2177 | 0.8313 | 0.95441 | 0.93081 |  |  | 60.2857 | 86.2857 | 116.8571 | 89.7143 | 161.4286 |  |  | 0.27342 | 0.38251 | 0.61323 | 0.73016 | 2.0824
64187 | ZPD-PT Solar Project 2017-021 LLC Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 0.7 | 2.5 | 3.5714 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.98679 | 0.92371 | 0.13111 | 1.417e-05 | 3.2725 | 120.5093 | ok | -7.1321 | ok | 309.2 | 0.051533 | 0.94847 | 6000 | 0 | 0 | 1 | 0.95652 | 0 | 0.7 | 0.7 | 0.0009178 | 0.95044 | 36 | 0.21945 | 11.8501 | 0.64806 | 0.0078214 | 0.0019842 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 |  |  | 0.89362 | 1.5192 | 0.97255 | 0.94211 | 0.93361 |  |  | 16.8 | 31.6 | 99.2 | 71.6 | 90 |  |  | 0.083566 | 0.12426 | 0.30598 | 0.32433 | 0.31646
64197 | Fifth Standard Solar PV, LLC (Hybrid) | CA | CISO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 137 | 137 | 1 | <1.5h | 2023 | 58 | C | HYBRID_ARTEFACT | 0.93238 | 0.85451 | 1.1259 | 0.45088 | 0.19589 | 6.9229 | ok | 0.039883 | ok | 2488.9927 | 0.41483 | 0.58517 | 6000 | 0 | 2 | 1 | 0.87159 | 2203 | 137 | 137 | 1.5425 | 0.85795 | 28 | 0.57542 | 12185.7371 | 999.6192 | 354.8338 | 53.1366 | 0.13809 | 0.19981 | 0.059141 | 0.03647 | 0.012384 | 0.018576 | 0.0052449 | 0.003096 | RTE_2023: 0.86408; RTE_2024: 0.85092; RTE_2025: 0.8619; EFC_2023: 348.4526; EFC_2024: 956.6861; EFC_2025: 1183.854; UTI_2023: 1.8173; UTI_2024: 1.0745; UTI_2025: 1.5621 | ELEVATED_P_AUX
64198 | Horn Rapids Solar, Storage and Training | WA | BPAT | Tucci Energy Services | Energy Northwest |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming | 1 | 4 | 4 | 2.5-4.5h | 2020 |  |  | HYBRID_ARTEFACT | 1.0803 | 0.79371 | 0.17637 | -0.0097818 | 2.218 | 232.1889 | ok | -0.89009 | ok | 1131.75 | 0.18862 | 0.81137 | 6000 | 0 | 0 | 1 | 1.0677 | 0 | 1 | 1 | 0.0017637 | 1.1123 | 36 | 0.0024876 | 50.1719 | 4.573 | 1.924 | 0.011201 | 0.08949 | 0.14465 | 0.049641 | 0.0011993 | 0.0078125 | 0.013021 | 0.0043574 | 0.0001 |  | 0.63889 | 0.74384 | 0.79192 | 4.6402 | 0.78062 | 0.793 |  | 5.75 | 113.25 | 225.5 | 277.25 | 243.75 | 266.25 |  | 0.34363 | 0.58782 | 0.94142 | 1.057 | 0.90055 | 0.89012
64202 | Big Star Solar, LLC (Hybrid) | TX | ERCO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant | [10 empty] | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 0 |  | 0.83817 | 0 | [6 empty] | 1681.2957 | 92.9179 | 39.3864 | 46.7763 | 0.1346 | 0.13592 | 0.046901 | 0.20594 | 0.012047 | 0.012174 | 0.0041048 | 0.019216 | RTE_2025: 0.81784; EFC_2025: 0
64207 | Crane Battery Energy Storage System | IN | MISO | Duke Energy Indiana, LLC | Duke Energy Indiana, LLC |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 5 | 5 | 1 | <1.5h | 2020 | 159 | A | THERMAL_AUX | 0.91335 | 0.87986 | 0.10146 | -0.001674 | -1.3195 | 309.0985 | ok | -0.12888 | ok | 485.4 | 0.0809 | 0.9191 | 6000 | 0 | 3 | 1 | 0.9064 | 210.5 | 5 | 5 | 0.0050732 | 0.88804 | 23 | 0.21892 | 71.6441 | 3.1998 | 12.1076 | 2.1869 | 0.13542 | 0.11205 | 0.26216 | 0.22481 | 0.012126 | 0.009903 | 0.029806 | 0.021221 | RTE_2024: 0.90654; RTE_2025: 0.86559; EFC_2024: 271.6; EFC_2025: 213.8; UTI_2024: 0.74935; UTI_2025: 0.56074 | THERMAL_AUX
64210 | Bellefield Solar and Energy Storage Farm | CA | CISO | 50LW 8me LLC | 50LW 8me LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 500 | 2000 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 500 | 500
64213 | Auburn Solar Project | MA | ISNE | Agilitas Energy, Inc. | Agilitas Energy, Inc. |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 3.8 | 9.4 | 2.4737 | 1.5-2.5h | 2022 | 267 | C | HYBRID_ARTEFACT | 0.8986 | 0.86372 | 0.067113 | -0.00024975 | 4.4218 | 25.9025 | ok | -1.5443 | ok | 240.7447 | 0.040124 | 0.95988 | 6000 | 0 | 4 | 1 | 0.89116 | 103.5 | 3.7 | 3.7 | 0.0025503 | 0.8824 | 33 | 0.35278 | 73.0682 | 1.7125 | 0.66247 | 0.5462 | 0.17028 | 0.076884 | 0.024013 | 0.076884 | 0.015556 | 0.0066667 | 0.0020513 | 0.0066667 | RTE_2022: 0.88104; RTE_2023: 0.82018; RTE_2024: 0.89908; RTE_2025: 0.89535; EFC_2022: 25.2128; EFC_2023: 39.7872; EFC_2024: 93.8298; EFC_2025: 81.9149; UTI_2022: 0.16312; UTI_2023: 0.18476; UTI_2024: 0.80813; UTI_2025: 0.76609 | FULL_OUTAGE
64222 | Burt County Solar Hybrid | NE | SWPP | BCSB, LLC | BCSB, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Voltage or Reactive Power Support | 0.7 | 3 | 4.2857 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.91067 | 0.92105 | -0.013116 | 4.2834e-05 | -4.9068 | -158.6772 | ok | -0.78 | ok | 222.6667 | 0.037111 | 0.96289 | 6000 | 0 | 0 | 1 | 0.93333 | 0 | 0.7 | 0.7 | -9.1812e-05 | 0.91868 | 36 | 0.033827 | 5.7339 | 0.52263 | 0.21988 | 0.0012802 | 0.08949 | 0.14465 | 0.049641 | 0.0011993 | 0.0078125 | 0.013021 | 0.0043574 | 0.0001 |  |  | 0.85227 | 0.75758 | 0.9125 | 0.92941 | 0.912 |  |  | 25 | 58.3333 | 48.6667 | 52.6667 | 38 |  |  | 0.22719 | 0.22888 | 0.16017 | 0.18435 | 0.13698
64223 | Dodge County Solar Hybrid | NE | SWPP | BCSB, LLC | BCSB, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Voltage or Reactive Power Support | 0.7 | 3 | 4.2857 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.89278 | 0.92692 | -0.0636 | -9.8752e-06 | -0.3402 | -31.0113 | ok | 1.7521 | ok | 219 | 0.0365 | 0.9635 | 6000 | 0 | 2 | 1 | 0.89286 | 10.651 | 0.7 | 0.7 | -0.0004452 | 0.91435 | 35 | 0.27475 | 4.8738 | 0.44423 | 0.1869 | 0.0010881 | 0.08949 | 0.14465 | 0.049641 | 0.0011993 | 0.0078125 | 0.013021 | 0.0043574 | 0.0001 |  |  | 0.83871 | 0.7897 | 0.9058 | 0.90303 | 0.93798 |  |  | 26 | 61.3333 | 41.6667 | 49.6667 | 40.3333 |  |  | 0.23627 | 0.24066 | 0.16142 | 0.18317 | 0.12798
64231 | Hadley 3 Solar (North) | MA | ISNE | Hadley 3 Solar, LLC (North) | Hadley 3 Solar, LLC (North) |  |  | TRUE | pv_same_plant | LIB | CS |  | 1 | 4.4 | 4.4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.90893 | 0.85178 | 0.30493 | -0.0001081 |  |  | insufficient_history |  | insufficient_history | 84.3182 | 0.014053 | 0.98595 | 6000 | 0 | 0 | 1 | 0.86364 | 0 | 1 | 1 | 0.0030493 | 0.85287 | 12 | 0.21459 | 27.4174 | 2.9988 | 0.0164 | 0.0041605 | 0.12884 | 0.24108 | 0.0011985 | 0.0011993 | 0.011494 | 0.022989 | 0.0001 | 0.0001 | RTE_2025: 0.85287; EFC_2025: 84.3182; UTI_2025: 0.38526
64232 | Hadley 3 Solar (South) | MA | ISNE | Hadley 3 Solar, LLC (South) | Hadley 3 Solar, LLC (South) |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CT | Co-Located Renewable Firming, Excess Wind and Solar Generation | 1 | 1 | 1 | <1.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
64256 | AES Maui Kuihelani Solar Hybrid | HI | HECO | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Transmission and Distribution Deferral, Voltage or Reactive Power Support | 60 | 240 | 4 | 2.5-4.5h | 2024 | 84 | C | HYBRID_ARTEFACT | 1.0479 | 0.97448 | 0.94944 | -0.090763 |  |  | insufficient_history | 1.3288 | ok | 411.4083 | 0.068568 | 0.93143 | 6000 | 0 | 2 | 1 | 0.98189 | 1129 | 60 | 60 | 0.56966 | 0.97462 | 17 | 0.10593 | 3105.645 | 169.8413 | 100.4754 | 243.762 | 0.081309 | 0.081309 | 0.038345 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033255 | 0.031802 | RTE_2024: 0.97829; RTE_2025: 0.97315; EFC_2024: 118.3125; EFC_2025: 293.0958; UTI_2024: 0.98895; UTI_2025: 1.046 | PARTIAL_AVAILABILITY
64293 | Alvin | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2020 | 163 | B | PARTIAL_AVAILABILITY | 0.94288 | 0.92006 | 0.15703 | 0.0020927 | -2.9445 | -61.5833 | ok | 0.72631 | ok | 1273.0303 | 0.21217 | 0.78783 | 6000 | 0 | 2 | 1 | 0.93458 | 278 | 9.9 | 9.9 | 0.015546 | 0.92388 | 24 | 0.85789 | 150.4138 | 30.1613 | 19.0614 | 4.3726 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2020: 0.89349; RTE_2024: 0.93025; RTE_2025: 0.91552; EFC_2020: 45.7576; EFC_2024: 701.8182; EFC_2025: 525.4545; UTI_2020: 0.8515; UTI_2024: 1.6055; UTI_2025: 1.525 | PARTIAL_AVAILABILITY
64294 | Odessa | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2020 |  |  | UNATTRIBUTED | 0.95354 | 0.92073 | 0.2309 | -0.0032815 | -3.1998 | -90.7806 | ok | -0.045571 | ok | 1261.1111 | 0.21019 | 0.78981 | 6000 | 1 | 0 | 1 | 0.93527 | 0 | 9.9 | 9.9 | 0.022859 | 0.92422 | 24 | 0.88852 | 146.231 | 29.3226 | 18.5314 | 4.251 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2020: 0.9094; RTE_2024: 0.92925; RTE_2025: 0.91737; EFC_2020: 53.7374; EFC_2024: 700.5051; EFC_2025: 506.8687; UTI_2020: 1.0817; UTI_2024: 1.5268; UTI_2025: 1.5027
64295 | Angleton | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2020 | 112 | B | PARTIAL_AVAILABILITY | 0.93027 | 0.91542 | 0.1111 | 0.010911 | -1.3634 | 4.796 | ok | 0.20314 | ok | 1212.9293 | 0.20215 | 0.79785 | 6000 | 0 | 4 | 1 | 0.93151 | 504.5 | 9.9 | 9.9 | 0.010999 | 0.91718 | 24 | 0.085759 | 158.2775 | 31.7382 | 20.058 | 4.6012 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2020: 0.87536; RTE_2024: 0.92564; RTE_2025: 0.90711; EFC_2020: 30.5051; EFC_2024: 648.7879; EFC_2025: 533.6364; UTI_2020: 0.92446; UTI_2024: 1.4746; UTI_2025: 1.7527 | PARTIAL_AVAILABILITY
64296 | Brazoria | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2020 | 208 | B | PARTIAL_AVAILABILITY | 0.9418 | 0.92175 | 0.14137 | -0.0038033 | -1.1939 | -24.9447 | ok | 0.1418 | ok | 1226.1616 | 0.20436 | 0.79564 | 6000 | 0 | 2 | 1 | 0.93268 | 87 | 9.9 | 9.9 | 0.013996 | 0.9239 | 24 | 0.37711 | 144.5579 | 28.9871 | 18.3193 | 4.2024 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2020: 0.94671; RTE_2024: 0.92664; RTE_2025: 0.92064; EFC_2020: 53.8384; EFC_2024: 637.9798; EFC_2025: 534.3434; UTI_2020: 1.7649; UTI_2024: 1.4731; UTI_2025: 1.6746 | PARTIAL_AVAILABILITY
64297 | Heights | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2020 |  |  | HEALTHY | 0.93018 | 0.92037 | 0.074782 | 0.0015692 | -2.9192 | -46.0156 | ok | 0.18227 | ok | 1265.0505 | 0.21084 | 0.78916 | 6000 | 0 | 0 | 1 | 0.93141 | 0 | 9.9 | 9.9 | 0.0074034 | 0.92177 | 24 | 0.13463 | 162.795 | 32.644 | 20.6305 | 4.7325 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2020: 0.9898; RTE_2024: 0.92788; RTE_2025: 0.91441; EFC_2020: 39.1919; EFC_2024: 674.4444; EFC_2025: 551.4141; UTI_2020: 2.6443; UTI_2024: 2.8154; UTI_2025: 2.3306
64298 | Magnolia TX | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2020 |  |  | UNDER_DISPATCH | 0.91928 | 0.92299 | -0.019784 | -0.0050744 | -9.354 | -276.8144 | ok | 0.40833 | ok | 1109.4949 | 0.18492 | 0.81508 | 6000 | 0 | 0 | 1 | 0.93333 | 118 | 9.9 | 9.9 | -0.0019587 | 0.92437 | 24 | 0.030565 | 133.6826 | 26.8064 | 16.9412 | 3.8862 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2020: 0.81739; RTE_2024: 0.93069; RTE_2025: 0.91417; EFC_2020: 9.4949; EFC_2024: 683.6364; EFC_2025: 416.3636; UTI_2020: 0.59224; UTI_2024: 2.8551; UTI_2025: 1.9518
64312 | Bat Cave | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 100 | 110 | 1.1 | <1.5h | 2021 | 16 | A | THERMAL_AUX | 0.85162 | 0.75705 | 0.68933 | 0.12007 | 2.7566 | 34.3119 | ok | -0.28548 | ok | 1779.8273 | 0.29664 | 0.70336 | 6000 | 4 | 0 | 1 | 0.82106 | 18031.9146 | 100 | 100 | 0.68933 | 0.76758 | 51 | 0.72544 | 978.7775 | 196.2668 | 204.8169 | 28.4534 | 0.053242 | 0.18177 | 0.14235 | 0.087152 | 0.0045593 | 0.016717 | 0.013877 | 0.0075988 |  |  | 0.68051 | 0.78091 | 0.79347 | 0.76848 | 0.72311 |  |  | 49.1636 | 431.1182 | 538.8909 | 448.7 | 311.9545 |  |  | 0.28807 | 1.4195 | 1.1545 | 2.1034 | 1.4244 | THERMAL_AUX
64314 | Dickinson | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2021 | 209 | B | PARTIAL_AVAILABILITY | 0.9263 | 0.9228 | 0.024102 | -0.0013762 | -4.6362 | -174.3227 | ok | 0.1535 | ok | 2741.9024 | 0.45698 | 0.54302 | 6000 | 0 | 2 | 1 | 0.93558 | 85 | 9.9 | 9.9 | 0.0023861 | 0.92396 | 24 | 0.046683 | 141.7136 | 28.4168 | 17.9589 | 4.1197 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2024: 0.92945; RTE_2025: 0.91735; EFC_2024: 622.8283; EFC_2025: 510.101; UTI_2024: 2.9515; UTI_2025: 2.3334 | PARTIAL_AVAILABILITY
64315 | Loop 463 | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2021 | 226 | B | PARTIAL_AVAILABILITY | 0.94573 | 0.9189 | 0.19446 | -0.0004705 | -0.10245 | 5.0165 | ok | 0.37297 | ok | 2816.3721 | 0.4694 | 0.5306 | 6000 | 1 | 2 | 1 | 0.93166 | 66.5 | 9.9 | 9.9 | 0.019251 | 0.92143 | 24 | 0.724 | 153.2581 | 30.7317 | 19.4219 | 4.4553 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2024: 0.92623; RTE_2025: 0.91547; EFC_2024: 668.3838; EFC_2025: 532.7273; UTI_2024: 3.0325; UTI_2025: 2.4582 | PARTIAL_AVAILABILITY
64316 | Lopeno | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.96808 | 0.91199 | 0.29139 | -0.0014198 | -2.2123 | -85.3568 | ok | -1.4422 | ok | 1747.1717 | 0.2912 | 0.7088 | 6000 | 14 | 0 | 1 | 0.98034 | 507.26 | 9.9 | 9.9 | 0.028848 | 0.92831 | 36 | 0.8486 | 29.1092 | 7.9596 | 13.8476 | 29.4483 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2022: 0.77067; RTE_2023: 0.89178; RTE_2024: 0.98035; RTE_2025: 0.90087; EFC_2022: 91.3131; EFC_2023: 487.7778; EFC_2024: 665.0505; EFC_2025: 503.0303; UTI_2022: 0.28548; UTI_2023: 1.0583; UTI_2024: 3.21; UTI_2025: 2.3272
64317 | North Fork TX | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 100 | 110 | 1.1 | <1.5h | 2021 | 26 | A | THERMAL_AUX | 0.80552 | 0.74578 | 0.40881 | 0.26469 | 6.7575 | 62.7073 | ok | -1.6413 | ok | 1796.1273 | 0.29935 | 0.70065 | 6000 | 4 | 3 | 1 | 0.81567 | 11067.9758 | 100 | 100 | 0.40881 | 0.7633 | 50 | 0.24023 | 936.6147 | 187.8123 | 295.9811 | 27.2277 | 0.053242 | 0.18177 | 0.20017 | 0.087152 | 0.0045593 | 0.016717 | 0.020956 | 0.0075988 |  |  | 0.74894 | 0.77039 | 0.77961 | 0.77041 | 0.71436 |  |  | 35.2545 | 433.9182 | 542.6091 | 466.1091 | 318.2364 |  |  | 0.27177 | 1.3593 | 1.1103 | 2.1099 | 1.4147 | THERMAL_AUX
64318 | Pueblo BA | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 19.8 | 19.8 | 1 | <1.5h | 2022 | 223 | B | UNDER_DISPATCH | 0.92569 | 0.87259 | 0.30558 | 0.0014673 | -1.6454 | -25.9747 | ok | -0.1704 | ok | 1782.2727 | 0.29705 | 0.70295 | 6000 | 12 | 2 | 1 | 0.90249 | 1156.52 | 19.8 | 19.8 | 0.060505 | 0.88672 | 36 | 0.9645 | 52.5928 | 14.3809 | 25.019 | 53.2054 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2022: 0.68499; RTE_2023: 0.88478; RTE_2024: 0.89961; RTE_2025: 0.87088; EFC_2022: 112.0202; EFC_2023: 602.6768; EFC_2024: 637.6768; EFC_2025: 429.899; UTI_2022: 0.55299; UTI_2023: 1.4873; UTI_2024: 3.051; UTI_2025: 1.9426 | PARTIAL_AVAILABILITY
64319 | Ranchtown | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2021 | 144 | A | PARTIAL_AVAILABILITY | 0.93547 | 0.9086 | 0.19076 | 0.0027401 | -2.8921 | -88.6541 | ok | 0.11309 | ok | 2560.7828 | 0.4268 | 0.5732 | 6000 | 2 | 3 | 1 | 0.92725 | 290.5 | 9.9 | 9.9 | 0.018885 | 0.91072 | 24 | 0.64239 | 158.4448 | 31.7717 | 20.0792 | 4.606 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2024: 0.91417; RTE_2025: 0.90675; EFC_2024: 622.9293; EFC_2025: 536.2626; UTI_2024: 2.6888; UTI_2025: 2.3952 | PARTIAL_AVAILABILITY
64321 | Sweeny | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2021 |  |  | HEALTHY | 0.92051 | 0.92198 | -0.007498 | -0.0030667 | -4.1713 | -75.652 | ok | 0.12907 | ok | 2382.6768 | 0.39711 | 0.60289 | 6000 | 0 | 0 | 1 | 0.93511 | 0 | 9.9 | 9.9 | -0.0007423 | 0.9228 | 24 | 0.00087054 | 136.3596 | 27.3432 | 17.2804 | 3.964 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2024: 0.92451; RTE_2025: 0.92091; EFC_2024: 512.1212; EFC_2025: 462.2222; UTI_2024: 2.3989; UTI_2025: 2.0666
64322 | Zapata | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 19.8 | 19.8 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.93268 | 0.88901 | 0.27505 | 0.011392 | -1.8836 | -93.3452 | ok | -0.49825 | ok | 1868.1313 | 0.31136 | 0.68864 | 6000 | 14 | 0 | 1 | 0.90163 | 524.52 | 19.8 | 19.8 | 0.05446 | 0.8965 | 36 | 0.95111 | 57.2044 | 15.642 | 27.2128 | 57.8708 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2022: 0.76648; RTE_2023: 0.88872; RTE_2024: 0.90581; RTE_2025: 0.89497; EFC_2022: 151.5152; EFC_2023: 612.2727; EFC_2024: 604.697; EFC_2025: 499.6465; UTI_2022: 0.47369; UTI_2023: 1.4578; UTI_2024: 2.7341; UTI_2025: 2.3229
64374 | Norwich Solar and Energy Storage CSG | NY | NYIS | DG New York CS, LLC | DG New York CS, LLC |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_tight | LIB | CS | Co-Located Renewable Firming, System Peak Shaving | 5 | 15 | 3 | 2.5-4.5h | 2021 | 149 | C | FULL_OUTAGE | 0.83305 | 0.77867 | 0.0015708 | 0.0034413 |  |  | insufficient_history |  | insufficient_history | 189.9333 | 0.031656 | 0.96834 | 6000 | 0 | 20 | 1 | 0.91133 | 298.5 | 3 | 3 | 7.854e-05 | 0.88235 | 15 | 0.00035342 | 0 | 0 | 0 | 0 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.92479; RTE_2023: 0.83791; RTE_2024: 0.90767; EFC_2022: 132.8; EFC_2023: 22.4; EFC_2024: 34.7333; EFC_2025: 0; UTI_2022: 0.53269; UTI_2023: 0.045152; UTI_2024: 0.0026738; UTI_2025: 0 | FULL_OUTAGE
64375 | Decorah Battery | IA | MISO | Interstate Power and Light Co | Interstate Power and Light Co |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 2.5 | 2.9 | 1.16 | <1.5h | 2021 |  |  | UNDER_DISPATCH | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 0 | 1 | 0 | 2087.075 | 2.5 | 2.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.13542 | 0.11205 | 0.054422 | 0.22481 | 0.012126 | 0.009903 | 0.0048018 | 0.021221 | RTE_2024: 0; RTE_2025: 0; EFC_2024: 0; EFC_2025: 0; UTI_2024: 0; UTI_2025: 0
64395 | ZPD-PT Solar Project 2017-006 LLC Hybrid | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 2.5 | 5 | 2 | 1.5-2.5h | 2021 | 218 | C | HYBRID_ARTEFACT | 0.78096 | 0.79906 | -0.018853 | -0.0026291 | 9.8891 | 157.1732 | ok | 2.0225 | ok | 388.2 | 0.0647 | 0.9353 | 6000 | 0 | 3 | 1 | 0.89815 | 75.5 | 2.5 | 2.5 | -0.00047134 | 0.83402 | 35 | 0.0046787 | 37.542 | 1.1406 | 0.39798 | 0.10914 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  | 0.93548 | 0.89755 | 0.86751 | 0.82367 | 0.81486 |  |  | 23.2 | 80.6 | 95.6 | 68.2 | 120.6 |  |  | 0.20637 | 0.35731 | 0.5567 | 0.44 | 1.3364 | LOW_ETA_AND_LOW_UTI
64400 | BYU - Hawaii | HI | HECO | SkyHigh 2 Solar | SkyHigh 2 Solar |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 1.9 | 1.9 | 1 | <1.5h | 2021 | 435 | C | FULL_OUTAGE | 0.89749 | 0.85559 | 0.40272 | -0.0014524 |  |  | insufficient_history |  | insufficient_history | 1460.5263 | 0.24342 | 0.75658 | 6000 | 0 | 24 | 1 | 0.89761 | 435.693 | 1.9 | 1.9 | 0.0076518 | 0.85566 | 12 | 0.07519 | 107.0049 | 3.9013 | 0.052479 | 1.2443 | 0.15484 | 0.10609 | 0.0011985 | 0.10609 | 0.014019 | 0.0093458 | 0.0001 | 0.0093458 | RTE_2022: 0.89547; RTE_2025: 0.85566; EFC_2022: 811.5789; EFC_2023: 0; EFC_2024: 0; EFC_2025: 648.9474; UTI_2022: 0.98729; UTI_2023: 0; UTI_2024: 0; UTI_2025: 1.9103 | FULL_OUTAGE
64423 | TX7 Flat Top | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 16.5 | 1.6667 | 1.5-2.5h | 2020 | 56 | A | CELL_DEGRADATION | 0.85489 | 0.8564 | -0.0038786 | -0.009172 | -5.0812 | -160.7191 | ok | 2.0852 | ok | 1334.202 | 0.22237 | 0.77763 | 6000 | 2 | 7 | 1 | 0.86749 | 2231.2653 | 9.9 | 9.9 | -0.00038398 | 0.86014 | 17 | 0.00059035 | 133.6238 | 14.6152 | 7.5047 | 11.6535 | 0.10203 | 0.19366 | 0.08068 | 0.41615 | 0.0089686 | 0.017937 | 0.0073263 | 0.044843 | RTE_2024: 0.86339; RTE_2025: 0.85474; EFC_2024: 253.5758; EFC_2025: 150.8485; UTI_2024: 1.012; UTI_2025: 0.48823 | FULL_OUTAGE
64424 | TX8 Worsham | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 17.9 | 1.8081 | 1.5-2.5h | 2020 |  |  | UNDER_DISPATCH | 0.89225 | 0.64287 | 0.28775 | -0.0091523 |  |  | insufficient_history | 0.90709 | ok | 775.8659 | 0.12931 | 0.87069 | 6000 | 0 | 0 | 1 | 0.85231 | 6242.7227 | 9.9 | 9.9 | 0.028488 | 0.81616 | 19 | 0.97034 | 8.2281 | 0.89995 | 0.46211 | 0.71758 | 0.10203 | 0.19366 | 0.08068 | 0.41615 | 0.0089686 | 0.017937 | 0.0073263 | 0.044843 | RTE_2024: 0.83354; RTE_2025: 0.67637; EFC_2024: 148.8268; EFC_2025: 44.1341; UTI_2024: 0.50022; UTI_2025: 0.032266
64425 | TX2 Port Lavaca | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 9.9 | 11.9 | 1.202 | <1.5h | 2020 | 270 | B | CAPACITY_FADE |  | 0.31955 |  |  |  |  | insufficient_history | -21.0437 | ok | 65.5882 | 0.010931 | 0.98907 | 6000 | 0 | 3 | 1 | 0.41026 | 416.8883 | 9.9 | 9.9 |  |  |  |  | 1.8404 | 0.36905 | 0.23323 | 0.053502 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2024: 0.35422; RTE_2025: 0.29787; EFC_2024: 12.3529; EFC_2025: 5.8824; UTI_2024: 0.023419; UTI_2025: 0.015783 | FULL_OUTAGE
64426 | Wilmot Energy Center LLC | AZ | TEPC | Wilmot Energy Center LLC | Wilmot Energy Center LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, System Peak Shaving, Load Management, Excess Wind and Solar Generation | 30 | 60 | 2 | 1.5-2.5h | 2021 | 433 | C | HYBRID_ARTEFACT | 0.95268 | 0.84331 | 0.76463 | 0.062409 | 1.2347 | -0.24275 | ok | -1.4374 | ok | 1260.1833 | 0.21003 | 0.78997 | 6000 | 8 | 3 | 1 | 0.85508 | 1586 | 30 | 30 | 0.22939 | 0.85653 | 55 | 0.64186 | 2449.7408 | 156.2998 | 0.75792 | 14.243 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 |  |  | 0.78389 | 0.86255 | 0.83006 | 0.89293 | 0.87452 |  |  | 119.7 | 285.75 | 275.4 | 295.2167 | 284.1167 |  |  | 1.348 | 1.3104 | 1.2923 | 1.3249 | 1.1649 | PARTIAL_AVAILABILITY
64432 | Breckenridge Solar | MA | ISNE | Breckenridge Street Solar 1, LLC | Breckenridge Street Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 2.2 | 4.7 | 2.1364 | 1.5-2.5h | 2020 | 273 | C | HYBRID_ARTEFACT | 0.85091 | 0.73757 | 0.18357 | -0.00085094 | 12.1231 | 78.7071 | ok | 6.7202 | ok | 283.4043 | 0.047234 | 0.95277 | 6000 | 0 | 5 | 1 | 0.90769 | 23.2325 | 2.2 | 2.2 | 0.0040385 | 0.79401 | 32 | 0.61248 | 12.3556 | 0.37539 | 0.13098 | 0.035918 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.92241; RTE_2023: 0.74147; RTE_2024: 0.85512; RTE_2025: 0.82178; EFC_2022: 91.0638; EFC_2023: 87.8723; EFC_2024: 51.4894; EFC_2025: 52.9787; UTI_2022: 0.4037; UTI_2023: 0.44266; UTI_2024: 0.18135; UTI_2025: 0.41269 | LOW_ETA_AND_LOW_UTI
64436 | Wilmarth Solar | MA | ISNE | Wilmarth Lane Solar 1, LLC | Wilmarth Lane Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 2.3 | 4.6 | 2 | 1.5-2.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.90288 | 0.67152 | 0.24352 | -0.00018328 | -5.6644 | -20.223 | ok | 1.1665 | ok | 268.2609 | 0.04471 | 0.95529 | 6000 | 0 | 1 | 1 | 0.97826 | 20 | 2.3 | 2.3 | 0.0056009 | 0.82491 | 26 | 0.65858 | 7.6034 | 0.23101 | 0.080604 | 0.022103 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.72535; RTE_2023: 0.82793; RTE_2024: 0.73383; RTE_2025: 0.76804; EFC_2022: 67.1739; EFC_2023: 72.1739; EFC_2024: 64.1304; EFC_2025: 64.7826; UTI_2022: 0.29779; UTI_2023: 0.30235; UTI_2024: 0.28003; UTI_2025: 0.31396
64442 | Mt Pleasant Community Center | NY | NYIS | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS |  | 0.7 | 3 | 4.2857 | 2.5-4.5h | 2022 |  |  | HYBRID_ARTEFACT |  | 0.90218 |  |  |  |  | insufficient_history |  | insufficient_history | 41.3333 | 0.0068889 | 0.99311 | 6000 | 0 | 0 | 1.4 | 0.88235 | 0 | 0.5 | 0.7 |  |  |  |  | 17.0464 | 0.0036124 | 0.0045415 | 0.223 | 0.26632 | 0.0011993 | 0.0011985 | 0.20726 | 0.025806 | 0.0001 | 0.0001 | 0.019355 | RTE_2025: 0.85517; EFC_2025: 41.3333; UTI_2025: 0.12115
64446 | Arlington Microgrid | WA | BPAT | PUD No 1 of Snohomish County - (WA) | PUD No 1 of Snohomish County - (WA) |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Co-Located Renewable Firming, System Peak Shaving, Excess Wind and Solar Generation | 1 | 1.4 | 1.4 | <1.5h | 2021 | 365 | C | HYBRID_ARTEFACT | 0.73878 | 0.71272 | 0.028455 | 0.00065491 | -3.5772 | 81.8706 | ok | 11.9022 | ok | 232.8571 | 0.03881 | 0.96119 | 6000 | 0 | 0 | 1 | 0.89394 | 0 | 1 | 1 | 0.00028455 | 0.80882 | 29 | 0.012009 | 14.4045 | 0.52517 | 0.0070645 | 0.1675 | 0.15484 | 0.10609 | 0.0011985 | 0.10609 | 0.014019 | 0.0093458 | 0.0001 | 0.0093458 |  |  | 0.70833 | 0.2449 | 1 | 0.33333 | 0.8125 |  |  | 24.2857 | 8.5714 | 38.5714 | 12.8571 | 148.5714 |  |  | 0.089367 | 0.010633 | 0.063788 | 0.026264 | 0.31705 | LOW_ETA_AND_LOW_UTI
64450 | Grissom Solar, LLC | NC | PJM | SunStrong Management | SunStrong Management |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 10 | 10 | 1 | <1.5h | 2021 | 413 | C | HYBRID_ARTEFACT | 0.85338 | 0.83842 | 0.018346 | -0.0012412 | -4.1141 | 96.6121 | ok | 2.5831 | ok | 872.7 | 0.14545 | 0.85455 | 6000 | 0 | 0 | 1 | 6.6223 | 0 | 5 | 5 | 0.0018346 | 0.83644 | 33 | 0.036921 | 37.3795 | 1.6694 | 0.96006 | 1.141 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 |  |  |  |  | 0.88102 | 0.87118 | 0.69789 |  |  | 702.4 | 0 | 58.5 | 65.6 | 46.2 |  |  | 0.59667 | 0 | 0.038748 | 0.026365 | 0.027294 | LOW_ETA_AND_LOW_UTI
64453 | Volney II | NY | NYIS | DG New York CS, LLC | DG New York CS, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_tight | LIB | CS | Co-Located Renewable Firming, System Peak Shaving | 3 | 12 | 4 | 2.5-4.5h | 2021 | 320 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 0.33333 | 5.5556e-05 | 0.99994 | 6000 | 0 | 33 | 1 | 0.8 | 0 | 3 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.8; RTE_2023: 0; EFC_2022: 0.33333; EFC_2023: 0; EFC_2024: 0; EFC_2025: 0; UTI_2022: 0.013718; UTI_2023: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
64481 | Arlington Energy Center II | CA | CISO | Arlington Energy Center II | Arlington Energy Center II |  |  | TRUE | pv_same_plant | LIB | CT | Ramping / Spinning Reserve, Excess Wind and Solar Generation | 132 | 528 | 4 | 2.5-4.5h | 2022 | 414 | C | HYBRID_ARTEFACT | 0.84763 | 0.84657 | 0.036722 | 0.33015 | -1.8737 | -111.7583 | ok | -1.0293 | ok | 878.8864 | 0.14648 | 0.85352 | 6000 | 6 | 2 | 1 | 0.84534 | 2888 | 132 | 132 | 0.048473 | 0.84733 | 41 | 0.0014257 | 2609.8836 | 1046.6804 | 671.5618 | 349.0032 | 0.03025 | 0.20169 | 0.1029 | 0.20982 | 0.0025597 | 0.018771 | 0.00958 | 0.019625 | RTE_2022: 0.82262; RTE_2023: 0.83908; RTE_2024: 0.84546; RTE_2025: 0.86151; EFC_2022: 60.053; EFC_2023: 236.2689; EFC_2024: 292.3485; EFC_2025: 290.2159; UTI_2022: 0.5568; UTI_2023: 0.82784; UTI_2024: 1.1229; UTI_2025: 1.057 | LOW_ETA_AND_LOW_UTI
64489 | Resurgence Solar | CA | CISO | Resurgence Solar | Resurgence Solar |  |  | TRUE | pv_same_plant | OTH | CS | Excess Wind and Solar Generation | 75 | 300 | 4 | 2.5-4.5h | 2023 | 396 | C | HYBRID_ARTEFACT | 0.84459 | 0.85494 | -0.12772 | 0.33348 | 1.0405 | 70.2629 | ok | -0.63514 | ok | 575.1967 | 0.095866 | 0.90413 | 6000 | 5 | 0 | 1 | 0.82703 | 0 | 75 | 75 | -0.095791 | 0.85331 | 29 | 0.033827 | 1282.7732 | 514.4496 | 374.9703 | 171.5371 | 0.03025 | 0.20169 | 0.11525 | 0.20982 | 0.0025597 | 0.018771 | 0.010883 | 0.019625 | RTE_2023: 0.85856; RTE_2024: 0.85343; RTE_2025: 0.85111; EFC_2023: 100.3433; EFC_2024: 223.3267; EFC_2025: 251.5267; UTI_2023: 0.94369; UTI_2024: 0.92979; UTI_2025: 0.96195 | LOW_ETA_AND_LOW_UTI
64508 | Hall Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 2.5 | 5 | 2 | 1.5-2.5h | 2022 | 276 | C | HYBRID_ARTEFACT | 0.76372 | 0.60531 | 0.24274 | 0.0061637 | -10.9083 | -6.7309 | ok | -0.04974 | ok | 163 | 0.027167 | 0.97283 | 6000 | 0 | 1 | 1 | 0.84615 | 17.5 | 2 | 2 | 0.0060685 | 0.66185 | 31 | 0.3623 | 10.7033 | 0.0056193 | 0.0070645 | 0.0017922 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.75362; RTE_2023: 0.76; RTE_2024: 0.5906; RTE_2025: 0.54275; EFC_2022: 41.6; EFC_2023: 57; EFC_2024: 35.2; EFC_2025: 29.2; UTI_2022: 0.17955; UTI_2023: 0.27747; UTI_2024: 0.16167; UTI_2025: 0.14155 | LOW_ETA_AND_LOW_UTI
64509 | South River H4 Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 0.6 | 1.1 | 1.8333 | 1.5-2.5h | 2023 | 341 | C | HYBRID_ARTEFACT | 0.73349 | 0.76698 | -0.0033741 | -0.00068403 | 20.0483 | 155.4621 | ok | 1.3023 | ok | 107.2727 | 0.017879 | 0.98212 | 6000 | 0 | 1 | 1 | 0.7 | 2 | 0.5 | 0.5 | -2.0245e-05 | 0.7551 | 28 | 0.00012827 | 3.0581 | 0.0016055 | 0.0020184 | 0.00051206 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.7; RTE_2023: 0.63889; RTE_2024: 0.68421; RTE_2025: 0.73134; EFC_2022: 6.3636; EFC_2023: 20.9091; EFC_2024: 35.4545; EFC_2025: 44.5455; UTI_2022: 0.34984; UTI_2023: 0.065234; UTI_2024: 0.14845; UTI_2025: 0.15334 | LOW_ETA_AND_LOW_UTI
64510 | Arba Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Load Management, Excess Wind and Solar Generation | 5.1 | 10 | 1.9608 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.92772 | 0.73878 | 0.2598 | 0.003339 | -0.82563 | 0.39108 | ok | 15.0488 | ok | 156.5 | 0.026083 | 0.97392 | 6000 | 0 | 0 | 1 | 0.82313 | 0 | 0.5 | 0.5 | 0.01325 | 0.75973 | 36 | 0.69647 | 29.0519 | 0.015252 | 0.019175 | 0.0048646 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.74545; RTE_2023: 0.78402; RTE_2024: 0.73239; RTE_2025: 0.753; EFC_2022: 8.2; EFC_2023: 62.8; EFC_2024: 41.6; EFC_2025: 43.9; UTI_2022: 0.035393; UTI_2023: 0.28701; UTI_2024: 0.14845; UTI_2025: 0.16868
64511 | Rose Acre Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Load Management, Backup Power, Excess Wind and Solar Generation | 2.5 | 5 | 2 | 1.5-2.5h | 2023 | 349 | C | HYBRID_ARTEFACT | 0.85206 | 0.62036 | 0.49489 | 0.0014692 | -1.4444 | 15.4543 | ok | 3.4504 | ok | 157.6 | 0.026267 | 0.97373 | 6000 | 0 | 0 | 1 | 0.78689 | 0 | 2.5 | 2.5 | 0.012372 | 0.64233 | 34 | 0.53658 | 12.6147 | 0.0066227 | 0.008326 | 0.0021123 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2023: 0.69372; RTE_2024: 0.61625; RTE_2025: 0.59809; EFC_2023: 53; EFC_2024: 54.6; EFC_2025: 50; UTI_2023: 0.22313; UTI_2024: 0.22476; UTI_2025: 0.15017 | LOW_ETA_AND_LOW_UTI
64512 | Hamlet Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Load Management, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2023 | 343 | C | HYBRID_ARTEFACT | 0.786 | 0.69364 | 0.15193 | -0.00098879 | 8.5707 | 94.4743 | ok | -2.938 | ok | 119.0909 | 0.019848 | 0.98015 | 6000 | 0 | 0 | 1 | 0.7 | 0 | 0.5 | 0.5 | 0.00075965 | 0.70857 | 35 | 0.17553 | 2.2936 | 0.0012041 | 0.0015138 | 0.00038405 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.66667; RTE_2023: 0.70588; RTE_2024: 0.71642; RTE_2025: 0.68333; EFC_2022: 5.4545; EFC_2023: 32.7273; EFC_2024: 43.6364; EFC_2025: 37.2727; UTI_2022: 0.29987; UTI_2023: 0.1544; UTI_2024: 0.16553; UTI_2025: 0.12034 | LOW_ETA_AND_LOW_UTI
64513 | Wake RJ3 Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Load Management, Excess Wind and Solar Generation | 0.6 | 1.1 | 1.8333 | 1.5-2.5h | 2023 | 306 | C | HYBRID_ARTEFACT | 0.69068 | 0.66572 | 0.034174 | -0.00067964 | 15.4839 | 180.9181 | ok | 0.21143 | ok | 96.3636 | 0.016061 | 0.98394 | 6000 | 0 | 1 | 1 | 0.77778 | 3 | 0.5 | 0.5 | 0.00020504 | 0.69565 | 28 | 0.011615 | 3.0581 | 0.0016055 | 0.0020184 | 0.00051206 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.77778; RTE_2023: 0.66667; RTE_2024: 0.52941; RTE_2025: 0.7; EFC_2022: 6.3636; EFC_2023: 29.0909; EFC_2024: 16.3636; EFC_2025: 44.5455; UTI_2022: 0.34984; UTI_2023: 0.13388; UTI_2024: 0.042252; UTI_2025: 0.20241 | LOW_ETA_AND_LOW_UTI
64514 | Ludie Brown Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 2.5 | 2.5 | 1 | <1.5h | 2022 | 299 | C | HYBRID_ARTEFACT | 0.77384 | 0.62634 | 0.28226 | 0.0053342 | -3.3724 | 23.0906 | ok | 2.0154 | ok | 1656.8 | 0.27613 | 0.72387 | 6000 | 0 | 2 | 1 | 0.98435 | 4.5 | 2 | 2 | 0.0070566 | 0.65271 | 35 | 0.29563 | 13.3498 | 0.59623 | 0.34288 | 0.40749 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | RTE_2022: 0.98321; RTE_2023: 0.74084; RTE_2024: 0.6; RTE_2025: 0.58537; EFC_2022: 1381.6; EFC_2023: 113.2; EFC_2024: 85.2; EFC_2025: 76.8; UTI_2022: 1.6674; UTI_2023: 0.16467; UTI_2024: 0.20931; UTI_2025: 0.2135 | LOW_ETA_AND_LOW_UTI
64516 | Lowe Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 2.5 | 5 | 2 | 1.5-2.5h | 2022 | 355 | C | HYBRID_ARTEFACT | 0.80414 | 0.63645 | 0.30693 | 0.0058397 | -5.0093 | 21.5959 | ok | 2.2684 | ok | 180 | 0.03 | 0.97 | 6000 | 0 | 0 | 1 | 0.8125 | 0 | 2 | 2 | 0.0076733 | 0.65774 | 35 | 0.29248 | 12.2324 | 0.0064221 | 0.0080737 | 0.0020483 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.7911; RTE_2023: 0.73973; RTE_2024: 0.61782; RTE_2025: 0.58599; EFC_2022: 46.2; EFC_2023: 54; EFC_2024: 43; EFC_2025: 36.8; UTI_2022: 0.19941; UTI_2023: 0.24815; UTI_2024: 0.17743; UTI_2025: 0.14338 | LOW_ETA_AND_LOW_UTI
64520 | Spencer Meadow Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 2.5 | 5 | 2 | 1.5-2.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.87253 | 0.68485 | 0.27502 | 0.0033248 | -0.5373 | 15.1054 | ok | 4.408 | ok | 176 | 0.029333 | 0.97067 | 6000 | 0 | 0 | 1 | 0.84483 | 0 | 2 | 2 | 0.0068754 | 0.71492 | 34 | 0.53879 | 11.4679 | 0.0060207 | 0.0075691 | 0.0019202 | 0.1175 | 0.0011993 | 0.0011985 | 0.0011993 | 0.010417 | 0.0001 | 0.0001 | 0.0001 | RTE_2022: 0.73913; RTE_2023: 0.7801; RTE_2024: 0.65323; RTE_2025: 0.65942; EFC_2022: 47.6; EFC_2023: 59.6; EFC_2024: 32.4; EFC_2025: 36.4; UTI_2022: 0.20544; UTI_2023: 0.28478; UTI_2024: 0.14595; UTI_2025: 0.14759
64522 | Old Cedar Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | System Peak Shaving, Load Management | 1.3 | 2 | 1.5385 | 1.5-2.5h | 2021 | 289 | C | HYBRID_ARTEFACT | 0.83516 | 0.67027 | 0.25523 | 0.0024178 | -9.7326 | -48.9338 | ok | -3.0523 | ok | 252.5 | 0.042083 | 0.95792 | 6000 | 0 | 2 | 1 | 0.78788 | 7.5 | 1 | 1 | 0.003318 | 0.69709 | 35 | 0.59599 | 10.4863 | 0.28219 | 0.10403 | 0.17129 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 |  |  | 1 |  | 0.735 | 0.67262 | 0.64968 |  |  | 6 | 65.5 | 73.5 | 56.5 | 51 |  |  | 0.063987 | 0.28269 | 0.31998 | 0.25572 | 0.2003 | LOW_ETA_AND_LOW_UTI
64528 | Gambit Energy Storage - Angleton Storage | TX | ERCO | Gambit Energy Storage LLC | Gambit Energy Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 100 | 200 | 2 | 1.5-2.5h | 2021 | 50 | A | THERMAL_AUX | 0.7849 | 0.74463 | 0.34527 | -0.41698 | 3.454 | 41.0069 | ok | 0.25103 | ok | 962.635 | 0.16044 | 0.83956 | 6000 | 3 | 2 | 1 | 0.81013 | 5718.7137 | 100 | 100 | 0.34527 | 0.75432 | 54 | 0.15972 | 2488.1678 | 272.1455 | 348.4066 | 216.9958 | 0.10203 | 0.19366 | 0.17916 | 0.41615 | 0.0089686 | 0.017937 | 0.018266 | 0.044843 |  |  | 0.80476 | 0.76952 | 0.67607 | 0.7587 | 0.76365 |  |  | 148.405 | 211.825 | 152.025 | 215.58 | 234.8 |  |  | 5.0745 | 1.0517 | 0.80678 | 0.69537 | 0.86778 | THERMAL_AUX
64529 | Golden Triangle | MS | TVA | Origis Energy USA, Inc | Origis Energy USA, Inc |  |  | TRUE | pv_same_plant | LIB | CS |  | 50 | 200 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.88343 | 0.82221 | 0.60953 | -0.018195 |  |  | insufficient_history |  | insufficient_history | 167.255 | 0.027876 | 0.97212 | 6000 | 0 | 0 | 1 | 0.84006 | 0 | 50 | 50 | 0.30477 | 0.82945 | 11 | 0.38448 | 1434.1726 | 78.4319 | 47.3837 | 112.5682 | 0.081309 | 0.081309 | 0.039126 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033961 | 0.031802 | RTE_2025: 0.82945; EFC_2025: 167.255; UTI_2025: 0.55981
64534 | Darien Solar | WI | MISO | Wisconsin Electric Power Co | Wisconsin Electric Power Co |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
64545 | Ranchland Wind Storage | TX | ERCO | Ranchland Wind Storage, LLC | Ranchland Wind Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 73 | 108.6 | 1.4877 | <1.5h | 2023 | 96 | B | UNATTRIBUTED | 0.97981 | 0.79215 | 0.9469 | -0.028502 |  |  | insufficient_history |  | insufficient_history | 325.7366 | 0.054289 | 0.94571 | 6000 | 0 | 2 | 1 | 0.84763 | 1844.2783 | 71.5 | 71.5 | 0.69123 | 0.79949 | 16 | 0.70045 | 126.6086 | 34.6198 | 69.1057 | 128.0834 | 0.010638 | 0.052071 | 0.078139 | 0.46223 | 0.00089127 | 0.0044563 | 0.0070756 | 0.051693 | RTE_2024: 0.82292; RTE_2025: 0.7903; EFC_2024: 94.4383; EFC_2025: 231.2983; UTI_2024: 1.3939; UTI_2025: 0.87151 | PARTIAL_AVAILABILITY
64546 | Wynwood Energy Storage | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | FALSE |  | LIB | BL | Transmission and Distribution Deferral | 10 | 40 | 4 | 2.5-4.5h | 2019 | 127 | A | THERMAL_AUX | 0.83396 | 0.75132 | 0.44218 | 0.0097496 | 17.657 | 152.9185 | ok | 4.207 | ok | 508.5875 | 0.084765 | 0.91524 | 6000 | 0 | 0 | 1 | 0.78448 | 415.1626 | 10 | 10 | 0.044218 | 0.75466 | 24 | 0.55923 | 66.6665 | 23.6981 | 8.4745 | 0.027907 | 0.048771 | 0.27747 | 0.084478 | 0.0011993 | 0.0041667 | 0.027083 | 0.0077038 | 0.0001 | RTE_2024: 0.76767; RTE_2025: 0.73804; EFC_2024: 87.15; EFC_2025: 65.575; UTI_2024: 0.34742; UTI_2025: 0.22443 | THERMAL_AUX
64564 | Arlington Energy Center III | CA | CISO | Arlington Energy Center III | Arlington Energy Center III |  |  | TRUE | pv_same_plant | LIB | CT | Ramping / Spinning Reserve, Excess Wind and Solar Generation | 110 | 440 | 4 | 2.5-4.5h | 2022 | 405 | C | HYBRID_ARTEFACT | 0.83188 | 0.82531 | 0.11726 | 0.23776 | 0.40332 | -103.4428 | ok | -0.77025 | ok | 743.3909 | 0.1239 | 0.8761 | 6000 | 6 | 3 | 1 | 0.83841 | 3632.5 | 110 | 110 | 0.12898 | 0.82544 | 41 | 0.00724 | 1784.1031 | 715.5054 | 459.0762 | 238.5768 | 0.03025 | 0.20169 | 0.1029 | 0.20982 | 0.0025597 | 0.018771 | 0.00958 | 0.019625 | RTE_2022: 0.81732; RTE_2023: 0.80661; RTE_2024: 0.8142; RTE_2025: 0.85221; EFC_2022: 76.85; EFC_2023: 170.5955; EFC_2024: 239.4977; EFC_2025: 256.4477; UTI_2022: 0.5844; UTI_2023: 0.56849; UTI_2024: 1.0016; UTI_2025: 0.84719 | LOW_ETA_AND_LOW_UTI
64601 | County of San Diego COC Hybrid | CA | CISO | 53 SP Solar Trust | Solar Star California LXXVIII, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.4 | 1 | 2.5 | 2.5-4.5h | 2020 | 243 | C | HYBRID_ARTEFACT | 0.87494 | 0.75129 | -0.93265 | 0.0043714 |  |  | ok | -1.5567 | ok | 688.5 | 0.11475 | 0.88525 | 6000 | 0 | 4 | 1 | 0.95455 | 45 | 0.4 | 0.4 | -0.0037306 | 1.1152 | 32 | 0.050575 | 6.1806 | 0.90134 | 0.37932 | 0.37731 | 0.080762 | 0.20113 | 0.069817 | 0.25527 | 0.0070175 | 0.018713 | 0.0062643 | 0.024561 |  |  | 0.76961 | 1 | 11.75 | 0.80435 | 0.70388 |  |  | 157 | 56 | 141 | 111 | 145 |  |  | 0.69033 | 0.21578 | 0.40818 | 0.58406 | 0.54129 | FULL_OUTAGE
64611 | SEPV Sierra | CA | CISO | SEPV Sierra, LLC | SEPV Sierra, LLC |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Ramping / Spinning Reserve, Co-Located Renewable Firming, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 8.3 | 3.4 | 0.40964 | <1.5h | 2020 | 464 | C | HYBRID_ARTEFACT | 1.4631 | 0.93648 | 0.55451 | 0.11579 | -5.8137 | -283.4072 | ok | -0.43767 | ok | 8997.3529 | 1.4996 | 0 | 6000 | 0 | 2 | 1 | 0.8801 | 44.5 | 6 | 6 | 0.046024 | 1.3414 | 36 | 0.0026616 | 1861.6481 | 42.4207 | 0.42665 | 2.7059 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  |  | 1.0476 | 0.99541 | 14.9964 | 0.93883 | 0.93442 |  |  | 271.7647 | 893.8235 | 2456.7647 | 2279.7059 | 2891.4706 |  |  | 0.4042 | 1.1166 | 3.1537 | 2.5223 | 3.9245 | PARTIAL_AVAILABILITY
64612 | Kearny North Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Load Following, Ramping / Spinning Reserve | 10 | 40 | 4 | 2.5-4.5h | 2022 | 72 | A | UNDER_DISPATCH | 0.86576 | 0.80896 | 0.52993 | -0.010835 |  |  | insufficient_history | 0.43067 | ok | 527.6875 | 0.087948 | 0.91205 | 6000 | 0 | 8 | 1 | 0.80717 | 6459.3623 | 10 | 10 | 0.052993 | 0.8126 | 16 | 0.2767 | 0 | 0 | 0 | 0 | 0.03025 | 0.20169 | 0.12131 | 0.20982 | 0.0025597 | 0.018771 | 0.011537 | 0.019625 | RTE_2024: 0.81201; RTE_2025: 0.815; EFC_2024: 166.95; EFC_2025: 40.75; UTI_2024: 0.62054; UTI_2025: 0 | FULL_OUTAGE
64614 | Kearny South Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 10 | 40 | 4 | 2.5-4.5h | 2022 | 139 | A | THERMAL_AUX | 0.85693 | 0.81905 | 0.37152 | 0.017937 | 5.2175 | 74.6177 | ok | 0.12316 | ok | 667.1292 | 0.11119 | 0.88881 | 6000 | 0 | 0 | 1 | 0.86699 | 314.6782 | 10 | 10 | 0.037152 | 0.83114 | 24 | 0.76717 | 154.7106 | 62.0459 | 97.8687 | 20.6885 | 0.03025 | 0.20169 | 0.21943 | 0.20982 | 0.0025597 | 0.018771 | 0.023552 | 0.019625 | RTE_2024: 0.80485; RTE_2025: 0.84636; EFC_2024: 140.95; EFC_2025: 256.025; UTI_2024: 0.50719; UTI_2025: 0.8213 | THERMAL_AUX
64617 | Kearsarge William Way | MA | ISNE | Kearsarge William Way LLC | Kearsarge William Way LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, System Peak Shaving | 2.6 | 9.5 | 3.6538 | 2.5-4.5h | 2021 | 153 | C | HYBRID_ARTEFACT | 0.9249 | 0.88451 | 0.37195 | 0.0011768 | -1.3935 | -26.2825 | ok | 1.2414 | ok | 916.6316 | 0.15277 | 0.84723 | 6000 | 0 | 4 | 1 | 0.90909 | 319.5 | 2.6 | 2.6 | 0.0096706 | 0.89239 | 36 | 0.92799 | 133.7918 | 7.3168 | 0.088307 | 0.022403 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 | RTE_2022: 0.89741; RTE_2023: 0.89788; RTE_2024: 0.89159; RTE_2025: 0.88707; EFC_2022: 236.6316; EFC_2023: 236; EFC_2024: 238.9474; EFC_2025: 205.0526; UTI_2022: 0.93053; UTI_2023: 0.90309; UTI_2024: 1.0237; UTI_2025: 1.0368 | PARTIAL_AVAILABILITY
64618 | Kearsarge Haverhill | MA | ISNE | Kearsarge Haverhill LLC | Kearsarge Haverhill LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, System Peak Shaving | 2 | 9 | 4.5 | >4.5h | 2021 | 398 | C | HYBRID_ARTEFACT | 0.85219 | 0.82231 | 0.26746 | -0.0025717 | -3.1706 | -36.1693 | ok | -1.3178 | ok | 627 | 0.1045 | 0.8955 | 6000 | 0 | 0 | 1 | 0.86325 | 0 | 2 | 2 | 0.0053492 | 0.83658 | 30 | 0.84595 | 128.9962 | 7.76 | 0.073168 | 1.8 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 |  |  | 0.68773 | 0.79926 | 0.84665 | 0.82109 | 0.81581 |  |  | 62.8889 | 119.8889 | 189.5556 | 105.5556 | 149.1111 |  |  | 0.61739 | 0.85969 | 5.0369 | 1.4978 | 1.4511 | LOW_ETA_AND_LOW_UTI
64619 | Kearsarge Upper Union | MA | ISNE | Kearsarge Upper Union LLC | Kearsarge Upper Union LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.8 | 3.9 | 4.875 | >4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.92088 | 0.892 | 0.27375 | 0.0017097 | 1.3116 | -30.8791 | ok | -1.3645 | ok | 476.9231 | 0.079487 | 0.92051 | 6000 | 0 | 0 | 1 | 0.88462 | 0 | 0.8 | 0.8 | 0.00219 | 0.89725 | 33 | 0.1515 | 61.3844 | 3.6927 | 0.034818 | 0.85654 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2023: 0.86135; RTE_2024: 0.90749; RTE_2025: 0.91411; EFC_2023: 127.4359; EFC_2024: 158.4615; EFC_2025: 191.0256; UTI_2023: 4.7383; UTI_2024: 1.8162; UTI_2025: 1.6969
64620 | Kearsarge Montague BD(CSG) | MA | ISNE | Kearsarge Montague BD LLC | Kearsarge Montague BD LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, System Peak Shaving | 1.3 | 5.1 | 3.9231 | 2.5-4.5h | 2021 | 404 | C | HYBRID_ARTEFACT | 0.9263 | 0.82941 | 1.0122 | 0.00040781 | -1.7482 | -8.7984 | ok | 0.34206 | ok | 742.1569 | 0.12369 | 0.87631 | 6000 | 0 | 0 | 1 | 0.87879 | 0 | 1.3 | 1.3 | 0.013159 | 0.84123 | 36 | 0.83729 | 68.8072 | 3.7629 | 0.045415 | 0.011521 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 | RTE_2022: 0.79975; RTE_2023: 0.85972; RTE_2024: 0.83392; RTE_2025: 0.82541; EFC_2022: 126.0784; EFC_2023: 242.7451; EFC_2024: 186.0784; EFC_2025: 187.2549; UTI_2022: 0.49579; UTI_2023: 0.9019; UTI_2024: 0.92492; UTI_2025: 0.86854 | ELEVATED_P_AUX
64624 | Hudson - High Desert Hybrid | CA | CISO | HDSI, LLC | MN8 Energy LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 50 | 50 | 1 | <1.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.88818 | 0.87525 | 0.20312 | 0.082366 | 2.5336 | 65.5819 | ok | 0.066539 | ok | 4394.84 | 0.73247 | 0.26753 | 6000 | 8 | 0 | 1 | 0.89444 | 0 | 50 | 50 | 0.10156 | 0.87548 | 49 | 0.055427 | 11056.4943 | 251.9404 | 2.5339 | 16.0708 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 |  |  | 0.83543 | 0.87523 | 0.87636 | 0.87872 | 0.87302 |  |  | 19.9 | 1010.8 | 1130.94 | 985.2 | 1248 |  |  | 0.32587 | 1.1863 | 1.69 | 1.1664 | 1.4525
64627 | Blodgett Solar CSG | MA | ISNE | Blodgett Street Solar 1, LLC | Blodgett Street Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving | 5 | 4.9 | 0.98 | <1.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.90951 | 0.46017 | 0.10739 | 0.0015718 |  |  | insufficient_history | 2.2079 | ok | 310 | 0.051667 | 0.94833 | 6000 | 0 | 0 | 1 | 0.9863 | 0 | 2.2 | 2.2 | 0.0053695 | 0.82484 | 19 | 0.62293 | 4.7262 | 1.2923 | 0.0085783 | 0.90678 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 | RTE_2022: 0.98158; RTE_2023: 0.094851; RTE_2024: 0.75342; RTE_2025: 0.7837; EFC_2022: 195.7143; EFC_2023: 7.1429; EFC_2024: 56.1224; EFC_2025: 51.0204; UTI_2022: 0.2932; UTI_2023: 0.013035; UTI_2024: 0.12202; UTI_2025: 0.10352
64630 | Rabbitbrush Solar, LLC | CA | CISO | Leeward Asset Management, LLC | Leeward Asset Management, LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | Excess Wind and Solar Generation | 20 | 50 | 2.5 | 2.5-4.5h | 2022 | 230 | C | HYBRID_ARTEFACT | 0.8556 | 0.84891 | 0.085388 | 0.0098947 | 2.6376 | 48.5133 | ok | -0.14217 | ok | 980.92 | 0.16349 | 0.83651 | 6000 | 1 | 2 | 1 | 0.87129 | 59 | 20 | 20 | 0.017078 | 0.85049 | 39 | 0.020371 | 273.0684 | 109.5127 | 71.6952 | 36.5157 | 0.03025 | 0.20169 | 0.10477 | 0.20982 | 0.0025597 | 0.018771 | 0.0097751 | 0.019625 | RTE_2022: 0.89401; RTE_2023: 0.85777; RTE_2024: 0.85294; RTE_2025: 0.83652; EFC_2022: 45.38; EFC_2023: 291.9; EFC_2024: 309.6; EFC_2025: 334.04; UTI_2022: 0.77267; UTI_2023: 0.95286; UTI_2024: 1.2362; UTI_2025: 1.1395 | PARTIAL_AVAILABILITY
64633 | Rexford Solar Farm | CA | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 240 | 960 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.93155 | 0.88265 | 0.71869 | 0.90149 |  |  | insufficient_history |  | insufficient_history | 264.9677 | 0.044161 | 0.95584 | 6000 | 0 | 0 | 1 | 0.89317 | 0 | 240 | 240 | 1.7248 | 0.88711 | 11 | 0.38912 | 7911.0263 | 1442.1257 | 178.2942 | 1149.882 | 0.051638 | 0.16199 | 0.017077 | 0.35714 | 0.0044183 | 0.014728 | 0.0014483 | 0.036819 | RTE_2025: 0.88711; EFC_2025: 264.9677; UTI_2025: 0.98693
64636 | Big Rock Solar Farm | CA | CISO | Big Rock ESS Assets, LLC | Big Rock ESS Assets, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 200 | 200 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.70547 |  |  |  |  | insufficient_history |  | insufficient_history | 306.825 | 0.051138 | 0.94886 | 6000 | 4 | 0 | 1 | 0.83219 | 49156.2347 | 200 | 200 |  |  |  |  | 9928.7899 | 271.4925 | 4.2665 | 476.2453 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.80738; EFC_2025: 306.825; UTI_2025: 0.60987
64640 | Hot Springs Energy Storage & Microgrid | NC | CPLW | Duke Energy Progress - (NC) | Duke Energy Progress - (NC) |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, System Peak Shaving, Backup Power | 4.4 | 4.4 | 1 | <1.5h | 2022 | 374 | C | HYBRID_ARTEFACT | 0.8571 | 0.7097 | 0.1393 | -0.0044041 |  |  | ok | -1.8796 | ok | 285.9091 | 0.047652 | 0.95235 | 6000 | 0 | 5 | 1 | 0.89109 | 38.6255 | 4.4 | 4.4 | 0.0061293 | 0.78799 | 28 | 0.58516 | 25.4587 | 0.0074255 | 0.79454 | 0.44406 | 0.20148 | 0.0011993 | 0.092498 | 0.20148 | 0.01875 | 0.0001 | 0.0085112 | 0.01875 | RTE_2022: 0.71053; RTE_2023: 0.81467; RTE_2024: 0.81991; RTE_2025: 0.66585; EFC_2022: 49.0909; EFC_2023: 47.9545; EFC_2024: 127.2727; EFC_2025: 61.5909; UTI_2022: 0.12785; UTI_2023: 0.0081504; UTI_2024: 0.28513; UTI_2025: 0.15049 | LOW_ETA_AND_LOW_UTI
64656 | AES West Oahu Solar Hybrid | HI | HECO | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Transmission and Distribution Deferral, Voltage or Reactive Power Support | 12.5 | 50 | 4 | 2.5-4.5h | 2024 | 135 | C | HYBRID_ARTEFACT | 1.0887 | 0.98454 | 1.3414 | -0.063874 |  |  | insufficient_history | 0.59883 | ok | 454.08 | 0.07568 | 0.92432 | 6000 | 0 | 3 | 1 | 0.99513 | 330 | 12.5 | 12.5 | 0.16767 | 0.9846 | 18 | 0.092844 | 648.8788 | 35.4858 | 20.9204 | 50.9305 | 0.081309 | 0.081309 | 0.038218 | 0.31725 | 0.0070671 | 0.0070671 | 0.003314 | 0.031802 | RTE_2024: 0.99949; RTE_2025: 0.97694; EFC_2024: 156.72; EFC_2025: 297.36; UTI_2024: 1.127; UTI_2025: 1.0343 | PARTIAL_AVAILABILITY
64664 | Clark Road Solar 1, LLC | MA | ISNE | Clark Road Solar 1, LLC | Clark Road Solar 1, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming | 3.3 | 3 | 0.90909 | <1.5h | 2021 | 436 | C | HYBRID_ARTEFACT | 1.0072 | 0.87813 | 0.47465 | 0.0028748 | 5.0416 | 148.7778 | ok | 0.16155 | ok | 1561.6667 | 0.26028 | 0.73972 | 6000 | 0 | 2 | 1 | 0.90909 | 29.5 | 3 | 3 | 0.015664 | 0.88747 | 36 | 0.75724 | 25.5768 | 6.9937 | 0.046424 | 4.9073 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 | RTE_2022: 0.94753; RTE_2023: 0.90503; RTE_2024: 0.89975; RTE_2025: 0.85526; EFC_2022: 499.6667; EFC_2023: 378; EFC_2024: 359; EFC_2025: 325; UTI_2022: 0.74854; UTI_2023: 0.93702; UTI_2024: 0.66585; UTI_2025: 0.76317 | PARTIAL_AVAILABILITY
64672 | Blue Jay Solar I, LLC | TX | ERCO | Blue Jay Solar I, LLC | Blue Jay Solar I, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 51.6 | 84.5 | 1.6376 | 1.5-2.5h | 2023 | 384 | C | HYBRID_ARTEFACT | 0.75549 | 0.68284 | 0.31472 | -0.12707 | 7.4084 | 24.1872 | ok | 0.65149 | ok | 383.9882 | 0.063998 | 0.936 | 6000 | 2 | 0 | 1 | 0.79165 | 0 | 50 | 50 | 0.1624 | 0.71564 | 31 | 0.48529 | 315.7343 | 51.8006 | 75.6308 | 88.1137 | 0.031828 | 0.092476 | 0.10107 | 0.404 | 0.0026954 | 0.0080863 | 0.009391 | 0.043127 | RTE_2023: 0.62197; RTE_2024: 0.65192; RTE_2025: 0.77213; EFC_2023: 43.3609; EFC_2024: 107.6095; EFC_2025: 233.0178; UTI_2023: 0.36213; UTI_2024: 0.38883; UTI_2025: 0.81935 | LOW_ETA_AND_LOW_UTI
64686 | Orangeville Storage | NY | NYIS | Invenergy Services LLC | Invenergy Services LLC |  |  | TRUE | rte_gt_1,dc_coupled | LIB | OT | Frequency Regulation | 24.7 | 20 | 0.80972 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.86179 | 0.82644 | 0.51707 | 0.13368 | -0.99321 | -5.4219 | ok | -0.088928 | ok | 2508.85 | 0.41814 | 0.58186 | 6000 | 0 | 0 | 1 | 0.70109 | 0 | 20 | 20 | 0.12772 | 0.81003 | 36 | 0.017559 | 907.788 | 40.5435 | 23.3158 | 27.7092 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | RTE_2022: 0.80398; RTE_2023: 0.82239; RTE_2024: 0.77464; RTE_2025: 0.84389; EFC_2022: 363.8; EFC_2023: 792.5; EFC_2024: 771.15; EFC_2025: 581.4; UTI_2022: 1.9891; UTI_2023: 1.3964; UTI_2024: 1.9897; UTI_2025: 1.78
64695 | Angel Fire Energy Facility | NM | PNM | Angel Fire Energy Facility, LLC | Angel Fire Energy Facility, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Excess Wind and Solar Generation | 3.7 | 15 | 4.0541 | 2.5-4.5h | 2023 | 229 | C | HYBRID_ARTEFACT | 0.89142 | 0.76354 | 0.57621 | -0.0057815 | -3.2687 | -31.4653 | ok | -0.32651 | ok | 299.1333 | 0.049856 | 0.95014 | 6000 | 0 | 2 | 1 | 0.84462 | 63 | 3.7 | 3.7 | 0.02132 | 0.822 | 28 | 0.94268 | 1.3688 | 23.7864 | 3.1502 | 1.785 | 0.0011993 | 0.31703 | 0.038587 | 0.085813 | 0.0001 | 0.031776 | 0.0033474 | 0.0074766 | RTE_2023: 0.82963; RTE_2024: 0.81515; RTE_2025: 0.81832; EFC_2023: 67.2; EFC_2024: 120.5333; EFC_2025: 111.4; UTI_2023: 0.47678; UTI_2024: 0.50919; UTI_2025: 0.51967 | PARTIAL_AVAILABILITY
64696 | Dunstable Solar 1, LLC | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CS | System Peak Shaving | 4.5 | 20.2 | 4.4889 | 2.5-4.5h | 2021 | 219 | C | HYBRID_ARTEFACT | 1.006 | 0.95613 | 0.10078 | -0.023674 | 0.89603 | 185.9976 | ok | -0.30537 | ok | 496.1386 | 0.08269 | 0.91731 | 6000 | 0 | 2 | 1 | 0.97614 | 135 | 4.5 | 4.5 | 0.0045351 | 0.97918 | 36 | 0.030673 | 172.018 | 9.4073 | 0.11354 | 0.028804 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 |  |  | 0.97497 | 0.91994 | 1.0132 | 0.94495 | 0.97579 |  |  | 104.1089 | 59.1584 | 117.4257 | 97.7228 | 117.7228 |  |  | 0.69165 | 0.23263 | 0.35761 | 0.40828 | 0.55134 | PARTIAL_AVAILABILITY
64701 | LeConte Energy Storage | CA | CISO | LeConte Energy Storage, LLC | LeConte Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve | 125 | 250 | 2 | 1.5-2.5h | 2022 | 431 | B | PARTIAL_AVAILABILITY | 0.86386 | 0.82203 | 0.46452 | 0.15574 | -2.4742 | 29.5818 | ok | 0.018091 | ok | 1136.22 | 0.18937 | 0.81063 | 6000 | 12 | 2 | 1 | 0.81651 | 240.849 | 125 | 125 | 0.58065 | 0.82117 | 40 | 0.033129 | 3029.4518 | 911.2095 | 190.0459 | 0.92735 | 0.066091 | 0.31344 | 0.058655 | 0.0011993 | 0.005698 | 0.031339 | 0.0051991 | 0.0001 | RTE_2022: 0.83442; RTE_2023: 0.86749; RTE_2024: 0.79628; RTE_2025: 0.80032; EFC_2022: 146.36; EFC_2023: 316.764; EFC_2024: 325.92; EFC_2025: 347.176; UTI_2022: 3.3421; UTI_2023: 1.0994; UTI_2024: 1.1922; UTI_2025: 1.069 | PARTIAL_AVAILABILITY
64712 | Sanborn BESS 1 | CA | CISO | Terra-Gen Operating Co-BESS | Terra-Gen Operating Co-BESS |  |  | FALSE |  | LIB | CS |  | 100 | 200 | 2 | 1.5-2.5h | 2021 | 55 | A | UNATTRIBUTED | 0.93574 | 0.82106 | 1.2689 | 0.040973 | 1.0726 | 11.9496 | ok | -0.18556 | ok | 1583.645 | 0.26394 | 0.73606 | 6000 | 1 | 4 | 1 | 0.81884 | 2243.8001 | 100 | 100 | 1.2689 | 0.82321 | 50 | 0.41431 | 3578.7463 | 391.4285 | 222.82 | 93.6319 | 0.095923 | 0.18264 | 0.083538 | 0.14038 | 0.0084034 | 0.016807 | 0.00761 | 0.012605 |  |  | 0.7976 | 0.80326 | 0.8476 | 0.82667 | 0.81265 |  |  | 65.04 | 320.785 | 450.215 | 396.23 | 351.375 |  |  | 7.4082 | 2.4297 | 1.6751 | 1.5438 | 1.2674 | ELEVATED_P_AUX
64713 | Sanborn BESS 2 | CA | CISO | Terra-Gen Operating Co-BESS | Terra-Gen Operating Co-BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation | 100 | 400 | 4 | 2.5-4.5h | 2021 | 33 | A | UNATTRIBUTED | 0.9207 | 0.85239 | 1.2883 | 0.11948 | -0.62767 | -5.7973 | ok | 0.26937 | ok | 1397.955 | 0.23299 | 0.76701 | 6000 | 1 | 0 | 1 | 0.97093 | 8546.1795 | 100 | 100 | 1.2883 | 0.85497 | 50 | 0.38783 | 5654.9715 | 824.6899 | 318.0168 | 345.2233 | 0.080762 | 0.20113 | 0.064357 | 0.25527 | 0.0070175 | 0.018713 | 0.00574 | 0.024561 |  |  | 0.85455 | 0.85334 | 0.86483 | 0.85379 | 0.84624 |  |  | 61.31 | 318.1025 | 379.2425 | 324.9775 | 314.3225 |  |  | 1.8904 | 1.2818 | 1.2938 | 1.204 | 1.1256 | ELEVATED_P_AUX
64719 | Glenmere Lake | NY | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 2 | 7.5 | 3.75 | 2.5-4.5h | 2021 | 352 | C | HYBRID_ARTEFACT | 0.91193 | 0.93009 | 0.0012943 | -0.00024176 | -6.7815 | -134.1362 | ok | 1.1096 | ok | 167.4667 | 0.027911 | 0.97209 | 6000 | 0 | 2 | 1 | 0.92308 | 38 | 2 | 2 | 2.5886e-05 | 0.93814 | 34 | 0.00028168 | 21.4067 | 1.1707 | 0.014129 | 0.0035844 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 |  |  | 0.7619 | 0.49227 | 1.0309 | 0.89831 | 0.91899 |  |  | 4.2667 | 29.7333 | 35.6 | 49.4667 | 48.4 |  |  | 0.038081 | 0.11927 | 0.1335 | 0.19619 | 0.20467 | FULL_OUTAGE
64726 | West Haydenville PJ Community Solar | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | rte_gt_1,pv_same_plant,dc_tight | LIB | CT | System Peak Shaving | 3.6 | 8 | 2.2222 | 1.5-2.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.96924 | 0.84646 | 0.15938 | -0.0035089 | 1.4478 | -67.4908 | ok | 1.6618 | ok | 255.125 | 0.042521 | 0.95748 | 6000 | 0 | 0 | 1 | 0.88889 | 0 | 3 | 3 | 0.0057377 | 0.90743 | 32 | 0.26938 | 76.4932 | 1.7928 | 0.69501 | 0.5718 | 0.17028 | 0.076884 | 0.024063 | 0.076884 | 0.015556 | 0.0066667 | 0.0020557 | 0.0066667 | RTE_2023: 0.86364; RTE_2024: 0.8762; RTE_2025: 0.96684; EFC_2023: 80.75; EFC_2024: 79.625; EFC_2025: 94.75; UTI_2023: 0.525; UTI_2024: 0.4467; UTI_2025: 0.74397
64727 | Brookwood Drive Community Solar | MA | ISNE | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | OT | System Peak Shaving | 3 | 8 | 2.6667 | 2.5-4.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.89038 | 0.8888 | 0.01632 | 0.00038757 | -5.6493 | 5.2983 | ok | 2.0169 | ok | 355.125 | 0.059187 | 0.94081 | 6000 | 0 | 2 | 1 | 0.60971 | 294.981 | 3 | 3 | 0.00048959 | 0.86459 | 34 | 0.12464 | 63.8531 | 3.492 | 0.02195 | 0.8353 | 0.21337 | 0.21337 | 0.0011985 | 0.16473 | 0.02 | 0.02 | 0.0001 | 0.015 | RTE_2022: 0.61018; RTE_2023: 0.95095; RTE_2024: 0.90132; RTE_2025: 0.78102; EFC_2022: 122.875; EFC_2023: 87.25; EFC_2024: 51.375; EFC_2025: 93.625; UTI_2022: 1.0304; UTI_2023: 0.35567; UTI_2024: 0.22558; UTI_2025: 0.33528
64731 | Maple(CSG) | MA | ISNE | Maple Street Solar 1, LLC | Maple Street Solar 1, LLC |  |  | TRUE | pv_same_plant | OTH | CS |  | 2.3 | 4.8 | 2.087 | 1.5-2.5h | 2021 | 272 | C | HYBRID_ARTEFACT | 0.44174 | 0.63784 | -0.059366 | -0.0007318 |  |  | ok |  | insufficient_history | 42.9167 | 0.0071528 | 0.99285 | 6000 | 0 | 7 | 1 | 0.64865 | 24.5 | 2.2 | 2.2 | -0.0013654 | 0.48456 | 20 | 0.48139 | 0.47522 | 0.014438 | 0.0050378 | 0.0013815 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.66667; RTE_2023: 0.47689; RTE_2024: 0.28571; RTE_2025: 0.46154; EFC_2022: 0.41667; EFC_2023: 40.8333; EFC_2024: 0.41667; EFC_2025: 1.25; UTI_2022: 0.022906; UTI_2023: 0.23733; UTI_2024: 0; UTI_2025: 0.0043366 | FULL_OUTAGE
64743 | Tierra Buena Energy Storage | CA | CISO | VESI 10 LLC | VESI 10 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 5 | 5 | 1 | <1.5h | 2022 | 92 | A | THERMAL_AUX | 0.93867 | 0.83346 | 1.4052 | 0.012824 | 1.8418 | 41.2586 | ok | -0.0023139 | ok | 3386.8 | 0.56447 | 0.43553 | 6000 | 0 | 2 | 1 | 0.85303 | 1490.0099 | 5 | 5 | 0.070261 | 0.84019 | 36 | 0.52681 | 319.4814 | 26.2077 | 27.4792 | 1.3931 | 0.13809 | 0.19981 | 0.15629 | 0.03647 | 0.012384 | 0.018576 | 0.015493 | 0.003096 | RTE_2022: 0.8642; RTE_2023: 0.85042; RTE_2024: 0.85719; RTE_2025: 0.81107; EFC_2022: 448; EFC_2023: 921; EFC_2024: 1100.8; EFC_2025: 917; UTI_2022: 0.83845; UTI_2023: 1.5398; UTI_2024: 1.3812; UTI_2025: 1.1057 | THERMAL_AUX
64752 | John Hopkins Middle School Microgrid | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Backup Power, Excess Wind and Solar Generation | 2.5 | 18 | 7.2 | >4.5h | 2023 | 236 | C | HYBRID_ARTEFACT | 0.81709 | 0.79224 | 0.048521 | -0.007231 | 3.2873 | 45.6838 | ok | 4.993 | ok | 72.9444 | 0.012157 | 0.98784 | 6000 | 0 | 2 | 1 | 0.88591 | 50 | 2.5 | 2.5 | 0.001213 | 0.86024 | 22 | 0.16472 | 31.5818 | 1.8999 | 0.017914 | 0.44069 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2024: 0.8754; RTE_2025: 0.82877; EFC_2024: 46.0556; EFC_2025: 26.8889; UTI_2024: 0.38973; UTI_2025: 0.25164 | LOW_ETA_AND_LOW_UTI
64759 | Old Middleboro Road Solar | MA | ISNE | Old Middleboro Road Solar, LLC | Agilitas Energy, Inc. |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 4.5 | 13.4 | 2.9778 | 2.5-4.5h | 2023 | 247 | C | HYBRID_ARTEFACT | 0.89665 | 0.90606 | -0.044511 | -0.0016413 | -0.51481 | 100.3791 | ok | 0.34119 | ok | 257.3881 | 0.042898 | 0.9571 | 6000 | 0 | 5 | 1 | 0.90514 | 219 | 4.5 | 4.5 | -0.002003 | 0.90454 | 23 | 0.023257 | 209.1739 | 11.4393 | 0.071907 | 2.7363 | 0.21337 | 0.21337 | 0.0011985 | 0.16473 | 0.02 | 0.02 | 0.0001 | 0.015 | RTE_2024: 0.90877; RTE_2025: 0.90005; EFC_2024: 133.0597; EFC_2025: 124.3284; UTI_2024: 0.58188; UTI_2025: 0.61717 | PARTIAL_AVAILABILITY
64760 | Ocean State BTM | RI | ISNE | Ocean State BTM, LLC | Agilitas Energy, Inc. |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 3 | 10 | 3.3333 | 2.5-4.5h | 2022 | 54 | A | UNDER_DISPATCH | 0.92292 | 0.74123 | 1.0131 | 0.0080311 | -14.114 | -77.0562 | ok | -0.13446 | ok | 1441.8 | 0.2403 | 0.7597 | 6000 | 0 | 0 | 0.033333 | 0.9076 | 3999.0489 | 3 | 0.1 | 0.030392 | 0.74864 | 36 | 0.42787 | 128.4401 | 7.0241 | 0.044153 | 1.6802 | 0.21337 | 0.21337 | 0.0011985 | 0.16473 | 0.02 | 0.02 | 0.0001 | 0.015 | RTE_2022: 0.90754; RTE_2023: 0.73621; RTE_2024: 0.76081; RTE_2025: 0.74661; EFC_2022: 1125.8; EFC_2023: 97.4; EFC_2024: 119.6; EFC_2025: 99; UTI_2022: 7.1737; UTI_2023: 0.32616; UTI_2024: 0.5687; UTI_2025: 0.43703 | ELEVATED_P_AUX
64761 | Patchogue ESS | NY | NYIS | AE-ESS Cassel, LLC | Agilitas Energy, Inc. |  |  | FALSE |  | LIB | CS |  | 2 | 11.9 | 5.95 | >4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.90286 |  |  |  |  | insufficient_history |  | insufficient_history | 33.1092 | 0.0055182 | 0.99448 | 6000 | 0 | 0 | 1 | 0.89669 | 559.7873 | 2 | 2 |  |  |  |  | 37.8092 | 2.2745 | 0.021446 | 0.52758 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2025: 0.9016; EFC_2025: 33.1092; UTI_2025: 0.27852
64763 | Rumford ESS | ME | ISNE | Rumford ESS, LLC | Agilitas Energy, Inc. |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, System Peak Shaving | 4.9 | 10 | 2.0408 | 1.5-2.5h | 2021 | 259 | A | THERMAL_AUX | 0.59848 | 0.66294 | -0.11262 | 0.0018647 | 0.095003 | 161.0853 | ok | -11.4397 | ok | 128.1333 | 0.021356 | 0.97864 | 6000 | 0 | 0 | 1 | 0.6381 | 32.7134 | 4.9 | 4.9 | -0.0055185 | 0.64476 | 22 | 0.096819 | 39.4429 | 1.1984 | 0.87545 | 0.11466 | 0.14392 | 0.082709 | 0.047723 | 0.025567 | 0.01295 | 0.0071942 | 0.0041805 | 0.0021583 | RTE_2024: 0.67097; RTE_2025: 0.6084; EFC_2024: 20.8; EFC_2025: 53.6; UTI_2024: 0.19043; UTI_2025: 0.59822 | THERMAL_AUX
64764 | Madison BTM | ME | ISNE | Madison BTM, LLC | Agilitas Energy, Inc. |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Load Following | 1.5 | 3.1 | 2.0667 | 1.5-2.5h | 2020 | 286 | A | CELL_DEGRADATION | 0.6542 | 0.70224 | -0.053822 | -0.00048034 | -16.3247 | 13.4586 | ok | -11.2998 | ok | 303.871 | 0.050645 | 0.94935 | 6000 | 1 | 0 | 1 | 0.58442 | 212.831 | 1.5 | 1.5 | -0.00080733 | 0.63443 | 22 | 0.11632 | 33.7403 | 1.0251 | 0.36684 | 0.098084 | 0.14392 | 0.082709 | 0.023972 | 0.025567 | 0.01295 | 0.0071942 | 0.0020478 | 0.0021583 | RTE_2024: 0.74627; RTE_2025: 0.60136; EFC_2024: 32.2581; EFC_2025: 142.5806; UTI_2024: 0.52954; UTI_2025: 2.0931 | LOW_ETA_AND_LOW_UTI
64765 | Madison ESS | ME | ISNE | Madison ESS, LLC | Agilitas Energy, Inc. |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, System Peak Shaving | 4.9 | 10 | 2.0408 | 1.5-2.5h | 2019 | 194 | A | CAPACITY_FADE | 0.58379 | 0.66099 | -0.087204 | 0.014592 |  |  | ok | -4.2455 | ok | 178.3583 | 0.029726 | 0.97027 | 6000 | 1 | 1 | 1 | 0.6129 | 375.3213 | 4.9 | 4.9 | -0.004273 | 0.60698 | 22 | 0.017564 | 52.8537 | 0.82585 | 0.023464 | 1.317 | 0.16959 | 0.051712 | 0.0011985 | 0.23317 | 0.015487 | 0.0044248 | 0.0001 | 0.022124 | RTE_2024: 0.7695; RTE_2025: 0.5575; EFC_2024: 21.7; EFC_2025: 57.2; UTI_2024: 0.25872; UTI_2025: 0.65994 | LOW_ETA_AND_LOW_UTI
64766 | Redwood Coast Airport Microgrid | CA | CISO | Redwood Coast Energy Authority | Redwood Coast Energy Authority |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Co-Located Renewable Firming, Backup Power | 2.2 | 8.8 | 4 | 2.5-4.5h | 2021 | 227 | C | HYBRID_ARTEFACT | 0.87677 | 0.5 | 1.5711 | 0.044031 |  |  | ok | 2.6541 | ok | 677.9545 | 0.11299 | 0.88701 | 6000 | 0 | 2 | 1.2 | 0.4364 | 66 | 1.5 | 1.8 | 0.034564 | 0.78012 | 19 | 0.16853 | 22.9196 | 3.3425 | 1.4066 | 1.3992 | 0.080762 | 0.20113 | 0.069817 | 0.25527 | 0.0070175 | 0.018713 | 0.0062643 | 0.024561 |  |  | 0.77778 | 0.88369 | 0.87223 | 0.42173 | 0.13657 |  |  | 7.1591 | 255.5682 | 241.25 | 108.0682 | 65.9091 |  |  | 0.27843 | 0.98476 | 0.8092 | 0.43351 | 0.22024 | ELEVATED_P_AUX
64811 | Upton County BESS | TX | ERCO | VESI Upton County BESS, LLC | VESI Upton County BESS, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 24.8 | 25 | 1.0081 | <1.5h | 2023 | 123 | A | UNATTRIBUTED | 0.83197 | 0.73303 | 0.23673 | -0.0091081 |  |  | insufficient_history | -2.7416 | ok | 403.62 | 0.06727 | 0.93273 | 6000 | 1 | 0 | 1 | 0.85502 | 841.7356 | 24.8 | 24.8 | 0.058708 | 0.77778 | 23 | 0.63505 | 36.9915 | 10.115 | 19.2004 | 37.4224 | 0.010638 | 0.052071 | 0.074598 | 0.46223 | 0.00089127 | 0.0044563 | 0.0067286 | 0.051693 | RTE_2024: 0.67504; RTE_2025: 0.82634; EFC_2024: 96.72; EFC_2025: 250.48; UTI_2024: 0.39052; UTI_2025: 1.164 | LOW_ETA_AND_LOW_UTI
64844 | Three Rivers Solar LLC | MA | ISNE | ASD Three Rivers Road MA Solar LLC | ASD Three Rivers Road MA Solar LLC |  |  | TRUE | pv_same_plant,dc_coupled | PBB | CS | Arbitrage, Excess Wind and Solar Generation | 1.4 | 2.8 | 2 | 1.5-2.5h | 2024 | 361 | C | HYBRID_ARTEFACT |  | 0.84727 |  |  |  |  | insufficient_history |  | insufficient_history | 201.0714 | 0.033512 | 0.96649 | 6000 | 0 | 4 | 1 | 0.9639 | 0 | 1.3 | 1.3 |  |  |  |  | 28.3747 | 0.76356 | 0.29886 | 0.46349 | 0.18267 | 0.094486 | 0.029956 | 0.17213 | 0.016809 | 0.0082711 | 0.0025751 | 0.015742 | RTE_2024: 0.23077; RTE_2025: 0.95076; EFC_2024: 1.0714; EFC_2025: 200; UTI_2024: 0.24917; UTI_2025: 0.74828 | FULL_OUTAGE
64851 | Daggett 2 | CA | CISO | Daggett Solar Power 2 LLC | Daggett Solar Power 2 LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 131 | 4.6 | 0.035115 | <1.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.96015 | 0.90806 | 0.80581 | 0.60187 |  |  | insufficient_history | 0.0050199 | ok | 59919.1304 | 9.9865 | 0 | 6000 | 5 | 0 | 1 | 0.90423 | 0 | 2.3 | 2.3 | 1.0556 | 0.9063 | 23 | 0.03192 | 10616.9609 | 870.9295 | 317.8335 | 46.2958 | 0.13809 | 0.19981 | 0.060699 | 0.03647 | 0.012384 | 0.018576 | 0.0053922 | 0.003096 | RTE_2024: 0.94115; RTE_2025: 0.874; EFC_2024: 29927.3913; EFC_2025: 29991.7391; UTI_2024: 36.8771; UTI_2025: 39.7994
64852 | Daggett 3 | CA | CISO | Daggett Solar Power 3 LLC | Daggett Solar Power 3 LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 149 | 4.6 | 0.030872 | <1.5h | 2023 | 10 | C | HYBRID_ARTEFACT | 0.91085 | 0.92395 | -0.13862 | -0.46058 | -3.6916 | 94.1363 | ok | -0.0099375 | ok | 77804.3478 | 12.9674 | 0 | 6000 | 5 | 5 | 1 | 0.92645 | 26894 | 2.3 | 2.3 | -0.20654 | 0.92155 | 28 | 0.022768 | 10982.7966 | 900.9397 | 318.0682 | 47.8911 | 0.13809 | 0.19981 | 0.058839 | 0.03647 | 0.012384 | 0.018576 | 0.0052164 | 0.003096 | RTE_2023: 0.94849; RTE_2024: 0.93998; RTE_2025: 0.89187; EFC_2023: 9450.4348; EFC_2024: 37938.4783; EFC_2025: 30415.4348; UTI_2023: 37.7179; UTI_2024: 45.9286; UTI_2025: 42.6912 | PARTIAL_AVAILABILITY
64864 | Chaparral Springs | CA | CISO | Leeward Asset Management, LLC | Leeward Asset Management, LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | Excess Wind and Solar Generation | 88 | 352 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.85812 |  |  |  |  | insufficient_history |  | insufficient_history | 209.3892 | 0.034898 | 0.9651 | 6000 | 0 | 0 | 1 | 0.87527 | 0 | 88 | 88 |  |  |  |  | 2688.5686 | 490.1076 | 60.7768 | 390.7883 | 0.051638 | 0.16199 | 0.017128 | 0.35714 | 0.0044183 | 0.014728 | 0.0014527 | 0.036819 | RTE_2025: 0.85875; EFC_2025: 209.3892; UTI_2025: 0.91599
64875 | 276 Federal Rd(CSG) | MA | ISNE | 276FED WHAM8 Solar, LLC | 276FED WHAM8 Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 3.3 | 6.9 | 2.0909 | 1.5-2.5h | 2021 | 353 | C | HYBRID_ARTEFACT | 0.73674 | 0.66638 | 0.1537 | -0.0044727 | 8.7771 | -96.8655 | ok | 52.4324 | ok | 168.6957 | 0.028116 | 0.97188 | 6000 | 0 | 0 | 1 | 0.84962 | 0 | 3.3 | 3.3 | 0.0050719 | 0.74108 | 35 | 0.16237 | 21.8599 | 0.66415 | 0.23174 | 0.063548 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.875; RTE_2023: 0.46544; RTE_2024: 0.89011; RTE_2025: 0.80389; EFC_2022: 3.0435; EFC_2023: 29.2754; EFC_2024: 70.4348; EFC_2025: 65.942; UTI_2022: 0.013491; UTI_2023: 0.16385; UTI_2024: 0.34092; UTI_2025: 0.32494 | LOW_ETA_AND_LOW_UTI
64876 | 0 Hammond St CSG | MA | ISNE | 0HAM WHAM8 Solar, LLC | 0HAM WHAM8 Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | System Peak Shaving | 5 | 4.9 | 0.98 | <1.5h | 2021 | 262 | C | HYBRID_ARTEFACT | 0.91732 | 0.87455 | 0.15293 | -0.0059215 | -2.6009 | 27.234 | ok | -1.0236 | ok | 1370.2041 | 0.22837 | 0.77163 | 6000 | 0 | 4 | 1 | 0.86031 | 33 | 2.2 | 2.2 | 0.0076463 | 0.88939 | 36 | 0.16655 | 79.5106 | 21.7413 | 0.14432 | 15.2552 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 | RTE_2023: 0.81514; RTE_2024: 0.87853; RTE_2025: 0.90984; EFC_2023: 74.6939; EFC_2024: 640.6122; EFC_2025: 654.898; UTI_2023: 0.14995; UTI_2024: 1.1296; UTI_2025: 1.3239 | PARTIAL_AVAILABILITY
64877 | Edwards Sanborn E3 | CA | CISO | ES 1A Group 2 Opco, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation | 11 | 31.5 | 2.8636 | 2.5-4.5h | 2021 | 275 | C | HYBRID_ARTEFACT | 0.88596 | 0.83259 | 0.61978 | 0.0082459 | 4.4142 | 74.0167 | ok | 0.39606 | ok | 976.5714 | 0.16276 | 0.83724 | 6000 | 1 | 5 | 1 | 0.92888 | 94.5 | 11 | 11 | 0.068176 | 0.83427 | 44 | 0.11901 | 254.9489 | 37.1803 | 14.8709 | 15.5641 | 0.080762 | 0.20113 | 0.066589 | 0.25527 | 0.0070175 | 0.018713 | 0.0059536 | 0.024561 | RTE_2022: 0.82978; RTE_2023: 0.85468; RTE_2024: 0.8217; RTE_2025: 0.8221; EFC_2022: 204.127; EFC_2023: 327.3016; EFC_2024: 252.6667; EFC_2025: 192.4762; UTI_2022: 1.067; UTI_2023: 1.096; UTI_2024: 1.0536; UTI_2025: 0.66892 | PARTIAL_AVAILABILITY
64878 | Edwards Sanborn E1A | CA | CISO | Terra-Gen Operating Co-Hybrid | Terra-Gen Operating Co-Hybrid |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 144 | 272 | 1.8889 | 1.5-2.5h | 2022 | 53 | C | HYBRID_ARTEFACT | 0.81487 | 0.83161 | -0.14461 | 0.049893 | 1.9295 | 13.3609 | ok | 0.04106 | ok | 992.7684 | 0.16546 | 0.83454 | 6000 | 1 | 4 | 1 | 0.86375 | 4861.5 | 130 | 130 | -0.20823 | 0.83134 | 41 | 0.93534 | 2859.8711 | 860.2024 | 87.6497 | 0.87544 | 0.066091 | 0.31344 | 0.029561 | 0.0011993 | 0.005698 | 0.031339 | 0.00254 | 0.0001 | RTE_2022: 0.84372; RTE_2023: 0.81981; RTE_2024: 0.83184; RTE_2025: 0.8392; EFC_2022: 97.9301; EFC_2023: 309.0221; EFC_2024: 293.386; EFC_2025: 292.4301; UTI_2022: 0.84252; UTI_2023: 0.91982; UTI_2024: 0.91509; UTI_2025: 0.92211 | PARTIAL_AVAILABILITY
64879 | Edwards Sanborn E2 | CA | CISO | Terra-Gen Operating Co-Hybrid | Terra-Gen Operating Co-Hybrid |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 120 | 250 | 2.0833 | 1.5-2.5h | 2022 | 422 | C | HYBRID_ARTEFACT | 0.88516 | 0.811 | 0.65209 | 0.095498 | -6.5877 | -68.2979 | ok | 0.79637 | ok | 1004.256 | 0.16738 | 0.83262 | 6000 | 1 | 5 | 1 | 0.85477 | 2817 | 110 | 110 | 0.78251 | 0.81288 | 44 | 0.28319 | 1878.5612 | 565.0405 | 57.1211 | 0.57505 | 0.066091 | 0.31344 | 0.029335 | 0.0011993 | 0.005698 | 0.031339 | 0.00252 | 0.0001 | RTE_2022: 0.81038; RTE_2023: 0.83152; RTE_2024: 0.80598; RTE_2025: 0.79751; EFC_2022: 204.384; EFC_2023: 316.072; EFC_2024: 268.256; EFC_2025: 215.544; UTI_2022: 0.93349; UTI_2023: 0.93276; UTI_2024: 0.88873; UTI_2025: 0.68898 | PARTIAL_AVAILABILITY
64881 | NMSU Solar and Storage | NM | EPE | El Paso Electric Co | El Paso Electric Co |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, System Peak Shaving | 1 | 4 | 4 | 2.5-4.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
64908 | Scarlet Solar (CA) | CA | CISO | EDP Renewables North America LLC | EDP Renewables North America LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 40 | 200 | 5 | >4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.87465 | 0.82575 | 0.66984 | -0.23723 |  |  | insufficient_history | -0.83495 | ok | 281.515 | 0.046919 | 0.95308 | 6000 | 0 | 0 | 1 | 0.8494 | 0 | 40 | 40 | 0.26794 | 0.8278 | 19 | 0.10331 | 6292.3015 | 57.3522 | 123.1907 | 54.8758 | 0.26681 | 0.050409 | 0.081065 | 0.14373 | 0.025862 | 0.0043103 | 0.0073644 | 0.012931 | RTE_2024: 0.82865; RTE_2025: 0.82741; EFC_2024: 89.125; EFC_2025: 192.39; UTI_2024: 1.3099; UTI_2025: 1.6757
64915 | Flower Valley I | TX | ERCO | Flower Valley | Flower Valley |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 19.8 | 2 | 1.5-2.5h | 2021 |  |  | HEALTHY | 0.9258 | 0.88563 | 0.35535 | -0.00089937 | 12.8531 | 252.9179 | ok | -0.11712 | ok | 1475.5892 | 0.24593 | 0.75407 | 6000 | 2 | 0 | 1 | 0.89565 | 0 | 9.9 | 9.9 | 0.035179 | 0.88568 | 24 | 0.041691 | 345.2497 | 37.762 | 19.3903 | 30.1096 | 0.10203 | 0.19366 | 0.08068 | 0.41615 | 0.0089686 | 0.017937 | 0.0073263 | 0.044843 | RTE_2024: 0.88932; RTE_2025: 0.88215; EFC_2024: 314.899; EFC_2025: 320.9596; UTI_2024: 1.1632; UTI_2025: 1.1681
64916 | Swoose I | TX | ERCO | Swoose | Swoose |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 19.8 | 2 | 1.5-2.5h | 2021 | 142 | A | PARTIAL_AVAILABILITY | 0.93017 | 0.88356 | 0.38332 | 0.00036349 | 0.45947 | 34.2483 | ok | 0.48124 | ok | 1390.2778 | 0.23171 | 0.76829 | 6000 | 3 | 5 | 1 | 0.91016 | 313 | 9.9 | 9.9 | 0.037949 | 0.88411 | 24 | 0.145 | 292.261 | 31.9663 | 16.4143 | 25.4884 | 0.10203 | 0.19366 | 0.08068 | 0.41615 | 0.0089686 | 0.017937 | 0.0073263 | 0.044843 | RTE_2024: 0.88809; RTE_2025: 0.87969; EFC_2024: 316.6162; EFC_2025: 282.1212; UTI_2024: 1.2144; UTI_2025: 0.9945 | PARTIAL_AVAILABILITY
64917 | Triple Butte I | TX | ERCO | Triple Butte | Triple Butte |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 7.5 | 15 | 2 | 1.5-2.5h | 2021 | 168 | B | PARTIAL_AVAILABILITY | 0.91182 | 0.88433 | 0.25286 | 0.0013685 | 8.6065 | 274.7674 | ok | -0.12927 | ok | 1464.4667 | 0.24408 | 0.75592 | 6000 | 0 | 4 | 1 | 0.89267 | 188 | 7.5 | 7.5 | 0.018965 | 0.88445 | 24 | 0.034723 | 264.2855 | 28.9065 | 14.8431 | 23.0486 | 0.10203 | 0.19366 | 0.08068 | 0.41615 | 0.0089686 | 0.017937 | 0.0073263 | 0.044843 | RTE_2024: 0.88824; RTE_2025: 0.8807; EFC_2024: 325.3333; EFC_2025: 325.8; UTI_2024: 1.2044; UTI_2025: 1.1818 | PARTIAL_AVAILABILITY
64921 | Santa Ana Storage 2 | CA | CISO | Johanna Energy Center, LLC | Johanna Energy Center, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve | 20 | 80 | 4 | 2.5-4.5h | 2022 |  |  | HEALTHY | 0.88991 | 0.89544 | -0.31065 | -0.023942 |  |  | insufficient_history | -0.12755 | ok | 1679.45 | 0.27991 | 0.72009 | 6000 | 0 | 0 | 1 | 0.89539 | 0 | 20 | 20 | -0.06213 | 0.89494 | 12 | 0.046943 |  |  |  |  | 0.03025 | 0.20169 | 0.13886 | 0.20982 | 0.0025597 | 0.018771 | 0.01348 | 0.019625 | RTE_2022: 0.89067; RTE_2023: 0.89494; EFC_2022: 595.85; EFC_2023: 1083.6; UTI_2022: 3.4756; UTI_2023: 4.3973
64928 | Edwards Sanborn S3 | CA | CISO | ES 1A Group 2 Opco, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 33 | 70 | 2.1212 | 1.5-2.5h | 2022 | 90 | C | HYBRID_ARTEFACT | 1.1125 | 0.82026 | 2.3428 | -0.0024166 | 2.8411 | 12.2844 | ok | 0.0045188 | ok | 1059.8143 | 0.17664 | 0.82336 | 6000 | 1 | 6 | 1 | 0.97392 | 1582 | 33 | 33 | 0.77312 | 0.82097 | 42 | 0.41764 | 749.6262 | 225.4753 | 22.914 | 0.22947 | 0.066091 | 0.31344 | 0.029485 | 0.0011993 | 0.005698 | 0.031339 | 0.0025333 | 0.0001 | RTE_2022: 0.79946; RTE_2023: 0.82781; RTE_2024: 0.8183; RTE_2025: 0.8275; EFC_2022: 147.9; EFC_2023: 316.0714; EFC_2024: 299.0429; EFC_2025: 296.8; UTI_2022: 0.9123; UTI_2023: 0.9056; UTI_2024: 0.91612; UTI_2025: 0.92239 | PARTIAL_AVAILABILITY
64929 | Edwards Sanborn S1 | CA | CISO | ES 1A Group 2 Opco, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 40 | 83.5 | 2.0875 | 1.5-2.5h | 2022 | 102 | C | HYBRID_ARTEFACT | 0.83076 | 0.84854 | -0.097112 | 0.02204 | -3.7 | -98.1388 | ok | 0.036142 | ok | 829.2695 | 0.13821 | 0.86179 | 6000 | 1 | 6 | 1 | 0.84215 | 1091 | 40 | 40 | -0.038845 | 0.84455 | 42 | 0.0095529 | 492.6414 | 148.1785 | 15.0587 | 0.1508 | 0.066091 | 0.31344 | 0.029485 | 0.0011993 | 0.005698 | 0.031339 | 0.0025333 | 0.0001 | RTE_2022: 0.80041; RTE_2023: 0.88329; RTE_2024: 0.83154; RTE_2025: 0.85981; EFC_2022: 159.4491; EFC_2023: 204.5629; EFC_2024: 252.5389; EFC_2025: 212.7186; UTI_2022: 0.91836; UTI_2023: 0.53026; UTI_2024: 0.93636; UTI_2025: 0.53197 | LOW_ETA_AND_LOW_UTI
64970 | 59 Federal Rd(CSG) | MA | ISNE | 59FED WHAM8 Solar, LLC | 59FED WHAM8 Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 5 | 20.5 | 4.1 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.88007 | 0.61347 | 0.81852 | -0.040215 | -8.609 | -28.152 | ok |  | insufficient_history | 154.3902 | 0.025732 | 0.97427 | 6000 | 0 | 2 | 1 | 0.81918 | 1 | 5 | 5 | 0.040926 | 0.73674 | 21 | 0.48478 | 75.6879 | 4.1392 | 0.049956 | 0.012674 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 | RTE_2023: 0.28; RTE_2024: 0.65817; RTE_2025: 0.72426; EFC_2023: 0.34146; EFC_2024: 73.0732; EFC_2025: 80.9756; UTI_2023: 0; UTI_2024: 0.23859; UTI_2025: 0.26425
64980 | UMass Boston | MA | ISNE | MSS Energy Holdings, LLC (d.b.a. Calibrant Energy) | MSS Energy Holdings, LLC (d.b.a. Calibrant Energy) |  |  | TRUE | pv_same_plant | LIB | BL | Load Management, Excess Wind and Solar Generation | 0.5 | 2.1 | 4.2 | 2.5-4.5h | 2021 | 373 | C | HYBRID_ARTEFACT | 0.77373 | 0.5892 | 0.52018 | -0.00078605 | 18.0811 | 133.708 | ok | 8.7535 | ok | 283.3333 | 0.047222 | 0.95278 | 6000 | 0 | 0 | 1 | 0.9 | 0 | 0.5 | 0.5 | 0.0026009 | 0.72973 | 27 | 0.27226 | 2.2936 | 0.12543 | 0.0015138 | 0.00038405 | 0.1175 | 0.1175 | 0.0011985 | 0.0011993 | 0.010417 | 0.010417 | 0.0001 | 0.0001 |  |  |  | 0.69565 | 0.6962 | 0.65605 | 0.64516 |  |  | 111.4286 | 22.8571 | 52.381 | 49.0476 | 47.619 |  |  | 0.55426 | 0.089885 | 0.15507 | 0.15272 | 0.10099 | LOW_ETA_AND_LOW_UTI
64993 | BigBeau Solar, LLC | CA | CISO | Big Beau Solar, LLC | Big Beau Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 40 | 160 | 4 | 2.5-4.5h | 2022 |  |  | HYBRID_ARTEFACT | 1.0491 | 0.91991 | 1.0336 | 0.022043 | 2.7267 | 241.5472 | ok | 0.53841 | ok | 544.6125 | 0.090769 | 0.90923 | 6000 | 1 | 0 | 1 | 1.0598 | 0 | 40 | 40 | 0.41346 | 0.92737 | 36 | 0.31416 | 343.6134 | 137.8044 | 93.0592 | 45.9492 | 0.03025 | 0.20169 | 0.1077 | 0.20982 | 0.0025597 | 0.018771 | 0.010083 | 0.019625 | RTE_2023: 0.94452; RTE_2024: 0.94395; RTE_2025: 0.88194; EFC_2023: 224.5062; EFC_2024: 179.6625; EFC_2025: 140.4437; UTI_2023: 0.68573; UTI_2024: 0.64866; UTI_2025: 0.45995
65007 | Grant County | WI | MISO | Wisconsin Power & Light Co | Wisconsin Power & Light Co |  |  | TRUE | rte_gt_1,pv_same_plant | ECC | OT |  | 100 | 400 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 0.035 | 5.8333e-06 | 0.99999 | 6000 | 0 | 0 | 1 | 1.2 | 0 | 100 | 100 |  |  |  |  | 3.6244 | 0.39642 | 0.0020184 | 0.18965 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2025: 0.93333; EFC_2025: 0.035; UTI_2025: 0.00044246
65011 | Wood County | WI | MISO | Wisconsin Power & Light Co | Wisconsin Power & Light Co |  |  | TRUE | rte_gt_1,pv_same_plant | ECC | OT |  | 75 | 300 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 0.03 | 5e-06 | 0.99999 | 6000 | 0 | 0 | 1 | 1 | 0 | 75 | 75 |  |  |  |  | 4.0775 | 0.44598 | 0.0022707 | 0.21336 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2025: 1; EFC_2025: 0.03; UTI_2025: 0.00065359
65014 | ASD Cotuit MA Solar LLC | MA | ISNE | ASD Cotuit MA Solar LLC | ASD Cotuit MA Solar LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 2.5 | 4.2 | 1.68 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.97643 | 0.64149 | 0.0256 | -2.8451e-05 |  |  | insufficient_history |  | insufficient_history | 30.9524 | 0.0051587 | 0.99484 | 6000 | 0 | 0 | 1 | 0.94 | 0 | 1.5 | 1.5 | 0.00064001 | 0.92424 | 12 | 0.31065 | 5.2231 | 0.17138 | 0.057033 | 0.10021 | 0.17285 | 0.10762 | 0.02924 | 0.1884 | 0.015814 | 0.0094887 | 0.0025116 | 0.017396 | RTE_2024: 0.14815; RTE_2025: 0.92424; EFC_2024: 1.9048; EFC_2025: 29.0476; UTI_2024: 0.01318; UTI_2025: 0.10912
65015 | ASD Wallum MA Solar LLC(CSG) | MA | ISNE | ASD Wallum MA Solar LLC | ASD Wallum MA Solar LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 3.8 | 12.8 | 3.3684 | 2.5-4.5h | 2022 | 310 | C | HYBRID_ARTEFACT | 1.0065 | 0.77954 | 0.21923 | -0.0038855 | 0.10761 | 47.6376 | ok | -1.9646 | ok | 330.5469 | 0.055091 | 0.94491 | 6000 | 0 | 2 | 1 | 0.96875 | 2 | 3.8 | 3.8 | 0.0083307 | 0.9554 | 33 | 0.85226 | 225.3207 | 12.3223 | 0.077457 | 2.9476 | 0.21337 | 0.21337 | 0.0011985 | 0.16473 | 0.02 | 0.02 | 0.0001 | 0.015 | RTE_2022: 0.98042; RTE_2023: 0.97311; RTE_2024: 0.43226; RTE_2025: 0.96077; EFC_2022: 54.7656; EFC_2023: 138.5156; EFC_2024: 5.2344; EFC_2025: 132.0312; UTI_2022: 0.21536; UTI_2023: 0.4715; UTI_2024: 0.021116; UTI_2025: 0.59172 | PARTIAL_AVAILABILITY
65018 | Mossy Branch Battery Facility | GA | SOCO | Georgia Power Co | Georgia Power Co |  |  | FALSE |  | LIB | OT | Frequency Regulation, Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support | 65 | 260 | 4 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.89205 | 0.86396 | 0.50893 | 0.046937 |  |  | insufficient_history |  | insufficient_history | 380.6192 | 0.063437 | 0.93656 | 6000 | 0 | 0 | 1 | 0.86468 | 8721.9597 | 65 | 65 | 0.33081 | 0.86547 | 14 | 0.31349 | 3869.4132 | 211.6102 | 126.0584 | 303.7101 | 0.081309 | 0.081309 | 0.038602 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033487 | 0.031802 | RTE_2024: 0.86174; RTE_2025: 0.86609; EFC_2024: 53.8885; EFC_2025: 326.7308; UTI_2024: 1.0885; UTI_2025: 1.1689
65028 | Roseland Solar Project, LLC | TX | ERCO | Enel Kansas, LLC | Enel Green Power Roseland Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 51.8 | 84.5 | 1.6313 | 1.5-2.5h | 2023 | 383 | C | HYBRID_ARTEFACT | 0.79994 | 0.63692 | 0.75006 | -0.12591 | 10.7744 | 20.1882 | ok | -1.7449 | ok | 381.7278 | 0.063621 | 0.93638 | 6000 | 2 | 0 | 1 | 0.78525 | 0 | 50 | 50 | 0.38853 | 0.67586 | 30 | 0.87763 | 332.154 | 54.4945 | 80.3498 | 92.696 | 0.031828 | 0.092476 | 0.10197 | 0.404 | 0.0026954 | 0.0080863 | 0.0094837 | 0.043127 | RTE_2023: 0.55243; RTE_2024: 0.58943; RTE_2025: 0.75324; EFC_2023: 42.0237; EFC_2024: 102.2959; EFC_2025: 237.4083; UTI_2023: 0.43996; UTI_2024: 0.35267; UTI_2025: 0.81595 | LOW_ETA_AND_LOW_UTI
65029 | Bissell Solar and Battery Generator | MI | MISO | Consumers Energy Co - (MI) | Consumers Energy Co - (MI) |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant | LIB | BL | Arbitrage, Transmission and Distribution Deferral, System Peak Shaving, Load Management | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2021 | 298 | C | FULL_OUTAGE | 0.8708 | 0.55306 | 0.40144 | -0.00023521 |  |  | ok |  | insufficient_history | 234 | 0.039 | 0.961 | 6000 | 0 | 19 | 1 | 0.83333 | 12.5 | 0.3 | 0.3 | 0.0012043 | 0.73438 | 12 | 0.85898 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 |  |  | 0.8 | 0.76829 | 0.73016 | 0.13043 | 0.5 |  |  | 8 | 126 | 92 | 6 | 2 |  |  | 0.1587 | 0.5439 | 0.21178 | 0 | 0 | FULL_OUTAGE
65035 | Fox Hills Battery Station | NY | NYIS | Consolidated Edison Co-NY Inc | Consolidated Edison Co-NY Inc |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 7.5 | 30 | 4 | 2.5-4.5h | 2023 |  |  | UNDER_DISPATCH | 0.90022 | 0.80906 | 0.7632 | -0.053143 |  |  | insufficient_history |  | insufficient_history | 334.1444 | 0.055691 | 0.94431 | 6000 | 0 | 0 | 1 | 0.78579 | 1901.2362 | 7.5 | 7.5 | 0.05724 | 0.84668 | 15 | 0.28757 | 1223.5551 | 0.25929 | 0.32598 | 16.0061 | 0.26632 | 0.0011993 | 0.0011985 | 0.20726 | 0.025806 | 0.0001 | 0.0001 | 0.019355 | RTE_2024: 0.86861; RTE_2025: 0.83481; EFC_2024: 80.4333; EFC_2025: 226.9; UTI_2024: 0.994; UTI_2025: 0.9061
65044 | Dry Bridge Storage | VA | PJM | Dominion Energy Inc. | Dominion Energy Inc. |  |  | FALSE |  | LIB | CS |  | 20 | 80 | 4 | 2.5-4.5h | 2023 |  |  | UNATTRIBUTED | 0.95431 | 0.89685 | 0.842 | 0.048845 | -5.6905 | -243.4666 | ok | -0.26193 | ok | 629.4604 | 0.10491 | 0.89509 | 6000 | 0 | 0 | 1 | 0.94995 | 761.75 | 20 | 20 | 0.1684 | 0.89957 | 24 | 0.16864 | 1397.1631 | 89.6963 | 4.1271 | 24.3696 | 0.12376 | 0.14367 | 0.0056438 | 0.12376 | 0.01101 | 0.012925 | 0.00047304 | 0.01101 | RTE_2024: 0.86629; RTE_2025: 0.93396; EFC_2024: 284.8375; EFC_2025: 297.15; UTI_2024: 1.0082; UTI_2025: 0.9111
65053 | Blythe Mesa Solar II | CA | CISO | Intersect USA, LLC | Intersect USA, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Co-Located Renewable Firming | 112 | 448 | 4 | 2.5-4.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.93093 | 0.89402 | 0.60126 | 0.25775 | 2.6387 | 56.3078 | ok | -0.072987 | ok | 871.2924 | 0.14522 | 0.85478 | 6000 | 5 | 0 | 1 | 0.91017 | 0 | 112 | 112 | 0.67341 | 0.89552 | 34 | 0.29557 | 2450.1945 | 982.6379 | 677.8098 | 327.649 | 0.03025 | 0.20169 | 0.10976 | 0.20982 | 0.0025597 | 0.018771 | 0.010299 | 0.019625 | RTE_2023: 0.88815; RTE_2024: 0.8896; RTE_2025: 0.90597; EFC_2023: 223.7254; EFC_2024: 308.4018; EFC_2025: 339.1652; UTI_2023: 0.93017; UTI_2024: 1.174; UTI_2025: 1.1663
65054 | 71 Charlotte Furnace Rd Hybrid(CSG) | MA | ISNE | 71CFR WHAM8 Solar, LLC | 71CFR WHAM8 Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 1 | 5.4 | 5.4 | >4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.88448 | 0.85077 | 0.16668 | -0.0013099 | 0.6925 | 20.4573 | ok | -0.18717 | ok | 218.3333 | 0.036389 | 0.96361 | 6000 | 0 | 0 | 1 | 0.96842 | 0 | 1 | 1 | 0.0016668 | 0.87011 | 36 | 0.2463 | 29.8026 | 1.7928 | 0.016904 | 0.41586 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2023: 0.7378; RTE_2024: 0.94981; RTE_2025: 0.87426; EFC_2023: 44.8148; EFC_2024: 91.1111; EFC_2025: 82.4074; UTI_2023: 0.22301; UTI_2024: 0.87153; UTI_2025: 0.7538
65055 | 77 Farm to Market Rd Hybrid(CSG) | MA | ISNE | 77F2M WHAM8 Solar, LLC | 77F2M WHAM8 Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 2.2 | 4.8 | 2.1818 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.87578 | 0.6495 | 0.086878 | 0.0013742 | 6.5802 | 51.8561 | ok |  | insufficient_history | 161.0417 | 0.02684 | 0.97316 | 6000 | 0 | 0 | 1 | 0.95349 | 0 | 2.2 | 2.2 | 0.0019113 | 0.90403 | 30 | 0.44982 | 19.4838 | 0.59196 | 0.20655 | 0.05664 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2023: 0.48571; RTE_2024: 0.88647; RTE_2025: 0.93939; EFC_2023: 7.0833; EFC_2024: 76.4583; EFC_2025: 77.5; UTI_2023: 0.03665; UTI_2024: 0.49462; UTI_2025: 0.50909
65056 | 160 Tihonet Rd Hybrid(CSG) | MA | ISNE | 160TIH WHAM8 Solar, LLC | 160TIH WHAM8 Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 3.3 | 6.9 | 2.0909 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.9428 | 0.77737 | 0.088521 | 0.0053166 | -7.8839 | 27.3931 | ok |  | insufficient_history | 138.9855 | 0.023164 | 0.97684 | 6000 | 0 | 0 | 1 | 0.88182 | 0 | 3.3 | 3.3 | 0.0029212 | 0.8984 | 21 | 0.47557 | 34.6907 | 1.054 | 0.36776 | 0.10085 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 0.66667; RTE_2023: 0; RTE_2024: 0.91791; RTE_2025: 0.86431; EFC_2022: 0.28986; EFC_2023: 0; EFC_2024: 71.3043; EFC_2025: 67.3913; UTI_2022: 0.015935; UTI_2023: 0; UTI_2024: 0.45452; UTI_2025: 0.64655
65057 | 299 Farm to Market Rd Hybrid(CSG) | MA | ISNE | 299F2M WHAM8 Solar, LLC | 299F2M WHAM8 Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 2.3 | 4.9 | 2.1304 | 1.5-2.5h | 2021 | 368 | C | HYBRID_ARTEFACT | 0.84668 | 0.9371 | -0.21503 | -0.0014403 | 4.1933 | -79.5357 | ok | 14.2658 | ok | 258.5714 | 0.043095 | 0.9569 | 6000 | 0 | 0 | 1 | 1 | 0 | 2.2 | 2.2 | -0.0049457 | 0.98283 | 36 | 0.2742 | 22.3351 | 0.67859 | 0.23678 | 0.064929 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2022: 1; RTE_2023: 0.78492; RTE_2024: 1.1075; RTE_2025: 1.0744; EFC_2022: 1.6327; EFC_2023: 72.2449; EFC_2024: 90.4082; EFC_2025: 94.2857; UTI_2022: 0.089756; UTI_2023: 0.3886; UTI_2024: 0.45418; UTI_2025: 0.52554 | LOW_ETA_AND_LOW_UTI
65058 | Waiawa Solar Power Hybrid | HI | HECO | Waiawa Solar Power LLC | Waiawa Solar Power LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS |  | 36 | 4.6 | 0.12778 | <1.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.96914 | 0.91306 | 0.52627 | -0.16199 | -6.4196 | 182.2887 | ok | 0.025899 | ok | 17547.8261 | 2.9246 | 0 | 6000 | 0 | 0 | 1 | 0.85502 | 0 | 2.3 | 2.3 | 0.18946 | 0.9239 | 30 | 0.33864 | 3820.8648 | 1.1144 | 125.9439 | 66.6444 | 0.20148 | 0.0011993 | 0.097179 | 0.20148 | 0.01875 | 0.0001 | 0.0089893 | 0.01875 | RTE_2023: 0.98773; RTE_2024: 0.97404; RTE_2025: 0.83464; EFC_2023: 3798.4783; EFC_2024: 7731.9565; EFC_2025: 6017.3913; UTI_2023: 15.1362; UTI_2024: 19.9938; UTI_2025: 20.2626
65098 | South Sioux City Energy Storage | NE | SWPP | DG Nebraska Energy Storage, LLC | DG Nebraska Energy Storage, LLC |  |  | FALSE |  | LIB | CS | System Peak Shaving | 1.5 | 3 | 2 | 1.5-2.5h | 2020 | 253 | A | CAPACITY_FADE | 0.78582 | 0.79099 | -0.0022327 | 0.00017031 |  |  | insufficient_history | -12.3361 | ok | 533.75 | 0.088958 | 0.91104 | 6000 | 0 | 2 | 1 | 1 | 38.1524 | 1.5 | 1.5 | -3.3491e-05 | 0.87382 | 18 | 3.0593e-05 | 27.7268 | 1.769 | 0.0085783 | 0.16121 | 0.23407 | 0.26737 | 0.0011985 | 0.085053 | 0.022222 | 0.025926 | 0.0001 | 0.0074074 | RTE_2024: 1; RTE_2025: 0.71617; EFC_2024: 113; EFC_2025: 72.3333; UTI_2024: 0.11852; UTI_2025: 0.24205 | LOW_ETA_AND_LOW_UTI
65114 | 196 Tremont St(CSG) | MA | ISNE | 196TRE WHAM8 Solar, LLC | 196TRE WHAM8 Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 1.5 | 8 | 5.3333 | >4.5h | 2021 | 358 | C | HYBRID_ARTEFACT | 0.7903 | 0.77163 | -0.006448 | -0.00040893 | -1.6019 | 158.5156 | ok |  | insufficient_history | 192.375 | 0.032063 | 0.96794 | 6000 | 0 | 0 | 1 | 0.75758 | 0 | 1.5 | 1.5 | -9.6719e-05 | 0.81606 | 31 | 0.0053336 | 72.5047 | 4.3616 | 0.041126 | 1.0117 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2023: 0.57576; RTE_2024: 0.91434; RTE_2025: 0.77543; EFC_2023: 2.375; EFC_2024: 61.375; EFC_2025: 128.625; UTI_2023: 0.036093; UTI_2024: 0.50796; UTI_2025: 1.1927 | LOW_ETA_AND_LOW_UTI
65132 | University of the Pacific | CA | CISO | The Greater Light USA LLC | The Greater Light USA LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 1 | 2.2 | 2.2 | 1.5-2.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
65140 | Crimson | CA | CISO | Axium Infrastructure US Inc. | RE Crimson LLC |  |  | FALSE |  | LIB | CS |  | 350 | 1400 | 4 | 2.5-4.5h | 2022 | 426 | B | UNDER_DISPATCH | 0.87457 | 0.88237 | -0.13877 | 0.090012 | -1.1164 | -61.7587 | ok | 0.076813 | ok | 1052.2657 | 0.17538 | 0.82462 | 6000 | 5 | 2 | 1 | 0.88014 | 53619.2989 | 350 | 350 | -0.48569 | 0.88212 | 39 | 0.0398 | 7934.7639 | 3182.1963 | 2083.3034 | 1061.0657 | 0.03025 | 0.20169 | 0.10477 | 0.20982 | 0.0025597 | 0.018771 | 0.0097751 | 0.019625 | RTE_2022: 0.86777; RTE_2023: 0.88591; RTE_2024: 0.88036; RTE_2025: 0.88297; EFC_2022: 71.6571; EFC_2023: 333.84; EFC_2024: 291.03; EFC_2025: 355.7386; UTI_2022: 1.0764; UTI_2023: 1.211; UTI_2024: 1.2134; UTI_2025: 1.2238 | PARTIAL_AVAILABILITY
65154 | UMass PV Lot 22 | MA | ISNE | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Load Management, Excess Wind and Solar Generation | 2 | 4.3 | 2.15 | 1.5-2.5h | 2022 | 330 | C | HYBRID_ARTEFACT | 0.77745 | 0.6333 | 0.29175 | -0.0031181 |  |  | insufficient_history |  | insufficient_history | 55.5814 | 0.0092636 | 0.99074 | 6000 | 0 | 0 | 0.81818 | 0.8 | 0 | 1.1 | 0.9 | 0.0058351 | 0.69679 | 11 | 0.49371 | 18.267 | 0.42814 | 0.17457 | 0.13655 | 0.17028 | 0.076884 | 0.025277 | 0.076884 | 0.015556 | 0.0066667 | 0.0021622 | 0.0066667 | RTE_2025: 0.68678; EFC_2025: 55.5814; UTI_2025: 0.37521 | LOW_ETA_AND_LOW_UTI
65174 | Cranberry Highway Solar LLC | MA | ISNE | Cranberry Highway Solar, LLC | Cranberry Highway Solar, LLC |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 2 | 4.5 | 2.25 | 1.5-2.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.94094 | 0.95244 | 0.018345 | -0.0048397 | 10.1385 | 171.5639 | ok | 1.9096 | ok | 634.8889 | 0.10581 | 0.89419 | 6000 | 0 | 0 | 1 | 0.98691 | 0 | 2 | 2 | 0.0003669 | 0.93608 | 36 | 0.0010038 | 35.1659 | 1.0684 | 0.37279 | 0.10223 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 |  |  |  | 1.0423 | 0.87097 | 0.97528 | 0.96788 |  |  | 106.4444 | 235.5556 | 96 | 96.4444 | 100.4444 |  |  | 0.57732 | 1.0442 | 0.54515 | 0.6455 | 0.89837
65217 | South Goshen Community Solar | NY | NYIS | AES Distributed Energy | AES Distributed Energy |  |  | TRUE | pv_same_plant,dc_tight | LIB | OT | System Peak Shaving | 4.5 | 17 | 3.7778 | 2.5-4.5h | 2021 | 197 | C | HYBRID_ARTEFACT | 0.84243 | 0.81149 | 0.059015 | -0.0066795 | -4.0842 | -56.5645 | ok | -1.8124 | ok | 139.1765 | 0.023196 | 0.9768 | 6000 | 0 | 2 | 1 | 0.92607 | 102 | 4.5 | 4.5 | 0.0026557 | 0.86376 | 33 | 0.35577 | 98.2355 | 0.01746 | 0.02195 | 0.0055687 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 |  |  | 0 | 0.829 | 0.88769 | 0.81378 | 0.84919 |  |  | 0 | 13.1176 | 72.5294 | 25.7059 | 27.8235 |  |  | 0 | 0.052618 | 0.22399 | 0.068437 | 0.1086 | LOW_ETA_AND_LOW_UTI
65239 | AE-ESS NWS 1, LLC | NY | NYIS | AE-ESS NWS, LLC | Agilitas Energy, Inc. |  |  | FALSE |  | LIB | CS | Arbitrage | 5 | 24.6 | 4.92 | >4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.86399 |  |  |  |  | insufficient_history |  | insufficient_history | 80.3252 | 0.013388 | 0.98661 | 6000 | 0 | 0 | 1 | 0.91579 | 394.7713 | 4.8 | 4.8 |  |  |  |  | 226.8553 | 13.6469 | 0.12868 | 3.1655 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2025: 0.8334; EFC_2025: 80.3252; UTI_2025: 0.97786
65240 | Maysville BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 | 129 | A | UNATTRIBUTED | 0.76641 | 0.60601 | 0.5146 | 0.016122 | -12.5287 | -56.8912 | ok | -0.2462 | ok | 144.5 | 0.024083 | 0.97592 | 6000 | 0 | 0 | 1 | 0.63889 | 543.1289 | 5 | 5 | 0.02573 | 0.61884 | 24 | 0.54981 | 13.602 | 0.019266 | 0.024221 | 4.0332 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.63629; RTE_2025: 0.59832; EFC_2024: 80.3; EFC_2025: 64.2; UTI_2024: 0.35991; UTI_2025: 0.22139 | LOW_ETA_AND_LOW_UTI
65241 | McKinney BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 | 118 | A | UNATTRIBUTED | 0.75647 | 0.55359 | 0.595 | 0.016989 | -19.1091 | -62.175 | ok | 7.2757 | ok | 120.3 | 0.02005 | 0.97995 | 6000 | 0 | 0 | 1 | 0.74706 | 605.1894 | 5 | 5 | 0.02975 | 0.57368 | 24 | 0.59406 | 10.7683 | 0.015252 | 0.019175 | 3.193 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.60172; RTE_2025: 0.53895; EFC_2024: 69.8; EFC_2025: 50.5; UTI_2024: 0.28167; UTI_2025: 0.17161 | LOW_ETA_AND_LOW_UTI
65242 | Charlemont A | MA | ISNE | Agilitas Energy, Inc. | Agilitas Energy, Inc. |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving | 2.5 | 3.8 | 1.52 | 1.5-2.5h | 2021 | 178 | C | FULL_OUTAGE | 0.92833 | 0.89599 | 0.038476 |  |  |  | insufficient_history |  | insufficient_history | 97.1053 | 0.016184 | 0.98382 | 6000 | 0 | 20 | 1 | 1 | 154.5 | 1.5 | 1.5 | 0.00096191 | 0.92481 | 14 | 0.12621 | 0 | 0 | 0 | 0 | 0.14392 | 0.082709 | 0.023436 | 0.025567 | 0.01295 | 0.0071942 | 0.0020009 | 0.0021583 | RTE_2023: 0.88732; RTE_2024: 0.94186; EFC_2023: 33.1579; EFC_2024: 63.9474; EFC_2025: 0; UTI_2023: 0.14225; UTI_2024: 0.34649; UTI_2025: 0 | FULL_OUTAGE
65243 | New Rosewood BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 2.5 | 10 | 4 | 2.5-4.5h | 2024 | 136 | A | UNATTRIBUTED | 0.80712 | 0.58296 | 0.62295 | 0.0084851 |  |  | ok | 2.2373 | ok | 64.8 | 0.0108 | 0.9892 | 6000 | 0 | 2 | 1 | 0.80282 | 322.5731 | 2.5 | 2.5 | 0.015574 | 0.60837 | 23 | 0.63008 | 17.3736 | 1.1154 | 0.05132 | 0.30303 | 0.12376 | 0.14367 | 0.0056438 | 0.12376 | 0.01101 | 0.012925 | 0.00047304 | 0.01101 | RTE_2024: 0.63; RTE_2025: 0.56604; EFC_2024: 37.8; EFC_2025: 27; UTI_2024: 0.14524; UTI_2025: 0.089855 | LOW_ETA_AND_LOW_UTI
65244 | Queens Creek BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 2.5 | 5 | 2 | 1.5-2.5h | 2024 | 151 | A | UNATTRIBUTED | 0.74284 | 0.56978 | 0.52291 | 0.011315 | -4.2644 | -15.0072 | ok | 5.5831 | ok | 130.4 | 0.021733 | 0.97827 | 6000 | 0 | 0 | 1 | 0.7561 | 283.2905 | 2.5 | 2.5 | 0.013073 | 0.59502 | 23 | 0.54089 | 7.2261 | 0.010235 | 0.012868 | 2.1427 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.59331; RTE_2025: 0.58118; EFC_2024: 67.4; EFC_2025: 63; UTI_2024: 0.23171; UTI_2025: 0.22692 | LOW_ETA_AND_LOW_UTI
65245 | Rocky Point BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 5 | 1 | <1.5h | 2024 | 137 | A | UNATTRIBUTED | 0.77489 | 0.57105 | 0.27959 | 0.014739 | -13.9171 | -63.3737 | ok | 1.4572 | ok | 130.8 | 0.0218 | 0.9782 | 6000 | 0 | 0 | 1 | 0.76543 | 318.5144 | 2.5 | 2.5 | 0.01398 | 0.60957 | 22 | 0.52063 | 25.8146 | 1.2 | 0.25313 | 0.96807 | 0.15254 | 0.13124 | 0.023051 | 0.29943 | 0.013793 | 0.011724 | 0.0019672 | 0.029655 | RTE_2024: 0.61002; RTE_2025: 0.57643; EFC_2024: 68.2; EFC_2025: 62.6; UTI_2024: 0.15122; UTI_2025: 0.21092 | LOW_ETA_AND_LOW_UTI
65246 | Walkers Crossroads BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 | 128 | A | UNATTRIBUTED | 0.76413 | 0.58837 | 0.55027 | 0.021691 | -19.6192 | -75.0727 | ok | 0.70588 | ok | 138.8 | 0.023133 | 0.97687 | 6000 | 0 | 0 | 1 | 0.75625 | 554.747 | 5 | 5 | 0.027513 | 0.60984 | 24 | 0.59931 | 10.91 | 0.015453 | 0.019427 | 3.235 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.64198; RTE_2025: 0.56735; EFC_2024: 83.2; EFC_2025: 55.6; UTI_2024: 0.3298; UTI_2025: 0.18747 | LOW_ETA_AND_LOW_UTI
65247 | Zion Hill BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 | 111 | A | UNATTRIBUTED | 0.84647 | 0.57685 | 0.75651 | 0.020864 | -21.0861 | -51.5355 | ok | -1.9659 | ok | 134.6 | 0.022433 | 0.97757 | 6000 | 0 | 0 | 1 | 0.7561 | 568.7892 | 5 | 5 | 0.037825 | 0.60143 | 24 | 0.65201 | 9.7765 | 0.013848 | 0.017409 | 2.8989 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.64139; RTE_2025: 0.54407; EFC_2024: 84.6; EFC_2025: 50; UTI_2024: 0.35024; UTI_2025: 0.22241 | LOW_ETA_AND_LOW_UTI
65248 | Collier BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 2.5 | 5 | 2 | 1.5-2.5h | 2024 | 160 | A | UNATTRIBUTED | 0.78737 | 0.58869 | 0.58524 | 0.0063515 | -13.88 | -39.947 | ok | 7.6922 | ok | 139.8 | 0.0233 | 0.9767 | 6000 | 0 | 0 | 1 | 0.75 | 273.1698 | 2.5 | 2.5 | 0.014631 | 0.61316 | 24 | 0.74225 | 6.376 | 0.009031 | 0.011354 | 1.8906 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.64823; RTE_2025: 0.56646; EFC_2024: 84.4; EFC_2025: 55.4; UTI_2024: 0.32523; UTI_2025: 0.22686 | LOW_ETA_AND_LOW_UTI
65249 | Docs Road BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 | 124 | A | UNATTRIBUTED | 0.73752 | 0.55415 | 0.47812 | 0.0090328 | -14.5652 | -48.1898 | ok | -0.31377 | ok | 119.1 | 0.01985 | 0.98015 | 6000 | 0 | 1 | 1 | 0.59211 | 573.002 | 5 | 5 | 0.023906 | 0.59829 | 22 | 0.8206 | 8.7847 | 0.012443 | 0.015643 | 2.6048 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.6276; RTE_2025: 0.54432; EFC_2024: 75.5; EFC_2025: 43.6; UTI_2024: 0.31578; UTI_2025: 0.13153 | LOW_ETA_AND_LOW_UTI
65250 | Five Points BESS | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | 0.87328 | 0.62118 | 0.68729 | 0.018446 |  |  | ok | 1.6959 | ok | 136.2 | 0.0227 | 0.9773 | 6000 | 0 | 0 | 1 | 0.60927 | 3298.4658 | 5 | 5 | 0.034364 | 0.63319 | 23 | 0.65701 | 13.602 | 0.019266 | 0.024221 | 4.0332 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.63874; RTE_2025: 0.60811; EFC_2024: 73.2; EFC_2025: 63; UTI_2024: 0.32854; UTI_2025: 0.2235
65259 | Byrd Ranch Storage | TX | ERCO | Byrd Ranch Storage LLC | Byrd Ranch Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Voltage or Reactive Power Support | 50 | 50 | 1 | <1.5h | 2022 |  |  | CAPACITY_FADE | 0.86009 | 0.6037 | 0.44434 | 0.0079761 | 1.2934 | -6.7221 | ok | -10.1518 | ok | 496.82 | 0.082803 | 0.9172 | 6000 | 2 | 0 | 1 | 0.81448 | 5199.9566 | 50 | 50 | 0.22217 | 0.73898 | 29 | 0.92685 | 80.3609 | 21.9739 | 38.2286 | 81.297 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2023: 0.33671; RTE_2024: 0.70895; RTE_2025: 0.78218; EFC_2023: 26.62; EFC_2024: 170.36; EFC_2025: 299.84; UTI_2023: 0.053676; UTI_2024: 0.64749; UTI_2025: 1.3216
65271 | Noble Solar | TX | ERCO | Geronimo Power | Geronimo Power |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Voltage or Reactive Power Support | 125 | 125 | 1 | <1.5h | 2022 | 101 | C | HYBRID_ARTEFACT | 0.88097 | 0.65553 | 0.14635 | -0.026995 | 5.948 | -105.4531 | ok | -7.2931 | ok | 258.648 | 0.043108 | 0.95689 | 6000 | 3 | 2 | 1 | 0.84788 | 681 | 125 | 125 | 0.18293 | 0.79696 | 31 | 0.44476 | 80.2628 | 21.947 | 37.4602 | 81.1978 | 0.010638 | 0.052071 | 0.067596 | 0.46223 | 0.00089127 | 0.0044563 | 0.0060502 | 0.051693 | RTE_2022: 0.34871; RTE_2023: 0.47526; RTE_2024: 0.81996; RTE_2025: 0.8868; EFC_2022: 9.432; EFC_2023: 28.816; EFC_2024: 90.36; EFC_2025: 130.04; UTI_2022: 0.091192; UTI_2023: 0.023886; UTI_2024: 0.33792; UTI_2025: 0.52873 | PARTIAL_AVAILABILITY
65291 | Golden Triangle II | MS | TVA | Origis Energy USA, Inc | Origis Energy USA, Inc |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 50 | 200 | 4 | 2.5-4.5h | 2024 | 363 | C | HYBRID_ARTEFACT | 0.99357 | 0.79495 | 1.3048 | 0.12897 |  |  | insufficient_history | -1.7292 | ok | 208.23 | 0.034705 | 0.9653 | 6000 | 0 | 0 | 1 | 0.82464 | 0 | 50 | 50 | 0.65242 | 0.81418 | 19 | 0.70442 | 1368.0399 | 74.8153 | 43.9551 | 107.3774 | 0.081309 | 0.081309 | 0.038091 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033026 | 0.031802 | RTE_2024: 0.78818; RTE_2025: 0.82659; EFC_2024: 65.135; EFC_2025: 143.095; UTI_2024: 0.36603; UTI_2025: 0.54322 | ELEVATED_P_AUX
65351 | General Dynamics | AR | MISO | Today's Power, Inc. | Today's Power, Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 5 | 9.6 | 1.92 | 1.5-2.5h | 2020 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 5 | 5
65382 | Lincoln WWTF Hybrid | CA | CISO | ST TOTAL Strong Solar Statutory Trust | Lincoln Solar Star, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 1 | 2 | 2 | 1.5-2.5h | 2022 | 244 | C | HYBRID_ARTEFACT | 0.79206 | 0.75764 | 0.09945 | 0.0043897 |  |  | insufficient_history |  | insufficient_history | 217 | 0.036167 | 0.96383 | 6000 | 0 | 2 | 1 | 0.84 | 43.5 | 1 | 1 | 0.0009945 | 0.78481 | 12 | 0.91057 | 16.519 | 4.9686 | 0.54834 | 0.0050566 | 0.066091 | 0.31344 | 0.031937 | 0.0011993 | 0.005698 | 0.031339 | 0.0027511 | 0.0001 | RTE_2025: 0.78481; EFC_2025: 217; UTI_2025: 0.73766 | PARTIAL_AVAILABILITY
65396 | Black Walnut Energy Storage LLC | CA | CISO | Black Walnut Energy Storage LLC | Black Walnut Energy Storage LLC |  |  | FALSE |  | LIB | CS |  | 15 | 15 | 1 | <1.5h | 2025 |  |  | HEALTHY |  | 0.89259 |  |  |  |  | insufficient_history |  | insufficient_history | 144.0667 | 0.024011 | 0.97599 | 6000 | 0 | 0 | 1 | 0.87569 | 0 | 15 | 15 |  |  |  |  | 1268.8418 | 34.6952 | 0.54523 | 60.8614 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.89187; EFC_2025: 144.0667; UTI_2025: 1.2112
65397 | Santa Paula Energy Storage LLC | CA | CISO | Santa Paula Energy Storage, LLC | Santa Paula Energy Storage, LLC |  |  | FALSE |  | LIB | CS |  | 30 | 30 | 1 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.87257 | 0.9019 | -0.24667 | 0.045558 |  |  | insufficient_history |  | insufficient_history | 729.0333 | 0.12151 | 0.87849 | 6000 | 0 | 0 | 1 | 0.84848 | 1399.2438 | 30 | 30 | -0.074002 | 0.89956 | 14 | 0.040613 | 1885.9416 | 51.5691 | 0.8104 | 90.4613 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.88707; RTE_2025: 0.90148; EFC_2024: 95.8333; EFC_2025: 633.2; UTI_2024: 0.86007; UTI_2025: 0.7635
65408 | Gilead Oceanside Solar Project | CA | CISO | Gilead Sciences Inc. | Gilead Sciences Inc. |  |  | TRUE | pv_same_plant | LIB | CT | Arbitrage, System Peak Shaving, Excess Wind and Solar Generation | 0.7 | 3 | 4.2857 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT |  | 0.85504 |  |  |  |  | insufficient_history |  | insufficient_history | 66.3333 | 0.011056 | 0.98894 | 6000 | 0 | 1 | 1 | 0.85185 | 28.5 | 0.7 | 0.7 |  |  |  |  | 12.3612 | 1.8027 | 0.92085 | 0.75462 | 0.080762 | 0.20113 | 0.083474 | 0.25527 | 0.0070175 | 0.018713 | 0.0076036 | 0.024561 | RTE_2025: 0.869; EFC_2025: 66.3333; UTI_2025: 0.33849
65409 | Gilead Foster City Solar Project | CA | CISO | Gilead Sciences Inc. Foster City | Gilead Sciences Inc. Foster City |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CT | Excess Wind and Solar Generation | 0.5 | 0.9 | 1.8 | 1.5-2.5h | 2021 | 304 | C | HYBRID_ARTEFACT | 0.81278 | 0.87323 | -0.51053 | -0.00013673 | -8.2075 | -107.7373 | ok | -0.025066 | ok | 866.6667 | 0.14444 | 0.85556 | 6000 | 0 | 2 | 1 | 0.89286 | 3.5 | 0.5 | 0.5 | -0.0025527 | 0.87542 | 36 | 0.54851 | 13.5687 | 1.4841 | 0.95025 | 0.355 | 0.095923 | 0.18264 | 0.092976 | 0.14038 | 0.0084034 | 0.016807 | 0.0085598 | 0.012605 | RTE_2023: 0.87986; RTE_2024: 0.87869; RTE_2025: 0.86799; EFC_2023: 276.6667; EFC_2024: 297.7778; EFC_2025: 292.2222; UTI_2023: 0.92167; UTI_2024: 0.92766; UTI_2025: 0.90168 | LOW_ETA_AND_LOW_UTI
65410 | Cunningham Storage | TX | ERCO | Acciona Energy USA Global, LLC | Acciona Energy USA Global, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 190 | 380 | 2 | 1.5-2.5h | 2023 |  |  | UNDER_DISPATCH | 0.91724 | 0.84784 | 0.36317 | 0.13725 | -3.9994 | -42.6671 | ok | -0.055152 | ok | 486.9079 | 0.081151 | 0.91885 | 6000 | 1 | 0 | 1 | 0.871 | 38282.3417 | 190 | 190 | 0.69003 | 0.85443 | 29 | 0.73884 | 1545.8317 | 253.615 | 377.6751 | 431.4037 | 0.031828 | 0.092476 | 0.10288 | 0.404 | 0.0026954 | 0.0080863 | 0.0095783 | 0.043127 | RTE_2023: 0.82049; RTE_2024: 0.85444; RTE_2025: 0.86171; EFC_2023: 52.5632; EFC_2024: 177.2868; EFC_2025: 257.0579; UTI_2023: 0.52476; UTI_2024: 0.63384; UTI_2025: 0.88404
65422 | FPL Chipola River Solar Energy Center | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.7489 |  |  |  |  | insufficient_history |  | insufficient_history | 2.2819 | 0.00038031 | 0.99962 | 6000 | 0 | 0 | 1 | 0.7489 | 0 | 74.5 | 74.5 |  |  |  |  | 264.5309 | 14.4667 | 9.0603 | 20.763 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.7489; EFC_2025: 2.2819; UTI_2025: 0.098199
65429 | FPL Shirer Branch Solar Energy Center | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.78501 |  |  |  |  | insufficient_history |  | insufficient_history | 2.4832 | 0.00041387 | 0.99959 | 6000 | 0 | 0 | 1 | 0.78501 | 0 | 74.5 | 74.5 |  |  |  |  | 287.8719 | 15.7431 | 9.8598 | 22.5951 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.78501; EFC_2025: 2.4832; UTI_2025: 0.10686
65433 | Blackwater River Solar Energy Center | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.78165 |  |  |  |  | insufficient_history |  | insufficient_history | 1.906 | 0.00031767 | 0.99968 | 6000 | 0 | 0 | 1 | 0.78165 | 0 | 74.5 | 74.5 |  |  |  |  | 220.9611 | 12.0839 | 7.568 | 17.3432 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.78165; EFC_2025: 1.906; UTI_2025: 0.082025
65441 | USS Itasca Clean Energy Solar LLC | MN | MISO | USS Itasca Clean Energy Solar LLC | United States Solar Corporation |  |  | TRUE | pv_same_plant | LIB | CS | Backup Power, Excess Wind and Solar Generation | 1 | 3 | 3 | 2.5-4.5h | 2022 | 334 | C | HYBRID_ARTEFACT | 0.7807 | 0.63604 | 0.20507 | -0.0023477 | 2.9957 | 57.0581 | ok | 6.1825 | ok | 86.3333 | 0.014389 | 0.98561 | 6000 | 6 | 2 | 1 | 0.78261 | 4 | 1 | 1 | 0.0020507 | 0.66061 | 33 | 0.11808 | 5.2525 | 0.3372 | 0.015424 | 0.091615 | 0.12376 | 0.14367 | 0.0056108 | 0.12376 | 0.01101 | 0.012925 | 0.00047026 | 0.01101 | RTE_2023: 0.7; RTE_2024: 0.52101; RTE_2025: 0.60959; EFC_2022: 10.3333; EFC_2023: 25.6667; EFC_2024: 20.6667; EFC_2025: 29.6667; UTI_2022: 0.085911; UTI_2023: 0.098363; UTI_2024: 0.072011; UTI_2025: 0.089317 | LOW_ETA_AND_LOW_UTI
65456 | Separator (Etiwanda) BESS | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS | Frequency Regulation | 112.5 | 450 | 4 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 0.83033 | 0.84309 | -0.17261 | -0.13296 |  |  | insufficient_history |  | insufficient_history | 223.2889 | 0.037215 | 0.96279 | 6000 | 2 | 0 | 1 | 0.82643 | 3738.1529 | 112.5 | 112.5 | -0.19419 | 0.84098 | 11 | 0.094359 | 3110.7754 | 567.0729 | 70.1089 | 452.1568 | 0.051638 | 0.16199 | 0.017077 | 0.35714 | 0.0044183 | 0.014728 | 0.0014483 | 0.036819 | RTE_2025: 0.84098; EFC_2025: 223.2889; UTI_2025: 0.83005
65457 | Cathode (Hinson) BESS | CA | CISO | Southern California Edison Co | Southern California Edison Co |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 200 | 800 | 4 | 2.5-4.5h | 2024 | 57 | A | UNATTRIBUTED | 0.84594 | 0.80782 | 0.31586 | 0.43742 |  |  | insufficient_history |  | insufficient_history | 229.0888 | 0.038181 | 0.96182 | 6000 | 0 | 0 | 1 | 0.82783 | 7453.9646 | 200 | 200 | 0.63173 | 0.82707 | 11 | 0.96341 | 5963.4274 | 1087.0918 | 274.3724 | 866.7949 | 0.051638 | 0.16199 | 0.03424 | 0.35714 | 0.0044183 | 0.014728 | 0.0029567 | 0.036819 | RTE_2025: 0.82707; EFC_2025: 229.0888; UTI_2025: 0.92117 | THERMAL_AUX
65468 | Highland Park Borough Solar | NJ | PJM | Public Service Elec & Gas Co | Public Service Elec & Gas Co |  |  | TRUE | colocated_firming,pv_same_plant | LIB | BL | Arbitrage, Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving | 0.6 | 2.1 | 3.5 | 2.5-4.5h | 2019 |  |  | HYBRID_ARTEFACT |  | 0.62578 |  |  |  |  | insufficient_history |  | insufficient_history | 91.9048 | 0.015317 | 0.98468 | 6000 | 0 | 0 | 1 | 0.86364 | 0 | 0.5 | 0.5 |  |  |  |  | 14.0036 | 0.76583 | 0.35064 | 0.36268 | 0.18053 | 0.18053 | 0.067514 | 0.25593 | 0.016591 | 0.016591 | 0.0060424 | 0.024635 | RTE_2025: 0.73384; EFC_2025: 91.9048; UTI_2025: 0.23068
65469 | Sealed Air Madera Solar Project | CA | CISO | Sealed Air Corporation | Sealed Air Corporation |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 0.8 | 3.1 | 3.875 | 2.5-4.5h | 2022 | 274 | C | HYBRID_ARTEFACT | 1.1201 | 0.86616 | 1.9594 | -0.002662 | 9.3463 | 218.9901 | ok | 1.0821 | ok | 589.0323 | 0.098172 | 0.90183 | 6000 | 0 | 2 | 1 | 0.87912 | 20.5 | 0.8 | 0.8 | 0.015675 | 0.87608 | 36 | 0.55245 | 9.9571 | 3.9932 | 2.6966 | 1.3315 | 0.03025 | 0.20169 | 0.1077 | 0.20982 | 0.0025597 | 0.018771 | 0.010083 | 0.019625 | RTE_2022: 0.66667; RTE_2023: 0.88652; RTE_2024: 0.88636; RTE_2025: 0.85438; EFC_2022: 0.64516; EFC_2023: 201.6129; EFC_2024: 201.2903; EFC_2025: 185.4839; UTI_2022: 0.023146; UTI_2023: 0.75171; UTI_2024: 0.75492; UTI_2025: 0.69427 | PARTIAL_AVAILABILITY
65472 | Chukar Battery Energy Storage System | NV | NEVP | Nevada Power Co | Nevada Power Co |  |  | FALSE |  | LIB | CS | System Peak Shaving | 10 | 40 | 4 | 2.5-4.5h | 2021 | 61 | A | THERMAL_AUX | 0.93037 | 0.83531 | 1.5973 | 0.013242 | 2.3594 | 37.0681 | ok | -0.19596 | ok | 1329.5625 | 0.22159 | 0.77841 | 6000 | 0 | 5 | 1 | 0.86076 | 2129.6654 | 10 | 10 | 0.15973 | 0.8357 | 24 | 0.18409 | 515.194 | 46.9582 | 64.4146 | 0.11502 | 0.08949 | 0.14465 | 0.14524 | 0.0011993 | 0.0078125 | 0.013021 | 0.014207 | 0.0001 | RTE_2024: 0.84281; RTE_2025: 0.82796; EFC_2024: 301.875; EFC_2025: 273; UTI_2024: 1.1395; UTI_2025: 0.92816 | THERMAL_AUX
65489 | Dickens | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 200 | 200 | 1 | <1.5h | 2024 | 22 | B | FULL_OUTAGE | 0.9098 | 0.92555 | -0.13399 | 0.02707 |  |  | insufficient_history |  | insufficient_history | 600.24 | 0.10004 | 0.89996 | 6000 | 0 | 2 | 1 | 0.91615 | 6616.1616 | 200 | 200 | -0.26798 | 0.92503 | 11 | 0.011665 | 7575.0157 | 355.0817 | 72.9811 | 679.5003 | 0.11369 | 0.098277 | 0.016625 | 0.46243 | 0.010057 | 0.0086207 | 0.0014094 | 0.051724 | RTE_2024: 0.98036; RTE_2025: 0.92006; EFC_2024: 52.42; EFC_2025: 547.82; UTI_2024: 2.8358; UTI_2025: 2.8684 | FULL_OUTAGE
65490 | Hydra | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 200 | 200 | 1 | <1.5h | 2024 | 23 | B | FULL_OUTAGE | 0.93013 | 0.88779 | 0.36612 | 0.22234 |  |  | insufficient_history |  | insufficient_history | 923.46 | 0.15391 | 0.84609 | 6000 | 0 | 2 | 1 | 0.87635 | 6616.1616 | 200 | 200 | 0.73225 | 0.89204 | 11 | 0.2638 | 6465.1895 | 303.0582 | 62.2885 | 579.9458 | 0.11369 | 0.098277 | 0.016625 | 0.46243 | 0.010057 | 0.0086207 | 0.0014094 | 0.051724 | RTE_2024: 0.98581; RTE_2025: 0.8773; EFC_2024: 138.645; EFC_2025: 784.815; UTI_2024: 7.5005; UTI_2025: 2.4111 | FULL_OUTAGE
65491 | Paleo | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 200 | 200 | 1 | <1.5h | 2024 | 9 | A | UNATTRIBUTED | 0.98965 | 0.84096 | 1.0362 | 0.27959 |  |  | insufficient_history |  | insufficient_history | 532.765 | 0.088794 | 0.91121 | 6000 | 0 | 2 | 1 | 0.98549 | 12502.8421 | 200 | 200 | 2.0723 | 0.86124 | 11 | 0.65066 | 5876.8746 | 275.4807 | 115.5882 | 527.1723 | 0.11369 | 0.098277 | 0.033351 | 0.46243 | 0.010057 | 0.0086207 | 0.0028772 | 0.051724 | RTE_2024: 0.98549; RTE_2025: 0.82685; EFC_2024: 132.125; EFC_2025: 400.64; UTI_2024: 7.1477; UTI_2025: 1.9873 | ELEVATED_P_AUX
65492 | Pavo | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 175 | 175 | 1 | <1.5h | 2024 |  |  | HEALTHY | 0.95828 | 0.94767 | 0.085082 | 0.60054 |  |  | insufficient_history |  | insufficient_history | 1028.3543 | 0.17139 | 0.82861 | 6000 | 0 | 0 | 1 | 0.92278 | 0 | 175 | 175 | 0.14889 | 0.93806 | 13 | 0.02763 | 6554.8762 | 307.2623 | 63.1526 | 587.9909 | 0.11369 | 0.098277 | 0.016625 | 0.46243 | 0.010057 | 0.0086207 | 0.0014094 | 0.051724 | RTE_2024: 0.98045; RTE_2025: 0.936; EFC_2024: 49.8514; EFC_2025: 978.5029; UTI_2024: 2.6969; UTI_2025: 2.8599
65493 | Tortolas | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 50 | 50 | 1 | <1.5h | 2024 |  |  | HEALTHY | 0.94856 | 0.87924 | 0.57376 | -0.018807 |  |  | insufficient_history |  | insufficient_history | 509.7 | 0.08495 | 0.91505 | 6000 | 0 | 0 | 1 | 0.88633 | 0 | 50 | 50 | 0.28688 | 0.87958 | 10 | 0.43069 | 1915.5297 | 89.7912 | 18.5367 | 171.8284 | 0.11369 | 0.098277 | 0.016698 | 0.46243 | 0.010057 | 0.0086207 | 0.0014156 | 0.051724 | RTE_2025: 0.87958; EFC_2025: 509.7; UTI_2025: 2.8158
65499 | Danville BESS 1 | VA | PJM | Doc Brown LLC | Doc Brown LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 10.5 | 24.6 | 2.3429 | 1.5-2.5h | 2022 |  |  | CAPACITY_FADE | 0.8863 | 0.8252 | 0.35639 | 0.011007 | -0.1557 | 10.7661 | ok | -3.2414 | ok | 1504.4309 | 0.25074 | 0.74926 | 6000 | 0 | 0 | 1 | 0.86856 | 144.6535 | 10.5 | 10.5 | 0.03742 | 0.86774 | 33 | 0.97605 | 1411.3337 | 37.9789 | 14.0015 | 23.0538 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | RTE_2022: 0.53807; RTE_2023: 0.85809; RTE_2024: 0.87097; RTE_2025: 0.86336; EFC_2022: 4.3089; EFC_2023: 371.9106; EFC_2024: 644.3089; EFC_2025: 483.9024; UTI_2022: 0.11218; UTI_2023: 1.6955; UTI_2024: 2.8696; UTI_2025: 2.124
65530 | Portage Industrial Battery | WI | MISO | Wisconsin Power & Light Co | Wisconsin Power & Light Co |  |  | FALSE |  | LIB | CS |  | 5 | 10 | 2 | 1.5-2.5h | 2022 |  |  | UNATTRIBUTED | 0.88173 | 0.75196 | 0.66634 | -0.0061483 | -5.3216 | -23.3216 | ok | -0.06736 | ok | 528.875 | 0.088146 | 0.91185 | 6000 | 0 | 0 | 1 | 0.77824 | 1294.04 | 5 | 5 | 0.033317 | 0.75719 | 24 | 0.66139 | 172.7157 | 4.6478 | 1.767 | 2.8213 | 0.18267 | 0.094486 | 0.029123 | 0.17213 | 0.016809 | 0.0082711 | 0.0025013 | 0.015742 | RTE_2024: 0.7526; RTE_2025: 0.76157; EFC_2024: 152.1; EFC_2025: 161.3; UTI_2024: 0.63945; UTI_2025: 0.64613
65531 | Deer Run Battery | IA | MISO | Interstate Power and Light Co | Interstate Power and Light Co |  |  | FALSE |  | LIB | CS |  | 5 | 10 | 2 | 1.5-2.5h | 2023 | 201 | A | UNATTRIBUTED | 0.77427 | 0.74313 | 0.17111 | -0.0043369 | -17.3698 | -200.5584 | ok | -0.45407 | ok | 430 | 0.071667 | 0.92833 | 6000 | 0 | 0 | 1 | 0.74408 | 289.7642 | 1 | 1 | 0.0085555 | 0.74536 | 24 | 0.12094 | 149.8925 | 4.0336 | 1.5335 | 2.4485 | 0.18267 | 0.094486 | 0.029123 | 0.17213 | 0.016809 | 0.0082711 | 0.0025013 | 0.015742 | RTE_2024: 0.73553; RTE_2025: 0.7558; EFC_2024: 144.9; EFC_2025: 140.2; UTI_2024: 0.59787; UTI_2025: 0.56154 | LOW_ETA_AND_LOW_UTI
65562 | Amazon Bakersfield 1 Solar Project | CA | CISO | Solar Star Prime 3, LLC | Solar Star Prime 3, LLC |  |  | TRUE | pv_same_plant | MAB | BL | Excess Wind and Solar Generation | 1.6 | 5.9 | 3.6875 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.8696 | 0.79709 | 0.13763 | 0.0033253 | -0.23984 | -30.5925 | ok | 1.0928 | ok | 307.2881 | 0.051215 | 0.94879 | 6000 | 1 | 0 | 1 | 0.88636 | 0 | 1.4 | 1.4 | 0.0022021 | 0.85863 | 22 | 0.17462 | 27.5634 | 5.0246 | 0.60926 | 4.0064 | 0.051638 | 0.16199 | 0.016754 | 0.35714 | 0.0044183 | 0.014728 | 0.0014205 | 0.036819 | RTE_2024: 0.84676; RTE_2025: 0.86063; EFC_2024: 146.1017; EFC_2025: 161.1864; UTI_2024: 0.44699; UTI_2025: 0.6199
65568 | Google Moffett Park Solar Project | CA | CISO | Google, Inc. | Google, Inc. |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, System Peak Shaving | 0.6 | 1.1 | 1.8333 | 1.5-2.5h | 2021 | 288 | C | HYBRID_ARTEFACT | 0.89537 | 0.89218 | 0.029605 | -0.00060686 | 3.8783 | 177.5847 | ok | 0.054229 | ok | 992.7273 | 0.16545 | 0.83455 | 6000 | 0 | 4 | 1 | 0.86486 | 27 | 0.6 | 0.6 | 0.00017763 | 0.8912 | 36 | 0.010751 | 15.1106 | 1.6527 | 1.0582 | 0.39534 | 0.095923 | 0.18264 | 0.092976 | 0.14038 | 0.0084034 | 0.016807 | 0.0085598 | 0.012605 | RTE_2022: 0.89252; RTE_2023: 0.89802; RTE_2024: 0.89181; RTE_2025: 0.88291; EFC_2022: 173.6364; EFC_2023: 288.1818; EFC_2024: 277.2727; EFC_2025: 253.6364; UTI_2022: 0.64424; UTI_2023: 0.95836; UTI_2024: 0.89961; UTI_2025: 0.81021 | PARTIAL_AVAILABILITY
65569 | Gilead Sciences La Verne Rooftop Solar | CA | CISO | Gilead Sciences, Inc. - La Verne | Gilead Sciences, Inc. - La Verne |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 1.1 | 2.1 | 1.9091 | 1.5-2.5h | 2021 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.1 | 1.1
65588 | Antlia | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 70 | 140 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.86297 |  |  |  |  | insufficient_history |  | insufficient_history | 145.9429 | 0.024324 | 0.97568 | 6000 | 1 | 0 | 1 | 0.88597 | 0 | 70 | 70 |  |  |  |  | 583.4018 | 127.6202 | 297.4194 | 284.923 | 0.022471 | 0.086899 | 0.14381 | 0.47079 | 0.0018939 | 0.0075758 | 0.014044 | 0.05303 | RTE_2025: 0.86247; EFC_2025: 145.9429; UTI_2025: 1.1896
65589 | Carina | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 150 | 300 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.87442 |  |  |  |  | insufficient_history |  | insufficient_history | 112.76 | 0.018793 | 0.98121 | 6000 | 0 | 0 | 1 | 0.89646 | 0 | 150 | 150 |  |  |  |  | 1120.4456 | 245.0994 | 579.6837 | 547.2055 | 0.022471 | 0.086899 | 0.14563 | 0.47079 | 0.0018939 | 0.0075758 | 0.014252 | 0.05303 | RTE_2025: 0.8768; EFC_2025: 112.76; UTI_2025: 1.1483
65591 | AVEP BESS | CA | CISO | Leeward Asset Management, LLC | Leeward Asset Management, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Management | 126 | 504 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.82952 |  |  |  |  | insufficient_history |  | insufficient_history | 160.2639 | 0.026711 | 0.97329 | 6000 | 0 | 0 | 1 | 0.85723 | 27892.853 | 126 | 126 |  |  |  |  | 3432.781 | 625.7723 | 77.6002 | 498.9609 | 0.051638 | 0.16199 | 0.017128 | 0.35714 | 0.0044183 | 0.014728 | 0.0014527 | 0.036819 | RTE_2025: 0.82428; EFC_2025: 160.2639; UTI_2025: 0.83331
65614 | Orange Coast College PH2 Solar Project | CA | CISO | Solar Star Coastal Pirate, LLC | Solar Star Coastal Pirate, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 2.1 | 4 | 1.9048 | 1.5-2.5h | 2022 | 388 | C | HYBRID_ARTEFACT | 0.51731 | 0.85881 | -3.932 | 0.0054448 | 13.1996 | 205.7822 | ok | -1.2835 | ok | 505 | 0.084167 | 0.91583 | 6000 | 0 | 2 | 1 | 0.85542 | 38 | 2 | 2 | -0.082572 | 1.149 | 36 | 0.40805 | 29.2741 | 8.8052 | 0.90922 | 0.0089611 | 0.066091 | 0.31344 | 0.029945 | 0.0011993 | 0.005698 | 0.031339 | 0.0025741 | 0.0001 | RTE_2023: 43.25; RTE_2024: 0.85696; RTE_2025: 0.86189; EFC_2023: 129.75; EFC_2024: 167.75; EFC_2025: 207.5; UTI_2023: 0.40088; UTI_2024: 0.50881; UTI_2025: 0.64005 | LOW_ETA_AND_LOW_UTI
65633 | Boaz Microgrid Battery | WI | MISO | Wisconsin Power & Light Co | Wisconsin Power & Light Co |  |  | FALSE |  | LIB | CS |  | 3.6 | 3 | 0.83333 | <1.5h | 2023 |  |  | UNDER_DISPATCH |  | 0.34706 |  |  |  |  | insufficient_history |  | insufficient_history | 30.6667 | 0.0051111 | 0.99489 | 6000 | 0 | 0 | 1 | 0.52174 | 2880.3501 | 1 | 1 |  |  |  |  | 0.88999 | 0.039748 | 0.023639 | 0.027166 | 0.13542 | 0.11205 | 0.053167 | 0.22481 | 0.012126 | 0.009903 | 0.0046847 | 0.021221 | RTE_2023: 0.34831; RTE_2024: 0.28788; RTE_2025: 0.17164; EFC_2023: 10.3333; EFC_2024: 12.6667; EFC_2025: 7.6667; UTI_2023: 0.058204; UTI_2024: 0.011156; UTI_2025: 0.010648
65635 | Hecate Energy Desert Storage 1 LLC | CA | CISO | Hecate Energy Desert Storage 1 LLC | Hecate Energy Desert Storage 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 10 | 20 | 2 | 1.5-2.5h | 2025 |  |  | UNATTRIBUTED |  | 0.78637 |  |  |  |  | insufficient_history |  | insufficient_history | 206.7 | 0.03445 | 0.96555 | 6000 | 1 | 0 | 1 | 0.79005 | 30.4027 | 10 | 10 |  |  |  |  | 2371.5134 | 0.23561 | 0.29621 | 27.5763 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.78893; EFC_2025: 206.7; UTI_2025: 1.016
65644 | Lumina II Solar Project | TX | ERCO | Intersect USA, LLC | Intersect USA, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 160 | 320 | 2 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.84179 |  |  |  |  | insufficient_history |  | insufficient_history | 74.225 | 0.012371 | 0.98763 | 6000 | 0 | 0 | 1 | 0.84775 | 0 | 160 | 160 |  |  |  |  | 1005.8364 | 220.0285 | 528.2288 | 491.2325 | 0.022471 | 0.086899 | 0.14749 | 0.47079 | 0.0018939 | 0.0075758 | 0.014467 | 0.05303 | RTE_2025: 0.84224; EFC_2025: 74.225; UTI_2025: 1.0034
65645 | Lumina Solar Project | TX | ERCO | Intersect USA, LLC | Intersect USA, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 160 | 320 | 2 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.83476 |  |  |  |  | insufficient_history |  | insufficient_history | 108.625 | 0.018104 | 0.9819 | 6000 | 0 | 0 | 1 | 0.84283 | 0 | 160 | 160 |  |  |  |  | 1212.5361 | 265.2444 | 627.3284 | 592.1809 | 0.022471 | 0.086899 | 0.14563 | 0.47079 | 0.0018939 | 0.0075758 | 0.014252 | 0.05303 | RTE_2025: 0.83602; EFC_2025: 108.625; UTI_2025: 1.089
65650 | Brockelman Road Solar 2 | MA | ISNE | Brockelman Road Solar 2, LLC | Brockelman Road Solar 2, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CT | Co-Located Renewable Firming | 2 | 1.7 | 0.85 | <1.5h | 2021 | 303 | C | HYBRID_ARTEFACT | 0.92922 | 0.90533 | 0.053857 | -2.4252e-05 | 8.7138 | 124.8994 | ok |  | insufficient_history | 457.6471 | 0.076275 | 0.92373 | 6000 | 0 | 2 | 1 | 0.90476 | 3.5 | 1 | 1 | 0.0010771 | 0.90676 | 24 | 0.13025 | 7.6452 | 2.0905 | 0.013877 | 1.4669 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 | RTE_2024: 0.90154; RTE_2025: 0.91471; EFC_2024: 274.7059; EFC_2025: 182.9412; UTI_2024: 0.48246; UTI_2025: 0.39428 | PARTIAL_AVAILABILITY
65656 | Ortega Grid, LLC | CA | CISO | Ortega Grid, LLC | Ortega Grid, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 20 | 40 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.7988 |  |  |  |  | insufficient_history |  | insufficient_history | 182.7 | 0.03045 | 0.96955 | 6000 | 1 | 0 | 1 | 0.84271 | 0 | 20 | 20 |  |  |  |  | 4781.4073 | 0.47503 | 0.5972 | 55.5989 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.8007; EFC_2025: 182.7; UTI_2025: 1.0663
65657 | San Jacinto Grid, LLC | CA | CISO | San Jacinto Grid, LLC | San Jacinto Grid, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 65 | 40 | 0.61538 | <1.5h | 2025 |  |  | UNATTRIBUTED |  | 0.79631 |  |  |  |  | insufficient_history |  | insufficient_history | 232.625 | 0.038771 | 0.96123 | 6000 | 0 | 0 | 1 | 0.79901 | 251.6527 | 20 | 20 |  |  |  |  | 3628.6175 | 99.2208 | 1.5592 | 174.0506 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.79639; EFC_2025: 232.625; UTI_2025: 1.3278
65664 | Sandrini Solar 100 | CA | CISO | EDPR CA Solar Park II LLC | EDPR CA Solar Park II LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, Transmission and Distribution Deferral, System Peak Shaving, Load Management, Voltage or Reactive Power Support, Backup Power | 95.4 | 368 | 3.8574 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 92 | 92
65669 | Faunce Corner Community Solar | MA | ISNE | Faunce Corner Road Dartmouth Solar 1, LLC | Faunce Corner Road Dartmouth Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 1 | 3.9 | 3.9 | 2.5-4.5h | 2022 | 369 | C | HYBRID_ARTEFACT | 0.76918 | 0.61269 | 0.29527 | -0.0016874 | 12.0474 | 67.9477 | ok | -0.25713 | ok | 266.9231 | 0.044487 | 0.95551 | 6000 | 0 | 0 | 1 | 0.83333 | 0 | 1 | 1 | 0.0029527 | 0.75018 | 29 | 0.71403 | 58.7155 | 3.211 | 0.020184 | 0.7681 | 0.21337 | 0.21337 | 0.0011985 | 0.16473 | 0.02 | 0.02 | 0.0001 | 0.015 | RTE_2023: 0.32692; RTE_2024: 0.73669; RTE_2025: 0.76744; EFC_2023: 8.7179; EFC_2024: 131.2821; EFC_2025: 126.9231; UTI_2023: 0.025198; UTI_2024: 0.49896; UTI_2025: 0.6167 | LOW_ETA_AND_LOW_UTI
65670 | Ventura | MA | ISNE | Ventura Drive Dartmouth Solar 1, LLC | Ventura Drive Dartmouth Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 1 | 5 | 5 | >4.5h | 2022 | 233 | C | HYBRID_ARTEFACT | 0.77168 | 0.77371 | 0.051479 | -0.0013079 | -7.9832 | -1.5545 | ok | -0.39749 | ok | 249 | 0.0415 | 0.9585 | 6000 | 0 | 2 | 1 | 0.95833 | 53 | 1 | 1 | 0.00051479 | 0.7791 | 30 | 0.15821 | 24.4648 | 1.4717 | 0.013877 | 0.34138 | 0.13537 | 0.14786 | 0.0011985 | 0.10985 | 0.012121 | 0.013333 | 0.0001 | 0.009697 | RTE_2023: 0.89507; RTE_2024: 0.69355; RTE_2025: 0.7086; EFC_2023: 112.6; EFC_2024: 68.8; EFC_2025: 67.6; UTI_2023: 5.3128; UTI_2024: 0.80645; UTI_2025: 0.81056 | LOW_ETA_AND_LOW_UTI
65672 | Sanborn BESS 3 | CA | CISO | EdSan 1B Group 3, LLC | Terra-Gen Operating Co-BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation | 169 | 676 | 4 | 2.5-4.5h | 2023 | 11 | A | PARTIAL_AVAILABILITY | 0.87625 | 0.87156 | 0.095771 | 0.17656 | 5.3859 | 81.795 | ok | -0.45163 | ok | 710.4911 | 0.11842 | 0.88158 | 6000 | 1 | 3 | 1 | 0.92584 | 10837.1258 | 169 | 169 | 0.16185 | 0.87217 | 26 | 0.0077954 | 3510.0605 | 1407.6917 | 2168.3307 | 469.3781 | 0.03025 | 0.20169 | 0.21541 | 0.20982 | 0.0025597 | 0.018771 | 0.022999 | 0.019625 | RTE_2023: 0.86151; RTE_2024: 0.87395; RTE_2025: 0.87135; EFC_2023: 31.8299; EFC_2024: 348.7352; EFC_2025: 329.926; UTI_2023: 0.67913; UTI_2024: 1.3115; UTI_2025: 1.1475 | PARTIAL_AVAILABILITY
65673 | Sanborn BESS 4 | CA | CISO | EdSan 1B Group 2, LLC | Terra-Gen Operating Co-BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation | 47 | 188 | 4 | 2.5-4.5h | 2023 | 24 | A | UNATTRIBUTED | 0.95292 | 0.87047 | 1.3487 | 0.18005 |  |  | ok | -0.011759 | ok | 675.0319 | 0.11251 | 0.88749 | 6000 | 1 | 0 | 1 | 0.87398 | 6319.5133 | 47 | 47 | 0.6339 | 0.87258 | 26 | 0.14481 | 958.1346 | 384.255 | 893.8374 | 128.1253 | 0.03025 | 0.20169 | 0.2926 | 0.20982 | 0.0025597 | 0.018771 | 0.034732 | 0.019625 | RTE_2023: 0.87126; RTE_2024: 0.88429; RTE_2025: 0.86233; EFC_2023: 38.5904; EFC_2024: 303.3351; EFC_2025: 333.1064; UTI_2023: 0.83613; UTI_2024: 1.2054; UTI_2025: 1.0729 | ELEVATED_P_AUX
65674 | Edwards Sanborn E1B | CA | CISO | EdSan 1B Group 1 Sanborn, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation | 136 | 136 | 1 | <1.5h | 2023 | 438 | C | HYBRID_ARTEFACT | 0.94939 | 0.85349 | 0.98147 | 0.44256 | 1.9858 | 9.2546 | ok | -0.5964 | ok | 1617.0441 | 0.26951 | 0.73049 | 6000 | 1 | 2 | 1 | 0.87639 | 0 | 136 | 136 | 1.3348 | 0.85548 | 26 | 0.42981 | 8207.8987 | 673.3096 | 241.6439 | 35.791 | 0.13809 | 0.19981 | 0.059755 | 0.03647 | 0.012384 | 0.018576 | 0.0053028 | 0.003096 | RTE_2023: 0.82752; RTE_2024: 0.85331; RTE_2025: 0.86076; EFC_2023: 83.6765; EFC_2024: 757.4412; EFC_2025: 775.9265; UTI_2023: 0.9803; UTI_2024: 0.88005; UTI_2025: 0.94797 | PARTIAL_AVAILABILITY
65675 | Edwards Sanborn E4 | CA | CISO | EdSan 1B Group 1 Sanborn, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Frequency Regulation | 100 | 100 | 1 | <1.5h | 2023 | 399 | C | HYBRID_ARTEFACT | 1.0514 | 0.83358 | 0.85621 | 0.11503 | 11.7913 | 148.229 | ok | 0.00057345 | ok | 635.08 | 0.10585 | 0.89415 | 6000 | 1 | 2 | 1 | 0.64445 | 0 | 100 | 100 | 0.85621 | 0.82621 | 26 | 0.097362 | 2218.1913 | 181.9625 | 65.3045 | 9.6725 | 0.13809 | 0.19981 | 0.059755 | 0.03647 | 0.012384 | 0.018576 | 0.0053028 | 0.003096 | RTE_2023: 0.80729; RTE_2024: 0.79582; RTE_2025: 0.86157; EFC_2023: 40.51; EFC_2024: 296.07; EFC_2025: 298.5; UTI_2023: 0.47843; UTI_2024: 0.36037; UTI_2025: 0.37068 | PARTIAL_AVAILABILITY
65676 | Edwards Sanborn E5 | CA | CISO | EdSan 1B Group 1 Sanborn, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation | 47 | 188 | 4 | 2.5-4.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 47 | 47
65677 | Edwards Sanborn S4 | CA | CISO | EdSan 1B Group 1 Sanborn, LLC | Terra-Gen Operating Co-Hybrid |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Frequency Regulation | 18.8 | 18.8 | 1 | <1.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.92792 | 0.90896 | 0.076706 | 0.0048232 | 1.0708 | -2.7472 | ok | 0.089983 | ok | 753.1383 | 0.12552 | 0.87448 | 6000 | 1 | 0 | 1 | 0.91563 | 0 | 18.8 | 18.8 | 0.014421 | 0.90967 | 30 | 0.036061 | 498.5363 | 40.8959 | 14.3599 | 2.1739 | 0.13809 | 0.19981 | 0.05854 | 0.03647 | 0.012384 | 0.018576 | 0.0051882 | 0.003096 | RTE_2023: 0.92798; RTE_2024: 0.88772; RTE_2025: 0.92278; EFC_2023: 143.9362; EFC_2024: 295.2128; EFC_2025: 313.9894; UTI_2023: 0.42011; UTI_2024: 0.35296; UTI_2025: 0.42058
65692 | NY6 Battery | NY | NYIS | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 20 | 42 | 2.1 | 1.5-2.5h | 2023 | 205 | B | PARTIAL_AVAILABILITY | 0.90135 | 0.86174 | 0.81142 | 0.0057087 | 0.083518 | 18.583 | ok | 0.097165 | ok | 1841.9524 | 0.30699 | 0.69301 | 6000 | 0 | 2 | 1 | 0.87643 | 94.5 | 20 | 20 | 0.16228 | 0.86303 | 24 | 0.66094 | 2842.4064 | 76.489 | 29.0804 | 46.4301 | 0.18267 | 0.094486 | 0.029123 | 0.17213 | 0.016809 | 0.0082711 | 0.0025013 | 0.015742 | RTE_2024: 0.86645; RTE_2025: 0.85952; EFC_2024: 699.4286; EFC_2025: 676.2381; UTI_2024: 3.3458; UTI_2025: 2.3818 | PARTIAL_AVAILABILITY
65693 | TX10 Hummingbird Storage | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | TRUE | dc_coupled | LIB | CS | Voltage or Reactive Power Support | 100 | 227 | 2.27 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.87929 | 0.81243 | 0.53806 | 0.12043 |  |  | insufficient_history |  | insufficient_history | 366.0396 | 0.061007 | 0.93899 | 6000 | 0 | 0 | 1 | 0.85571 | 0 | 100 | 100 | 0.53806 | 0.82997 | 15 | 0.94515 | 803.0289 | 175.664 | 357.15 | 392.1849 | 0.022471 | 0.086899 | 0.12785 | 0.47079 | 0.0018939 | 0.0075758 | 0.012252 | 0.05303 | RTE_2024: 0.82172; RTE_2025: 0.83138; EFC_2024: 52.7313; EFC_2025: 313.3084; UTI_2024: 0.80619; UTI_2025: 1.0542
65694 | TX11 Republic Road Storage | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Backup Power | 50 | 50 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.88423 | 0.51616 | 0.74128 | 0.041425 | 4.0929 | 11.1248 | ok | -2.1531 | ok | 380.16 | 0.06336 | 0.93664 | 6000 | 2 | 0 | 1 | 0.80399 | 32756.3289 | 50 | 50 | 0.37064 | 0.63017 | 31 | 0.95796 | 52.4619 | 14.3452 | 24.485 | 53.073 | 0.010638 | 0.052071 | 0.067596 | 0.46223 | 0.00089127 | 0.0044563 | 0.0060502 | 0.051693 | RTE_2022: 0.48372; RTE_2023: 0.40562; RTE_2024: 0.54215; RTE_2025: 0.70509; EFC_2022: 18.72; EFC_2023: 48.82; EFC_2024: 90.94; EFC_2025: 221.68; UTI_2022: 0.35121; UTI_2023: 0.085497; UTI_2024: 0.40038; UTI_2025: 0.91383
65695 | TX12 Silicon Hill Storage | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Backup Power | 100 | 100 | 1 | <1.5h | 2022 | 385 | C | HYBRID_ARTEFACT | 0.58996 | 0.53913 | 0.075363 | 0.46534 | 12.1497 | 37.8778 | ok | -0.14911 | ok | 418.52 | 0.069753 | 0.93025 | 6000 | 3 | 0 | 1 | 0.82096 | 0 | 100 | 100 | 0.075363 | 0.62542 | 34 | 0.10114 | 126.3796 | 34.5572 | 58.9838 | 127.8517 | 0.010638 | 0.052071 | 0.067596 | 0.46223 | 0.00089127 | 0.0044563 | 0.0060502 | 0.051693 | RTE_2022: 1.0499; RTE_2023: 0.41039; RTE_2024: 0.57144; RTE_2025: 0.67896; EFC_2022: 9.25; EFC_2023: 47.49; EFC_2024: 124.22; EFC_2025: 237.56; UTI_2022: 0.14634; UTI_2023: 0.093404; UTI_2024: 0.5037; UTI_2025: 1.0633 | LOW_ETA_AND_LOW_UTI
65696 | TX13 Endurance Park Storage | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Backup Power | 50 | 50 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.89675 | 0.77802 | 0.60047 | 0.1244 | -1.0733 | 0.19078 | ok | -0.10892 | ok | 1101.5 | 0.18358 | 0.81642 | 6000 | 3 | 0 | 1 | 0.85335 | 7860.9036 | 50 | 50 | 0.30023 | 0.80715 | 30 | 0.9674 | 150.2557 | 41.0859 | 74.3431 | 152.0059 | 0.010638 | 0.052071 | 0.071364 | 0.46223 | 0.00089127 | 0.0044563 | 0.0064139 | 0.051693 | RTE_2023: 0.6982; RTE_2024: 0.81209; RTE_2025: 0.8222; EFC_2023: 84.72; EFC_2024: 420.08; EFC_2025: 582.58; UTI_2023: 0.3078; UTI_2024: 1.9939; UTI_2025: 2.4073
65697 | Walnut Grove Demonstration Plant | MS | SOCO | Mississippi Power Co | Mississippi Power Co |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 1.5 | 1.5 | 1 | <1.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.5 | 1.5
65698 | TX15 Limousin Oak Storage | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | TRUE | dc_coupled | LIB | CS | Voltage or Reactive Power Support | 100 | 227 | 2.27 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.90276 | 0.81985 | 0.75482 | 0.14296 |  |  | insufficient_history |  | insufficient_history | 372.7093 | 0.062118 | 0.93788 | 6000 | 0 | 0 | 1 | 0.87341 | 0 | 100 | 100 | 0.75482 | 0.82944 | 15 | 0.73174 | 885.4585 | 193.6956 | 393.8109 | 432.4421 | 0.022471 | 0.086899 | 0.12785 | 0.47079 | 0.0018939 | 0.0075758 | 0.012252 | 0.05303 | RTE_2024: 0.80852; RTE_2025: 0.83265; EFC_2024: 48.3084; EFC_2025: 324.4009; UTI_2024: 0.70496; UTI_2025: 1.1899
65699 | TX19 River Valley Storage 1 | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 50 | 111 | 2.22 | 1.5-2.5h | 2023 | 67 | A | THERMAL_AUX | 0.82307 | 0.71118 | 0.40757 | -0.17189 | 7.9602 | 52.4238 | ok | -12.4177 | ok | 447.1441 | 0.074524 | 0.92548 | 6000 | 3 | 0 | 1 | 0.8521 | 2218.3354 | 50 | 50 | 0.20379 | 0.79485 | 30 | 0.69596 | 617.8183 | 101.3616 | 305.1027 | 172.4179 | 0.031828 | 0.092476 | 0.18785 | 0.404 | 0.0026954 | 0.0080863 | 0.019361 | 0.043127 | RTE_2023: 0.55928; RTE_2024: 0.73481; RTE_2025: 0.83394; EFC_2023: 15.045; EFC_2024: 108.2162; EFC_2025: 323.8829; UTI_2023: 0.10878; UTI_2024: 0.45538; UTI_2025: 1.1644 | THERMAL_AUX
65700 | TX21 River Valley Storage 2 | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 50 | 107 | 2.14 | 1.5-2.5h | 2023 | 46 | A | THERMAL_AUX | 0.83567 | 0.72038 | 0.3769 | -0.1466 | 11.3861 | 74.3987 | ok | -12.5265 | ok | 475.3645 | 0.079227 | 0.92077 | 6000 | 3 | 2 | 1 | 0.85072 | 3476.1446 | 50 | 50 | 0.18845 | 0.80294 | 29 | 0.66065 | 601.4975 | 98.684 | 448.5803 | 167.8632 | 0.031828 | 0.092476 | 0.25848 | 0.404 | 0.0026954 | 0.0080863 | 0.029238 | 0.043127 | RTE_2023: 0.58794; RTE_2024: 0.74521; RTE_2025: 0.83657; EFC_2023: 15.4019; EFC_2024: 121.8879; EFC_2025: 338.0748; UTI_2023: 0.094135; UTI_2024: 0.44471; UTI_2025: 1.2254 | THERMAL_AUX
65701 | TX23 Roughneck Storage | TX | ERCO | Key Capture Energy | Key Capture Energy |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management, Backup Power | 50 | 50 | 1 | <1.5h | 2022 |  |  | CAPACITY_FADE | 0.87222 | 0.56578 | 0.62599 | 0.020267 | -1.3946 | 5.2597 | ok | -3.5918 | ok | 323.77 | 0.053962 | 0.94604 | 6000 | 2 | 0 | 1 | 0.82447 | 6057.3259 | 50 | 50 | 0.31299 | 0.65027 | 27 | 0.9566 | 52.3311 | 14.3094 | 25.8922 | 52.9407 | 0.010638 | 0.052071 | 0.071364 | 0.46223 | 0.00089127 | 0.0044563 | 0.0064139 | 0.051693 | RTE_2023: 0.35458; RTE_2024: 0.58977; RTE_2025: 0.70533; EFC_2023: 17.58; EFC_2024: 97.36; EFC_2025: 205.9; UTI_2023: 0.076754; UTI_2024: 0.41469; UTI_2025: 0.91162
65711 | Vikings Energy Farm | CA | IID | Vikings Energy Farm, LLC | Vikings Energy Farm, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Load Management, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 150 | 600 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.89164 | 0.88766 | 0.044168 | -0.089139 |  |  | insufficient_history | -4.3111 | ok | 343.3 | 0.057217 | 0.94278 | 6000 | 6 | 0 | 1 | 0.89793 | 0 | 150 | 150 | 0.066252 | 0.88848 | 17 | 0.050887 | 7433.3192 | 406.5129 | 240.4866 | 583.441 | 0.081309 | 0.081309 | 0.038345 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033255 | 0.031802 | RTE_2024: 0.89124; RTE_2025: 0.88785; EFC_2024: 64.6267; EFC_2025: 278.6733; UTI_2024: 0.64779; UTI_2025: 0.99625
65733 | Carris Storage I | CA | CISO | Hecate Grid Carris Storage 1 LLC | Hecate Grid Carris Storage 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 10 | 20 | 2 | 1.5-2.5h | 2025 |  |  | UNATTRIBUTED |  | 0.79029 |  |  |  |  | insufficient_history |  | insufficient_history | 204.4 | 0.034067 | 0.96593 | 6000 | 1 | 0 | 1 | 0.8002 | 24.5999 | 10 | 10 |  |  |  |  | 2375.5534 | 0.23601 | 0.29671 | 27.6233 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.79286; EFC_2025: 204.4; UTI_2025: 0.9892
65734 | Oberon Solar Project | CA | CISO | Intersect USA, LLC | Intersect USA, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Co-Located Renewable Firming | 125 | 500 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.93729 | 0.89182 | 0.63184 | 0.1507 | 4.7709 | 114.4222 | ok | -3.3532 | ok | 717.174 | 0.11953 | 0.88047 | 6000 | 3 | 0 | 1 | 0.92365 | 0 | 125 | 125 | 0.7898 | 0.89895 | 28 | 0.79058 | 2931.9859 | 1175.8579 | 866.8807 | 392.0759 | 0.03025 | 0.20169 | 0.11641 | 0.20982 | 0.0025597 | 0.018771 | 0.011008 | 0.019625 | RTE_2023: 0.86382; RTE_2024: 0.89272; RTE_2025: 0.90941; EFC_2023: 52.952; EFC_2024: 296.8; EFC_2025: 367.422; UTI_2023: 0.63044; UTI_2024: 1.177; UTI_2025: 1.267
65735 | Oberon II Solar Project | CA | CISO | Intersect USA, LLC | Intersect USA, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Co-Located Renewable Firming | 125 | 500 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.93835 | 0.88999 | 0.6509 | 0.12602 | -1.5296 | -149.0146 | ok | -1.6595 | ok | 688.352 | 0.11473 | 0.88527 | 6000 | 3 | 0 | 1 | 0.91486 | 0 | 125 | 125 | 0.81362 | 0.89716 | 28 | 0.74805 | 2742.2377 | 1099.7603 | 810.7791 | 366.7021 | 0.03025 | 0.20169 | 0.11641 | 0.20982 | 0.0025597 | 0.018771 | 0.011008 | 0.019625 | RTE_2023: 0.86112; RTE_2024: 0.8925; RTE_2025: 0.90674; EFC_2023: 52.952; EFC_2024: 284.816; EFC_2025: 350.584; UTI_2023: 0.62511; UTI_2024: 1.1112; UTI_2025: 1.1588
65743 | Victory Pass | CA | CISO | Victory Pass I, LLC | Victory Pass I, LLC |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CT | Frequency Regulation, Excess Wind and Solar Generation | 50 | 200 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.85045 | 0.89551 | -0.49425 | -0.28757 |  |  | insufficient_history | -3.1048 | ok | 472.62 | 0.07877 | 0.92123 | 6000 | 3 | 0 | 1 | 0.82916 | 0 | 50 | 50 | -0.24713 | 0.88312 | 22 | 0.029719 | 1544.2002 | 281.4971 | 34.2343 | 224.4523 | 0.051638 | 0.16199 | 0.016803 | 0.35714 | 0.0044183 | 0.014728 | 0.0014247 | 0.036819 | RTE_2024: 0.96287; RTE_2025: 0.83335; EFC_2024: 198.01; EFC_2025: 274.61; UTI_2024: 0.87547; UTI_2025: 1.0082
65744 | Arica Solar | CA | CISO | Arica Solar, LLC | Arica Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Frequency Regulation, Excess Wind and Solar Generation | 136 | 544 | 4 | 2.5-4.5h | 2024 | 7 | C | HYBRID_ARTEFACT | 0.82595 | 0.86919 | -0.25485 | -2.4207 |  |  | insufficient_history | -0.47575 | ok | 500.8989 | 0.083483 | 0.91652 | 6000 | 3 | 3 | 1 | 0.77082 | 13366 | 136 | 136 | -0.3466 | 0.85104 | 22 | 0.011408 | 4208.286 | 767.1416 | 93.296 | 611.682 | 0.051638 | 0.16199 | 0.016803 | 0.35714 | 0.0044183 | 0.014728 | 0.0014247 | 0.036819 | RTE_2024: 0.89445; RTE_2025: 0.82157; EFC_2024: 212.8934; EFC_2025: 288.0055; UTI_2024: 1.0416; UTI_2025: 0.9769 | PARTIAL_AVAILABILITY
65809 | Caterina | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.93041 | 0.84911 | 0.21804 | -0.0010377 | -4.8961 | -41.7998 | ok | -0.013822 | ok | 671.9192 | 0.11199 | 0.88801 | 6000 | 10 | 0 | 1 | 0.89179 | 3264.194 | 9.9 | 9.9 | 0.021586 | 0.85265 | 36 | 0.45547 | 11.2839 | 3.0855 | 5.3679 | 11.4153 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2022: 0.81204; RTE_2023: 0.87379; RTE_2024: 0.8355; RTE_2025: 0.84575; EFC_2022: 88.5859; EFC_2023: 209.0909; EFC_2024: 162.1212; EFC_2025: 212.1212; UTI_2022: 0.84852; UTI_2023: 0.38968; UTI_2024: 0.7252; UTI_2025: 0.93198
65810 | Cedarville (TX) | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.9257 | 0.84579 | 0.21076 | 0.00041128 | -11.9661 | -255.3337 | ok | 0.24482 | ok | 646.8013 | 0.1078 | 0.8922 | 6000 | 2 | 0 | 1 | 0.8583 | 457.735 | 9.9 | 9.9 | 0.020865 | 0.85074 | 24 | 0.85749 | 12.167 | 3.3269 | 6.2713 | 12.3087 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.83945; RTE_2025: 0.85887; EFC_2024: 161.6162; EFC_2025: 229.2929; UTI_2024: 0.78017; UTI_2025: 1.0172
65811 | Coyote Springs (TX) | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 1.0193 | 0.84961 | 0.40951 | 0.0018343 | -12.5926 | -285.7033 | ok | -1.446 | ok | 641.1364 | 0.10686 | 0.89314 | 6000 | 2 | 0 | 1 | 0.88285 | 431.2679 | 9.9 | 9.9 | 0.040541 | 0.85746 | 24 | 0.9056 | 12.167 | 3.3269 | 6.2713 | 12.3087 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.82387; RTE_2025: 0.88261; EFC_2024: 159.697; EFC_2025: 228.5859; UTI_2024: 0.73765; UTI_2025: 1.0148
65812 | Farmersville (TX) | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | CAPACITY_FADE | 0.95493 | 0.80652 | 0.25175 | -0.00045463 |  |  | insufficient_history | -4.2984 | ok | 231.4141 | 0.038569 | 0.96143 | 6000 | 1 | 0 | 1 | 0.84699 | 60.1942 | 9.9 | 9.9 | 0.024923 | 0.82233 | 21 | 0.9347 | 100.39 | 4.7058 | 0.95598 | 9.0053 | 0.11369 | 0.098277 | 0.016436 | 0.46243 | 0.010057 | 0.0086207 | 0.001393 | 0.051724 | RTE_2024: 0.76857; RTE_2025: 0.84478; EFC_2024: 63.7374; EFC_2025: 167.6768; UTI_2024: 0.41459; UTI_2025: 0.74823
65813 | Faulkner | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.92551 | 0.85588 | 0.16796 | -0.00066438 | -6.1697 | -167.1057 | ok | -0.35055 | ok | 632.8788 | 0.10548 | 0.89452 | 6000 | 2 | 0 | 1 | 0.86555 | 501.735 | 9.9 | 9.9 | 0.016628 | 0.86204 | 24 | 0.88328 | 11.938 | 3.2643 | 6.1533 | 12.0771 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.84824; RTE_2025: 0.87142; EFC_2024: 148.4848; EFC_2025: 224.5455; UTI_2024: 0.66982; UTI_2025: 0.98379
65814 | Gomez | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2023 |  |  | UNATTRIBUTED | 0.93615 | 0.8397 | 0.23889 | -0.00053705 | -5.4337 | -73.9608 | ok | -0.10454 | ok | 468.9899 | 0.078165 | 0.92184 | 6000 | 0 | 0 | 1 | 0.86066 | 478.6159 | 9.9 | 9.9 | 0.02365 | 0.84654 | 24 | 0.88708 | 12.0689 | 3.3001 | 6.2207 | 12.2094 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.82491; RTE_2025: 0.86097; EFC_2024: 145.1515; EFC_2025: 227.0707; UTI_2024: 0.7251; UTI_2025: 0.99727
65815 | NY - Mines Press | NY | NYIS | NY - Mines Press | NY - Mines Press |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Load Following, Co-Located Renewable Firming, Transmission and Distribution Deferral, System Peak Shaving | 1 | 2.1 | 2.1 | 1.5-2.5h | 2022 | 327 | C | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 29.0476 | 0.0048413 | 0.99516 | 6000 | 0 | 2 | 1 | 0.034884 | 0 | 0.6 | 0.6 |  |  |  |  | 2.3214 | 0.076171 | 0.024956 | 0.044539 | 0.17285 | 0.10762 | 0.028802 | 0.1884 | 0.015814 | 0.0094887 | 0.0024728 | 0.017396 | RTE_2024: 0.021605; RTE_2025: 0.026549; EFC_2024: 13.3333; EFC_2025: 15.7143; UTI_2024: 0.047776; UTI_2025: 0.048199 | PARTIAL_AVAILABILITY
65820 | Ocotillo Wells | CA | CISO | Conductive Power | Conductive Power |  |  | TRUE | pv_same_plant | LIB | CS | Voltage or Reactive Power Support | 50 | 200 | 4 | 2.5-4.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 50 | 50
65829 | Holcomb (TX) | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.94324 | 0.81292 | 0.2925 | 0.0007824 | -5.1909 | -46.3082 | ok | -2.1876 | ok | 457.4747 | 0.076246 | 0.92375 | 6000 | 5 | 0 | 1 | 0.83628 | 826.1878 | 9.9 | 9.9 | 0.028957 | 0.82144 | 24 | 0.87057 | 10.4008 | 2.844 | 5.3609 | 10.522 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.79692; RTE_2025: 0.83867; EFC_2024: 130.8081; EFC_2025: 195.8586; UTI_2024: 0.54357; UTI_2025: 0.85952
65830 | Junction (TX) | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.94883 | 0.85162 | 0.21636 | -0.00012424 | -18.2485 | -277.4608 | ok | -1.9523 | ok | 365.303 | 0.060884 | 0.93912 | 6000 | 0 | 0 | 1 | 0.86473 | 630.8337 | 9.9 | 9.9 | 0.02142 | 0.85539 | 24 | 0.63973 | 10.3027 | 2.8172 | 5.3104 | 10.4227 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.84087; RTE_2025: 0.86597; EFC_2024: 137.1717; EFC_2025: 193.8384; UTI_2024: 0.60367; UTI_2025: 0.84838
65831 | Lonestar | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.93843 | 0.86837 | 0.17502 | 0.0012238 | -4.0012 | -82.5727 | ok | -0.44751 | ok | 669.1919 | 0.11153 | 0.88847 | 6000 | 6 | 0 | 1 | 0.90288 | 3572.8291 | 9.9 | 9.9 | 0.017327 | 0.8735 | 36 | 0.67321 | 11.7418 | 3.2107 | 5.5857 | 11.8786 | 0.010638 | 0.052071 | 0.068807 | 0.46223 | 0.00089127 | 0.0044563 | 0.0061668 | 0.051693 | RTE_2022: 0.80935; RTE_2023: 0.87758; RTE_2024: 0.85995; RTE_2025: 0.87867; EFC_2022: 87.4747; EFC_2023: 215.0505; EFC_2024: 145.7576; EFC_2025: 220.9091; UTI_2022: 0.83344; UTI_2023: 0.39901; UTI_2024: 0.61112; UTI_2025: 0.97126
65832 | Olney | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2023 |  |  | UNATTRIBUTED | 0.92372 | 0.7934 | 0.23139 | 0.0028272 | -5.2081 | -72.1088 | ok | -2.9884 | ok | 310.3367 | 0.051723 | 0.94828 | 6000 | 1 | 0 | 1 | 0.82584 | 1352.6493 | 9.9 | 9.9 | 0.022908 | 0.80331 | 24 | 0.87677 | 8.5038 | 2.3253 | 4.3832 | 8.6029 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.7632; RTE_2025: 0.828; EFC_2024: 90.5051; EFC_2025: 159.4949; UTI_2024: 0.40849; UTI_2025: 0.69944
65833 | Rattlesnake (TX) | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 1.005 | 0.84306 | 0.39134 | 0.012667 | -9.4883 | -159.8658 | ok | -1.1618 | ok | 626.3384 | 0.10439 | 0.89561 | 6000 | 3 | 0 | 1 | 0.82114 | 487.6714 | 9.9 | 9.9 | 0.038743 | 0.84875 | 24 | 0.52667 | 11.611 | 3.1749 | 5.9847 | 11.7462 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.81195; RTE_2025: 0.87748; EFC_2024: 157.8788; EFC_2025: 218.4848; UTI_2024: 0.72517; UTI_2025: 0.96072
65834 | Saddleback BESS2 | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2022 |  |  | UNDER_DISPATCH | 0.93469 | 0.81658 | 0.31729 | 0.0023196 | -11.3146 | -153.0926 | ok | -2.1525 | ok | 662.8535 | 0.11048 | 0.88952 | 6000 | 2 | 0 | 1 | 0.8373 | 461.9316 | 9.9 | 9.9 | 0.031411 | 0.82336 | 24 | 0.94162 | 12.167 | 3.3269 | 6.2713 | 12.3087 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.80154; RTE_2025: 0.83914; EFC_2024: 157.8788; EFC_2025: 228.6869; UTI_2024: 0.74415; UTI_2025: 1.0103
65835 | Screwbean | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.91427 | 0.87346 | 0.1047 | -0.0023208 | -6.5913 | -224.6717 | ok | -2.5977 | ok | 547.8788 | 0.091313 | 0.90869 | 6000 | 0 | 0 | 1 | 0.87712 | 450.735 | 9.9 | 9.9 | 0.010366 | 0.87583 | 24 | 0.60855 | 11.938 | 3.2643 | 6.1533 | 12.0771 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.87011; RTE_2025: 0.88; EFC_2024: 161.7172; EFC_2025: 224.4444; UTI_2024: 0.74485; UTI_2025: 0.98313
65836 | Toyah Power Station | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 10.4 | 9.9 | 0.95192 | <1.5h | 2021 |  |  | UNDER_DISPATCH | 0.99762 | 0.95644 | 0.086336 | -0.0056564 |  |  | ok | -1.2081 | ok | 749.4949 | 0.12492 | 0.87508 | 6000 | 2 | 0 | 1 | 0.96444 | 450.735 | 9.9 | 9.9 | 0.008979 | 0.95886 | 24 | 0.24444 | 63.9133 | 12.8161 | 8.0995 | 1.858 | 0.053242 | 0.18177 | 0.091439 | 0.087152 | 0.0045593 | 0.016717 | 0.0084037 | 0.0075988 | RTE_2024: 0.95146; RTE_2025: 0.96392; EFC_2024: 158.3838; EFC_2025: 234.7475; UTI_2024: 0.7424; UTI_2025: 1.049
65837 | Val Verde | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH | 0.92187 | 0.84573 | 0.1161 | 0.002082 | -1.7712 | -49.2525 | ok | -0.73254 | ok | 229.2929 | 0.038215 | 0.96178 | 6000 | 7 | 0 | 1 | 0.83516 | 1558.9081 | 9.9 | 9.9 | 0.011494 | 0.85146 | 24 | 0.84414 | 78.2451 | 3.6678 | 0.74187 | 7.0188 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.83675; RTE_2025: 0.86297; EFC_2024: 98.8889; EFC_2025: 130.404; UTI_2024: 0.45068; UTI_2025: 0.58251
65838 | Hoef's Road Storage | TX | ERCO | Form Energy Inc. | Anatolian Energy, LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 2 | 2 | 1 | <1.5h | 2021 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2 | 2
65857 | Sunlight Storage | CA | CISO | Sunlight Storage, LLC | Sunlight Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 230 | 920 | 4 | 2.5-4.5h | 2022 | 2 | A | CELL_DEGRADATION | 0.93992 | 0.82755 | 1.4699 | 1.4692 | -4.8496 | -49.3562 | ok | 0.20332 | ok | 652.2359 | 0.10871 | 0.89129 | 6000 | 5 | 0 | 1 | 0.84963 | 81894.0973 | 230 | 230 | 3.3807 | 0.83251 | 30 | 0.41515 | 4172.0188 | 1673.1667 | 4973.4283 | 557.8976 | 0.03025 | 0.20169 | 0.34538 | 0.20982 | 0.0025597 | 0.018771 | 0.044382 | 0.019625 | RTE_2023: 0.77064; RTE_2024: 0.84295; RTE_2025: 0.84581; EFC_2023: 88.963; EFC_2024: 234.2837; EFC_2025: 269.6804; UTI_2023: 0.63063; UTI_2024: 0.90955; UTI_2025: 0.96227 | ELEVATED_P_AUX
65860 | Avila | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 160 | 320 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.87659 |  |  |  |  | insufficient_history |  | insufficient_history | 110.7531 | 0.018459 | 0.98154 | 6000 | 0 | 0 | 1 | 0.8805 | 0 | 160 | 160 |  |  |  |  | 1232.9002 | 269.6991 | 637.8642 | 602.1264 | 0.022471 | 0.086899 | 0.14563 | 0.47079 | 0.0018939 | 0.0075758 | 0.014252 | 0.05303 | RTE_2025: 0.87671; EFC_2025: 110.7531; UTI_2025: 1.1138
65861 | Cachi | TX | ERCO | Engie North America | Engie North America |  |  | FALSE |  | LIB | CS | Arbitrage | 200 | 400 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.86563 |  |  |  |  | insufficient_history |  | insufficient_history | 97.435 | 0.016239 | 0.98376 | 6000 | 0 | 0 | 1 | 0.88471 | 3730.7696 | 200 | 200 |  |  |  |  | 1448.8437 | 316.9371 | 749.5866 | 707.5893 | 0.022471 | 0.086899 | 0.14563 | 0.47079 | 0.0018939 | 0.0075758 | 0.014252 | 0.05303 | RTE_2025: 0.86375; EFC_2025: 97.435; UTI_2025: 1.0186
65866 | Canoe | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.77822 |  |  |  |  | insufficient_history |  | insufficient_history | 2.6532 | 0.00044221 | 0.99956 | 6000 | 0 | 0 | 1 | 0.77822 | 0 | 74.5 | 74.5 |  |  |  |  | 307.582 | 16.821 | 10.5348 | 24.1421 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.77822; EFC_2025: 2.6532; UTI_2025: 0.11418
65886 | Tenmile Creek | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 74.5 | 74.5
65888 | Kayak | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.75179 |  |  |  |  | insufficient_history |  | insufficient_history | 2.3445 | 0.00039075 | 0.99961 | 6000 | 0 | 0 | 1 | 0.75179 | 0 | 74.5 | 74.5 |  |  |  |  | 271.7926 | 14.8638 | 9.309 | 21.333 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.75179; EFC_2025: 2.3445; UTI_2025: 0.10089
65927 | Fourmile Creek | FL | FPL | Florida Power & Light Co | Florida Power & Light Co |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 74.5 | 223.5 | 3 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.76397 |  |  |  |  | insufficient_history |  | insufficient_history | 2.4474 | 0.0004079 | 0.99959 | 6000 | 0 | 0 | 1 | 0.76397 | 0 | 74.5 | 74.5 |  |  |  |  | 283.7224 | 15.5162 | 9.7176 | 22.2694 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.76397; EFC_2025: 2.4474; UTI_2025: 0.10532
65933 | Sagebrush ESS | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 80 | 320 | 4 | 2.5-4.5h | 2023 | 27 | A | UNATTRIBUTED | 0.8332 | 0.80079 | 0.46467 | 0.46747 | 6.5875 | -45.0531 | ok | -0.5512 | ok | 557.2719 | 0.092879 | 0.90712 | 6000 | 1 | 0 | 1 | 0.87573 | 13852.8143 | 80 | 80 | 0.37173 | 0.80338 | 32 | 0.084293 | 1308.7931 | 524.8848 | 1525.9971 | 175.0166 | 0.03025 | 0.20169 | 0.34042 | 0.20982 | 0.0025597 | 0.018771 | 0.043409 | 0.019625 | RTE_2023: 0.77857; RTE_2024: 0.74946; RTE_2025: 0.85678; EFC_2023: 136.9969; EFC_2024: 162.6031; EFC_2025: 257.6719; UTI_2023: 0.69155; UTI_2024: 0.60454; UTI_2025: 0.87733 | THERMAL_AUX
65940 | Shasta College PH2 Solar Project | CA | CISO | Shasta College | TotalEnergies Distributed Generation, LLC |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
65945 | Brookville Smart Bus Depot Microgrid | MD | PJM | AlphaStruxure Montgomery County LLC | AlphaStruxure Service Co LP |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Load Management, Backup Power, Excess Wind and Solar Generation | 1.5 | 4.3 | 2.8667 | 2.5-4.5h | 2022 | 174 | C | HYBRID_ARTEFACT | 0.92614 | 0.90988 | 0.05583 | 0.0012633 | -1.9391 | -44.0217 | ok | -0.59568 | ok | 305.1163 | 0.050853 | 0.94915 | 6000 | 0 | 4 | 1 | 0.92929 | 162 | 1.5 | 1.5 | 0.00083745 | 0.91556 | 32 | 0.096521 | 14.6125 | 0.79912 | 0.31788 | 0.37845 | 0.18053 | 0.18053 | 0.05919 | 0.25593 | 0.016591 | 0.016591 | 0.0052496 | 0.024635 | RTE_2023: 0.91519; RTE_2024: 0.92045; RTE_2025: 0.90645; EFC_2023: 107.907; EFC_2024: 131.8605; EFC_2025: 65.3488; UTI_2023: 0.39157; UTI_2024: 0.44651; UTI_2025: 0.12544 | FULL_OUTAGE
65950 | Kearsarge 100 Sohier Rd | MA | ISNE | Kearsarge Beverly LLC | Kearsarge Beverly LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 1.8 | 6.4 | 3.5556 | 2.5-4.5h | 2023 | 185 | C | HYBRID_ARTEFACT | 0.94223 | 0.84405 | 0.48752 | 0.0013123 | -0.065887 | -55.5202 | ok | 0.58908 | ok | 425.1562 | 0.070859 | 0.92914 | 6000 | 0 | 3 | 1 | 0.91209 | 123.5 | 1.7 | 1.7 | 0.0087754 | 0.88505 | 30 | 0.73948 | 176.1465 | 9.6331 | 0.060553 | 2.3043 | 0.21337 | 0.21337 | 0.0011985 | 0.16473 | 0.02 | 0.02 | 0.0001 | 0.015 | RTE_2023: 0.82229; RTE_2024: 0.88213; RTE_2025: 0.89921; EFC_2023: 42.6562; EFC_2024: 185.9375; EFC_2025: 196.5625; UTI_2023: 0.20817; UTI_2024: 0.80974; UTI_2025: 0.94113 | PARTIAL_AVAILABILITY
65951 | Bowling Green Energy Storage Project | OH | PJM | VESI 21 LLC | VESI 21 LLC |  |  | FALSE |  | LIB | CS |  | 12 | 12 | 1 | <1.5h | 2023 | 145 | A | PARTIAL_AVAILABILITY | 0.90494 | 0.90889 | -0.10668 | 0.017499 | -3.1009 | -83.6818 | ok | -0.010027 | ok | 5467.6944 | 0.91128 | 0.088718 | 6000 | 0 | 3 | 1 | 0.91299 | 290 | 12 | 12 | -0.012802 | 0.9088 | 24 | 0.039137 | 1393.4736 | 152.4124 | 77.8 | 0.2625 | 0.10516 | 0.19926 | 0.082624 | 0.0011993 | 0.0092593 | 0.018519 | 0.0075191 | 0.0001 | RTE_2024: 0.90828; RTE_2025: 0.90938; EFC_2024: 2138.1667; EFC_2025: 1904.0833; UTI_2024: 1.0926; UTI_2025: 1.0551 | PARTIAL_AVAILABILITY
65952 | Andover Energy Storage Project | NJ | PJM | VESI 25 LLC | VESI 25 LLC |  |  | FALSE |  | LIB | CS |  | 20 | 20 | 1 | <1.5h | 2023 |  |  | THERMAL_AUX | 0.89744 | 0.89959 | -0.053916 | 0.027322 | 1.0565 | 83.1862 | ok | 0.012981 | ok | 4974.0833 | 0.82901 | 0.17099 | 6000 | 0 | 0 | 1 | 0.89577 | 20.3278 | 20 | 20 | -0.010783 | 0.89946 | 24 | 0.032857 | 2260.9542 | 247.2938 | 257.6988 | 0.42591 | 0.10516 | 0.19926 | 0.15508 | 0.0011993 | 0.0092593 | 0.018519 | 0.01535 | 0.0001 | RTE_2024: 0.89906; RTE_2025: 0.89991; EFC_2024: 2009.8; EFC_2025: 1791.9; UTI_2024: 1.0369; UTI_2025: 0.98486
65953 | Howell Energy Storage Project | NJ | PJM | VESI 24 LLC | VESI 24 LLC |  |  | FALSE |  | LIB | CS |  | 7 | 7 | 1 | <1.5h | 2023 | 179 | B | PARTIAL_AVAILABILITY | 0.89693 | 0.89879 | -0.043764 | 0.001205 | 3.1448 | 197.751 | ok | -0.041409 | ok | 5686.7143 | 0.94779 | 0.052214 | 6000 | 0 | 2 | 1 | 0.89911 | 143 | 7 | 7 | -0.0030635 | 0.8985 | 24 | 0.00083694 | 777.0968 | 84.9956 | 43.3866 | 0.14639 | 0.10516 | 0.19926 | 0.082624 | 0.0011993 | 0.0092593 | 0.018519 | 0.0075191 | 0.0001 | RTE_2024: 0.89749; RTE_2025: 0.89968; EFC_2024: 2113.7143; EFC_2025: 1811.5714; UTI_2024: 1.0623; UTI_2025: 1.0023 | PARTIAL_AVAILABILITY
65956 | Storey Solar and Storage | AZ | SRP | Storey Energy Center, LLC | Storey Energy Center, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation | 88 | 264 | 3 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.84183 | 0.86373 | -0.27809 | 0.33282 | -2.075 | -11.3173 | ok | -0.28943 | ok | 637.0417 | 0.10617 | 0.89383 | 6000 | 6 | 0 | 1 | 0.84855 | 0 | 88 | 88 | -0.24472 | 0.86277 | 26 | 0.057509 | 48.6641 | 845.6598 | 113.5797 | 63.4625 | 0.0011993 | 0.31703 | 0.03911 | 0.085813 | 0.0001 | 0.031776 | 0.0033947 | 0.0074766 | RTE_2023: 0.88916; RTE_2024: 0.86718; RTE_2025: 0.85549; EFC_2023: 36.0985; EFC_2024: 297.178; EFC_2025: 303.7652; UTI_2023: 0.86882; UTI_2024: 0.99611; UTI_2025: 0.94751
65962 | Mesquite Solar 4, LLC | AZ | CISO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | rte_gt_1,pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 10 | 47.7 | 4.77 | >4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.9267 | 0.64453 | 0.34555 | 0.09124 |  |  | ok | 17.3234 | ok | 209.8113 | 0.034969 | 0.96503 | 6000 | 7 | 0 | 1 | 0.87767 | 0 | 10 | 10 | 0.034555 | 0.86128 | 18 | 0.7153 | 5.589 | 34.4718 | 0.38426 | 10.9945 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2024: 0.79162; RTE_2025: 0.85662; EFC_2024: 31.6981; EFC_2025: 178.1132; UTI_2024: 0.04813; UTI_2025: 1.6708
65963 | Mesquite Solar 5, LLC | AZ | AZPS | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 60 | 240 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.88294 | 0.89366 | -0.15954 | -0.11928 | 9.2523 | 124.3598 | ok | 0.052483 | ok | 788.4875 | 0.13141 | 0.86859 | 6000 | 9 | 0 | 1 | 0.97685 | 0 | 60 | 60 | -0.095722 | 0.89337 | 30 | 0.089457 | 47.6733 | 1106.8111 | 3.2777 | 0.83153 | 0.0011993 | 0.39916 | 0.0011985 | 0.0011993 | 0.0001 | 0.042453 | 0.0001 | 0.0001 | RTE_2023: 0.89262; RTE_2024: 0.89456; RTE_2025: 0.89243; EFC_2023: 133.4208; EFC_2024: 335.7167; EFC_2025: 319.35; UTI_2023: 1.2325; UTI_2024: 1.2568; UTI_2025: 0.94845
65967 | Paris Solar | WI | MISO | Wisconsin Electric Power Co | Wisconsin Electric Power Co |  |  | TRUE | pv_same_plant | LIB | CS |  | 110 | 440 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 110 | 110
65980 | CED West Side Canal Battery Storage | CA | CISO | RWE Clean Energy | RWE Clean Energy |  |  | FALSE |  | LIB | CS |  | 131 | 524 | 4 | 2.5-4.5h | 2023 | 6 | A | THERMAL_AUX | 0.84016 | 0.80035 | 0.46437 | 0.88469 | -2.9449 | -128.3266 | ok | 0.20589 | ok | 632.2615 | 0.10538 | 0.89462 | 6000 | 11 | 5 | 1 | 0.82384 | 26663.5331 | 131 | 131 | 0.60833 | 0.8147 | 31 | 0.90014 | 2500.7314 | 1002.9055 | 2948.0614 | 334.407 | 0.03025 | 0.20169 | 0.34288 | 0.20982 | 0.0025597 | 0.018771 | 0.043891 | 0.019625 | RTE_2023: 0.78438; RTE_2024: 0.81053; RTE_2025: 0.82938; EFC_2023: 98.5611; EFC_2024: 246.7958; EFC_2025: 286.9046; UTI_2023: 0.65669; UTI_2024: 0.9087; UTI_2025: 1.035 | THERMAL_AUX
65987 | Desert Peak Energy Storage I | CA | CISO | Desert Peak Energy Storage I, LLC | Desert Peak Energy Storage I, LLC |  |  | TRUE | rte_gt_1 | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, System Peak Shaving | 325 | 1300 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.87936 | 0.88329 | 0.00099246 | -0.00037113 | 1.9223 | 193.9445 | ok | 21.6939 | ok | 567.6662 | 0.094611 | 0.90539 | 6000 | 5 | 0 | 1 | 0.88661 | 0 | 325 | 325 | 0.0032255 | 0.87593 | 30 | 0.00069757 | 7489.7009 | 3003.7061 | 2164.7949 | 1001.5502 | 0.03025 | 0.20169 | 0.1141 | 0.20982 | 0.0025597 | 0.018771 | 0.010761 | 0.019625 | RTE_2023: 0.94167; RTE_2024: 0.87103; RTE_2025: 0.87851; EFC_2023: 2.4338; EFC_2024: 214.2823; EFC_2025: 350.95; UTI_2023: 0.018607; UTI_2024: 0.8479; UTI_2025: 1.234
65988 | Desert Peak Energy Storage II | CA | CISO | Desert Peak Energy Storage II, LLC | Desert Peak Energy Storage II, LLC |  |  | TRUE | rte_gt_1 | LIB | CS | Frequency Regulation, Load Following | 75 | 300 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.87529 | 0.88018 | -0.024823 | 0.022976 | 1.3871 | 190.0377 | ok | -2.672 | ok | 570.5367 | 0.095089 | 0.90491 | 6000 | 5 | 0 | 1 | 0.88194 | 0 | 75 | 75 | -0.018617 | 0.87621 | 30 | 0.019063 | 1556.4052 | 624.1883 | 449.8575 | 208.1282 | 0.03025 | 0.20169 | 0.1141 | 0.20982 | 0.0025597 | 0.018771 | 0.010761 | 0.019625 | RTE_2023: 0.89383; RTE_2024: 0.8709; RTE_2025: 0.87751; EFC_2023: 42.3467; EFC_2024: 213.5033; EFC_2025: 314.6867; UTI_2023: 0.32639; UTI_2024: 0.83333; UTI_2025: 1.0736
66006 | House Mountain | TX | ERCO | House Mountain | House Mountain |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 73.2 | 120 | 1.6393 | 1.5-2.5h | 2024 | 69 | A | UNATTRIBUTED | 0.79801 | 0.90931 | -0.88172 | 0.1729 |  |  | insufficient_history | -0.060229 | ok | 612.05 | 0.10201 | 0.89799 | 6000 | 0 | 2 | 1 | 0.7644 | 1699.3775 | 60 | 60 | -0.64542 | 0.90355 | 23 | 0.12034 | 476.7159 | 104.2824 | 593.1009 | 232.8195 | 0.022471 | 0.086899 | 0.28987 | 0.47079 | 0.0018939 | 0.0075758 | 0.034272 | 0.05303 | RTE_2024: 0.93919; RTE_2025: 0.87659; EFC_2024: 273.9917; EFC_2025: 338.0583; UTI_2024: 1.1445; UTI_2025: 1.1881 | THERMAL_AUX
66007 | Flower Valley II | TX | ERCO | Flower Valley II | Flower Valley II |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 101 | 200 | 1.9802 | 1.5-2.5h | 2022 |  |  | UNDER_DISPATCH | 0.90959 | 0.84987 | 0.42644 | 0.13939 | -0.19288 | 12.2522 | ok | -0.10308 | ok | 948.925 | 0.15815 | 0.84185 | 6000 | 4 | 0 | 1 | 0.88852 | 7623.0104 | 100 | 100 | 0.4307 | 0.85294 | 36 | 0.41372 | 908.6262 | 149.0727 | 207.5045 | 253.5753 | 0.031828 | 0.092476 | 0.096827 | 0.404 | 0.0026954 | 0.0080863 | 0.0089532 | 0.043127 | RTE_2023: 0.85969; RTE_2024: 0.85518; RTE_2025: 0.84412; EFC_2023: 239.02; EFC_2024: 280.46; EFC_2025: 250.18; UTI_2023: 1.249; UTI_2024: 0.98415; UTI_2025: 1.0084
66008 | Swoose II | TX | ERCO | Swoose II | Swoose II |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 101 | 200 | 1.9802 | 1.5-2.5h | 2022 | 88 | B | PARTIAL_AVAILABILITY | 0.9039 | 0.85199 | 0.40806 | 0.12202 | -1.8256 | -1.0738 | ok | -0.20057 | ok | 908.9833 | 0.1515 | 0.8485 | 6000 | 6 | 4 | 1 | 0.82779 | 1393 | 100 | 100 | 0.41214 | 0.85231 | 36 | 0.080112 | 935.1352 | 153.4218 | 213.5584 | 260.9733 | 0.031828 | 0.092476 | 0.096827 | 0.404 | 0.0026954 | 0.0080863 | 0.0089532 | 0.043127 | RTE_2023: 0.85585; RTE_2024: 0.85333; RTE_2025: 0.84833; EFC_2023: 239.9; EFC_2024: 283.95; EFC_2025: 285.175; UTI_2023: 1.2501; UTI_2024: 1.0253; UTI_2025: 1.0641 | PARTIAL_AVAILABILITY
66009 | Crossett Power Management LLC | TX | ERCO | Crossett Power Management LLC | Crossett Power Management LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 203 | 400 | 1.9704 | 1.5-2.5h | 2022 |  |  | UNATTRIBUTED | 0.87845 | 0.87691 | 0.0076782 | 0.036261 | -5.7583 | -210.8828 | ok | 0.99543 | ok | 558.7735 | 0.093129 | 0.90687 | 6000 | 6 | 0 | 1 | 0.83312 | 68809.6053 | 200 | 200 | 0.015587 | 0.87705 | 36 | 0.0015343 | 1165.0119 | 191.1363 | 266.0557 | 325.1262 | 0.031828 | 0.092476 | 0.096827 | 0.404 | 0.0026954 | 0.0080863 | 0.0089532 | 0.043127 | RTE_2023: 0.87886; RTE_2024: 0.88477; RTE_2025: 0.87021; EFC_2023: 157.7975; EFC_2024: 126.67; EFC_2025: 182.2575; UTI_2023: 0.64827; UTI_2024: 0.31329; UTI_2025: 0.62603
66023 | Grossmont-Cuyamaca-Cuyamaca Col. Solar & | CA | CISO | Forefront Power, LLC | Forefront Power, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 1 | 1 | 1 | <1.5h | 2024 | 316 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 9 | 1 | 0 | 0 | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0; RTE_2025: 0; EFC_2024: 0; EFC_2025: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
66048 | Middleton Biogas Solar, LLC | WI | MISO | Juhl Clean Energy Assets, Inc. | Middleton Biogas Solar, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Backup Power | 0.3 | 0.4 | 1.3333 | <1.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.3 | 0.3
66050 | Lancaster Area Battery | CA | CISO | AES Distributed Energy | AES Distributed Energy |  |  | FALSE |  | LIB | CT | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 127 | 508 | 4 | 2.5-4.5h | 2022 | 20 | B | PARTIAL_AVAILABILITY | 0.91274 | 0.87176 | 0.67389 | 0.15591 | 0.84046 | 19.6776 | ok | -0.12087 | ok | 969.8839 | 0.16165 | 0.83835 | 6000 | 0 | 4 | 1 | 0.87706 | 15249.9819 | 127 | 127 | 0.85584 | 0.87191 | 40 | 0.1312 | 2415.0629 | 968.5486 | 627.6941 | 322.9511 | 0.03025 | 0.20169 | 0.10382 | 0.20982 | 0.0025597 | 0.018771 | 0.0096766 | 0.019625 | RTE_2022: 0.85036; RTE_2023: 0.87516; RTE_2024: 0.87252; RTE_2025: 0.87484; EFC_2022: 88.4724; EFC_2023: 291.3937; EFC_2024: 308.8524; EFC_2025: 281.1654; UTI_2022: 0.93412; UTI_2023: 0.99631; UTI_2024: 1.1675; UTI_2025: 1.0027 | PARTIAL_AVAILABILITY
66067 | Kapolei Energy Storage | HI | HECO | Kapolei Energy Storage I, LLC | Kapolei Energy Storage I, LLC |  |  | FALSE |  | LIB | CS |  | 185 | 565 | 3.0541 | 2.5-4.5h | 2023 | 13 | B | PARTIAL_AVAILABILITY | 0.93927 | 0.90432 | 0.45624 | -0.054413 | 0.19039 | 7.1219 | ok | 0.44025 | ok | 667.5274 | 0.11125 | 0.88875 | 6000 | 0 | 4 | 1 | 0.90642 | 9116 | 185 | 185 | 0.84404 | 0.90444 | 24 | 0.095168 | 107.1851 | 1862.6069 | 251.9464 | 139.7792 | 0.0011993 | 0.31703 | 0.039378 | 0.085813 | 0.0001 | 0.031776 | 0.0034189 | 0.0074766 | RTE_2024: 0.90522; RTE_2025: 0.90361; EFC_2024: 329.5858; EFC_2025: 310.4761; UTI_2024: 1.3009; UTI_2025: 1.0803 | PARTIAL_AVAILABILITY
66075 | Blacksmith Road Solar 1 | MA | ISNE | Blacksmith Road Solar 1, LLC | Blacksmith Road Solar 1, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CT | Co-Located Renewable Firming | 2 | 3.3 | 1.65 | 1.5-2.5h | 2021 | 302 | C | HYBRID_ARTEFACT | 0.91492 | 0.90753 | 0.052694 | -0.00017873 | 3.7115 | 196.419 | ok | 0.26671 | ok | 1004.2424 | 0.16737 | 0.83263 | 6000 | 0 | 2 | 1 | 0.89928 | 4 | 1 | 1 | 0.0010539 | 0.90844 | 36 | 0.054631 | 95.9935 | 2.9165 | 1.0176 | 0.27906 | 0.14392 | 0.082709 | 0.023389 | 0.025567 | 0.01295 | 0.0071942 | 0.0019967 | 0.0021583 | RTE_2023: 0.90304; RTE_2024: 0.89896; RTE_2025: 0.92272; EFC_2023: 279.3939; EFC_2024: 366.6667; EFC_2025: 358.1818; UTI_2023: 1.4344; UTI_2024: 2.8616; UTI_2025: 3.1563 | PARTIAL_AVAILABILITY
66076 | Electric Avenue Lunenburg Solar 1 | MA | ISNE | Electric Avenue Lunenburg Solar 1, LLC | Electric Avenue Lunenburg Solar 1, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CT |  | 1 | 1 | 1 | <1.5h | 2022 | 264 | C | HYBRID_ARTEFACT | 0.9461 | 0.92905 | 0.16839 | 0.00071599 | 13.1457 | 234.2955 | ok |  | insufficient_history | 1540 | 0.25667 | 0.74333 | 6000 | 0 | 2 | 1 | 0.95652 | 29.5 | 1 | 1 | 0.0016839 | 0.92995 | 24 | 0.029032 | 52.6364 | 2.8786 | 0.035827 | 0.30603 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.90184; RTE_2025: 0.95719; EFC_2024: 735; EFC_2025: 805; UTI_2024: 1.2099; UTI_2025: 1.4105 | PARTIAL_AVAILABILITY
66128 | Lake Mabel Solar and Battery Storage | FL | TEC | Tampa Electric Co | Tampa Electric Co |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, Transmission and Distribution Deferral, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 40 | 103 | 2.575 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.76409 |  |  |  |  | insufficient_history |  | insufficient_history | 76.0485 | 0.012675 | 0.98733 | 6000 | 0 | 0 | 1 | 0.81613 | 0 | 40 | 40 |  |  |  |  | 404.3174 | 22.1113 | 13.4057 | 31.7349 | 0.081309 | 0.081309 | 0.039259 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034081 | 0.031802 | RTE_2025: 0.77203; EFC_2025: 76.0485; UTI_2025: 0.3007
66129 | Dover Solar and Battery Storage | FL | TEC | Tampa Electric Co | Tampa Electric Co |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, Co-Located Renewable Firming, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 15 | 30 | 2 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.88093 | 0.77742 | 0.42208 | -0.11669 |  |  | insufficient_history |  | insufficient_history | 101.2 | 0.016867 | 0.98313 | 6000 | 0 | 0 | 1 | 0.87901 | 0 | 15 | 15 | 0.063311 | 0.78288 | 10 | 0.071979 | 346.3297 | 9.47 | 0.11429 | 6.0408 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2025: 0.78288; EFC_2025: 101.2; UTI_2025: 0.32748
66137 | Zier Solar | TX | ERCO | Cypress Creek Renewables | Cypress Creek Renewables |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 40.4 | 80 | 1.9802 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.87698 | 0.80575 | 0.62743 | -0.020861 |  |  | insufficient_history | -0.61195 | ok | 520.5625 | 0.08676 | 0.91324 | 6000 | 4 | 0 | 1 | 0.85962 | 0 | 40.4 | 40.4 | 0.25348 | 0.81156 | 21 | 0.56685 | 289.1293 | 63.2475 | 119.4468 | 141.2056 | 0.022471 | 0.086899 | 0.11987 | 0.47079 | 0.0018939 | 0.0075758 | 0.01138 | 0.05303 | RTE_2024: 0.80303; RTE_2025: 0.81664; EFC_2024: 192.275; EFC_2025: 328.2875; UTI_2024: 0.89611; UTI_2025: 1.1326
66163 | Jicarilla Solar 1 LLC | NM | PNM | Repsol Renewables NA | Repsol Renewables NA |  |  | TRUE | pv_same_plant | LIB | CS |  | 20 | 80 | 4 | 2.5-4.5h | 2023 | 400 | C | HYBRID_ARTEFACT | 0.84002 | 0.85841 | -0.20026 | -0.01955 | -1.8832 | 38.1259 | ok | 1.6486 | ok | 641.3125 | 0.10689 | 0.89311 | 6000 | 0 | 0 | 1 | 0.81411 | 0 | 20 | 20 | -0.040051 | 0.85498 | 30 | 0.019217 | 14.4991 | 251.957 | 33.3682 | 18.9081 | 0.0011993 | 0.31703 | 0.038587 | 0.085813 | 0.0001 | 0.031776 | 0.0033474 | 0.0074766 | RTE_2023: 0.84253; RTE_2024: 0.88289; RTE_2025: 0.8364; EFC_2023: 125.3375; EFC_2024: 247.375; EFC_2025: 268.6; UTI_2023: 1.0475; UTI_2024: 0.98082; UTI_2025: 1.0404 | LOW_ETA_AND_LOW_UTI
66170 | Revolution | TX | ERCO | Crane 2 BESS, LLC | Crane 2 BESS, LLC |  |  | FALSE |  | LIB | CS |  | 150 | 368.8 | 2.4587 | 1.5-2.5h | 2023 |  |  | UNDER_DISPATCH | 0.86359 | 0.85128 | 0.089038 | -0.052075 | -3.6788 | -72.1175 | ok | -0.46663 | ok | 444.7571 | 0.074126 | 0.92587 | 6000 | 3 | 0 | 1 | 0.86204 | 21589.6778 | 150 | 150 | 0.13356 | 0.85375 | 24 | 0.28237 | 1476.5918 | 242.2553 | 379.6967 | 412.0805 | 0.031828 | 0.092476 | 0.10769 | 0.404 | 0.0026954 | 0.0080863 | 0.010081 | 0.043127 | RTE_2024: 0.85005; RTE_2025: 0.85709; EFC_2024: 201.8465; EFC_2025: 226.09; UTI_2024: 0.71583; UTI_2025: 0.85232
66178 | South 49th 013445 SCS Norfolk, LLC | NE | WACM | Arevon Energy, Inc. | Arevon Energy, Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 2.1 | 2.1 | 1 | <1.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
66180 | Huxley Solar | MA | ISNE | Agilitas Energy, Inc. | Agilitas Energy, Inc. |  |  | TRUE | colocated_firming,pv_same_plant,dc_tight | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving | 5 | 3.5 | 0.7 | <1.5h | 2022 | 132 | C | HYBRID_ARTEFACT | 0.78454 | 0.79581 | 0.01016 | -0.01378 |  |  | insufficient_history |  | insufficient_history | 346.5714 | 0.057762 | 0.94224 | 6000 | 0 | 13 | 1 | 0.81068 | 356 | 3.5 | 3.5 | 0.00050802 | 0.80013 | 15 | 0.0030689 | 0 | 0 | 0 | 0 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2023: 0.89362; RTE_2024: 0.79055; EFC_2023: 36; EFC_2024: 310.5714; EFC_2025: 0; UTI_2023: 0.30597; UTI_2024: 0.74614; UTI_2025: 0 | FULL_OUTAGE
66181 | Beacon Solar, LLC | MA | ISNE | Agilitas Energy, Inc. | Agilitas Energy, Inc. |  |  | TRUE | colocated_firming,pv_same_plant,dc_tight | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving | 5 | 7.8 | 1.56 | 1.5-2.5h | 2022 | 140 | C | HYBRID_ARTEFACT | 0.94614 | 0.92097 | 0.070443 | 0.0043938 |  |  | insufficient_history |  | insufficient_history | 185.9402 | 0.03099 | 0.96901 | 6000 | 0 | 13 | 1 | 0.91515 | 314.5 | 2 | 2 | 0.0035222 | 0.92037 | 16 | 0.019257 | 0 | 0 | 0 | 0 | 0.17028 | 0.076884 | 0.024368 | 0.076884 | 0.015556 | 0.0066667 | 0.0020825 | 0.0066667 | RTE_2023: 0.90261; RTE_2024: 0.92726; EFC_2023: 48.7179; EFC_2024: 129.1026; EFC_2025: 0; UTI_2023: 0.52082; UTI_2024: 0.73986; UTI_2025: 0 | FULL_OUTAGE
66182 | Town of Amherst Solar | MA | ISNE | Agilitas Energy, Inc. | Agilitas Energy, Inc. |  |  | TRUE | colocated_firming,pv_same_plant,dc_tight | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving | 2.5 | 2 | 0.8 | <1.5h | 2022 | 202 | C | HYBRID_ARTEFACT | 0.69192 | 0.72898 | -0.039523 | -0.00053253 |  |  | insufficient_history |  | insufficient_history | 381 | 0.0635 | 0.9365 | 6000 | 0 | 12 | 1 | 0.72321 | 97.5 | 2 | 2 | -0.00098809 | 0.72133 | 20 | 0.059548 | 0 | 0 | 0 | 0 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2023: 0.95988; RTE_2024: 0.60053; EFC_2023: 155.5; EFC_2024: 225.5; EFC_2025: 0; UTI_2023: 0.66651; UTI_2024: 0.49143; UTI_2025: 0 | FULL_OUTAGE
66208 | North Central Valley | CA | CISO | North Central Valley Energy Storage, LLC | North Central Valley Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, System Peak Shaving | 132 | 528 | 4 | 2.5-4.5h | 2023 |  |  | THERMAL_AUX | 0.89239 | 0.88326 | 0.18067 | 0.33701 | -1.9931 | -125.6156 | ok | 0.48655 | ok | 775.3125 | 0.12922 | 0.87078 | 6000 | 0 | 0 | 1 | 0.92294 | 6569.8447 | 132 | 132 | 0.23848 | 0.88408 | 28 | 0.010875 | 2848.384 | 1142.3298 | 1719.2377 | 380.8963 | 0.03025 | 0.20169 | 0.21153 | 0.20982 | 0.0025597 | 0.018771 | 0.022472 | 0.019625 | RTE_2023: 0.86717; RTE_2024: 0.88861; RTE_2025: 0.88607; EFC_2023: 122.2121; EFC_2024: 320.3977; EFC_2025: 332.7027; UTI_2023: 1.4353; UTI_2024: 1.3035; UTI_2025: 1.1444
66218 | Dubois Solar (Hybrid) | NY | NYIS | Generate NY Community Solar Lessor III | Generate Capital |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 2 | 4 | 2 | 1.5-2.5h | 2020 | 190 | C | FULL_OUTAGE | 0.99165 | 0.92618 | 0.22136 | 8.9173e-05 |  |  | ok | 0.99281 | ok | 521.1856 | 0.086864 | 0.91314 | 6000 | 0 | 19 | 1 | 0.94737 | 278.5 | 2 | 2 | 0.0044273 | 0.93633 | 15 | 0.38437 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | RTE_2022: 0.89788; RTE_2023: 0.92965; RTE_2024: 0.96373; RTE_2025: 0.77778; EFC_2022: 153.8636; EFC_2023: 126.1364; EFC_2024: 46.5; EFC_2025: 28; UTI_2022: 0.6682; UTI_2023: 0.55724; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
66222 | Landau II Solar (Hybrid) | NY | NYIS | Generate NY Community Solar Lessor III | Generate Capital |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 4 | 8 | 2 | 1.5-2.5h | 2021 | 255 | C | FULL_OUTAGE | 0.85568 | 0.87992 | -0.025886 | 0.0011779 |  |  | ok | 3.5782 | ok | 114.9015 | 0.01915 | 0.98085 | 6000 | 0 | 19 | 1 | 0.95172 | 156 | 4 | 4 | -0.0010354 | 0.92426 | 16 | 0.11359 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | RTE_2022: 0.97484; RTE_2023: 0.92365; RTE_2024: 0.92857; RTE_2025: 0.68966; EFC_2022: 35.2273; EFC_2023: 56.3636; EFC_2024: 17.875; EFC_2025: 2.5; UTI_2022: 0.15298; UTI_2023: 0.14306; UTI_2024: 0.013081; UTI_2025: 0 | FULL_OUTAGE
66228 | Salt Point Solar (Hybrid) | NY | NYIS | Generate NY Community Solar Lessor III | Generate Capital |  |  | TRUE | rte_gt_1,pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 2 | 2 | 1 | <1.5h | 2021 | 157 | C | HYBRID_ARTEFACT | 0.93738 | 0.90946 | 0.057736 | -0.00109 |  |  | ok | -0.52937 | ok | 604.0455 | 0.10067 | 0.89933 | 6000 | 0 | 15 | 1 | 0.96774 | 347.192 | 2 | 2 | 0.0011547 | 0.92722 | 20 | 0.43947 | 0 | 0 | 0 | 0 | 0.13542 | 0.11205 | 0.051503 | 0.22481 | 0.012126 | 0.009903 | 0.00453 | 0.021221 | RTE_2022: 0.94681; RTE_2023: 0.9375; RTE_2024: 0.91451; RTE_2025: 0.84259; EFC_2022: 141.5909; EFC_2023: 98.8636; EFC_2024: 176.5; EFC_2025: 45.5; UTI_2022: 0.6149; UTI_2023: 0.44046; UTI_2024: 0.18451; UTI_2025: 0 | FULL_OUTAGE
66232 | Svenski Solar (Hybrid) | NY | NYIS | Generate NY Community Solar Lessor III | Generate Capital |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | Excess Wind and Solar Generation | 2 | 4 | 2 | 1.5-2.5h | 2022 | 287 | C | FULL_OUTAGE | 0.91985 | 0.90822 | 0.026711 | -0.00098853 |  |  | ok |  | insufficient_history | 195.2045 | 0.032534 | 0.96747 | 6000 | 0 | 25 | 1 | 0.97248 | 194 | 2 | 2 | 0.00053422 | 0.9382 | 11 | 0.072691 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028266 | 0.17213 | 0.016809 | 0.0082711 | 0.0024255 | 0.015742 | RTE_2022: 0.95455; RTE_2023: 0.93893; RTE_2025: 0.9; EFC_2022: 81.1364; EFC_2023: 111.8182; EFC_2024: 0; EFC_2025: 2.25; UTI_2022: 0.47872; UTI_2023: 0.34223; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
66263 | Eleven Mile Solar Center | AZ | SRP | Eleven Mile Solar Center, LLC | Eleven Mile Solar Center, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 300 | 1200 | 4 | 2.5-4.5h | 2024 | 390 | C | HYBRID_ARTEFACT | 0.92159 | 0.90196 | 0.32188 | 0.16421 |  |  | insufficient_history | 0.11275 | ok | 509.9908 | 0.084998 | 0.915 | 6000 | 6 | 2 | 1 | 0.90519 | 0 | 300 | 300 | 0.96564 | 0.90322 | 19 | 0.85305 | 17571.8561 | 960.9685 | 564.5831 | 1379.2145 | 0.081309 | 0.081309 | 0.038091 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033026 | 0.031802 | RTE_2024: 0.90059; RTE_2025: 0.90476; EFC_2024: 187.1358; EFC_2025: 322.855; UTI_2024: 1.1424; UTI_2025: 0.98292 | PARTIAL_AVAILABILITY
66265 | Paradise Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Load Following | 10 | 10 | 1 | <1.5h | 2024 | 117 | B | PARTIAL_AVAILABILITY | 0.91835 | 0.84672 | 0.88346 | 0.089774 |  |  | insufficient_history | 0.013208 | ok | 1702.1 | 0.28368 | 0.71632 | 6000 | 0 | 2 | 1 | 0.86254 | 913.875 | 10 | 10 | 0.088346 | 0.85528 | 22 | 0.29624 | 972.9157 | 26.6034 | 0.41807 | 46.667 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.83099; RTE_2025: 0.87321; EFC_2024: 702.1; EFC_2025: 1000; UTI_2024: 0.92291; UTI_2025: 1.1864 | PARTIAL_AVAILABILITY
66266 | Clairemont Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 10 | 10 | 1 | <1.5h | 2024 | 109 | B | UNATTRIBUTED | 0.90596 | 0.84075 | 0.65575 | -0.0040154 |  |  | insufficient_history | 0.22029 | ok | 1323 | 0.2205 | 0.7795 | 6000 | 0 | 2 | 1 | 0.86241 | 1302.7777 | 10 | 10 | 0.065575 | 0.84461 | 22 | 0.4625 | 761.5399 | 20.8235 | 0.32724 | 36.5281 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.83263; RTE_2025: 0.85342; EFC_2024: 552.7; EFC_2025: 770.3; UTI_2024: 0.71737; UTI_2025: 0.89366 | PARTIAL_AVAILABILITY
66270 | Proxima | CA | CISO | Proxima Solar, LLC | Proxima Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Excess Wind and Solar Generation | 162 | 648 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.92791 | 0.85074 | 0.97091 | -0.27375 |  |  | insufficient_history | 1.025 | ok | 348.8472 | 0.058141 | 0.94186 | 6000 | 0 | 0 | 1 | 0.87828 | 0 | 162 | 162 | 1.5729 | 0.85577 | 18 | 0.19567 | 4089.439 | 745.4766 | 91.2025 | 594.4073 | 0.051638 | 0.16199 | 0.016902 | 0.35714 | 0.0044183 | 0.014728 | 0.0014332 | 0.036819 | RTE_2024: 0.83032; RTE_2025: 0.87045; EFC_2024: 123.8148; EFC_2025: 225.0324; UTI_2024: 0.82411; UTI_2025: 0.79188
66271 | Ameresco HCE Solar LLC | CO | PSCO | Ameresco HCE Solar LLC | Ameresco HCE Solar LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management | 5.8 | 15.5 | 2.6724 | 2.5-4.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 5 | 5
66278 | Elliott Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 10 | 10 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH | 0.89311 | 0.84783 | 0.56775 | 0.087935 |  |  | insufficient_history | -0.33786 | ok | 1525.6 | 0.25427 | 0.74573 | 6000 | 0 | 0 | 1 | 0.8828 | 999.0116 | 10 | 10 | 0.056775 | 0.85262 | 21 | 0.083139 | 869.5765 | 23.7777 | 0.37366 | 41.7102 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.83144; RTE_2025: 0.86635; EFC_2024: 585; EFC_2025: 940.6; UTI_2024: 0.85611; UTI_2025: 1.2141
66279 | Boulevard Energy Storage | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 10 | 10 | 1 | <1.5h | 2024 | 64 | B | UNDER_DISPATCH | 0.93662 | 0.82637 | 0.88994 | 0.040728 |  |  | insufficient_history | -0.14514 | ok | 1215.3 | 0.20255 | 0.79745 | 6000 | 0 | 3 | 1 | 0.89388 | 4206.5578 | 10 | 10 | 0.088994 | 0.85117 | 19 | 0.78817 | 765.65 | 20.9359 | 0.329 | 36.7252 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.83163; RTE_2025: 0.86525; EFC_2024: 497.4; EFC_2025: 717.9; UTI_2024: 0.83461; UTI_2025: 1.0327 | FULL_OUTAGE
66280 | Pala Gomez Creek BESS | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 10 | 10 | 1 | <1.5h | 2024 |  |  | FULL_OUTAGE | 0.88255 | 0.87291 | 0.20733 | 0.021062 |  |  | insufficient_history | 0.25213 | ok | 3345.9 | 0.55765 | 0.44235 | 6000 | 0 | 1 | 1 | 0.87841 | 838.5 | 10 | 10 | 0.020733 | 0.87328 | 21 | 0.043806 | 1271.1904 | 34.7594 | 0.54624 | 60.974 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.86726; RTE_2025: 0.88273; EFC_2024: 2029.4; EFC_2025: 1316.5; UTI_2024: 3.6779; UTI_2025: 1.7461
66281 | Melrose BESS | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 20 | 20 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH | 0.88188 | 0.81454 | 0.57515 | 0.019269 |  |  | insufficient_history | -0.45416 | ok | 1094.15 | 0.18236 | 0.81764 | 6000 | 0 | 0 | 1 | 0.83683 | 7416.3752 | 20 | 20 | 0.11503 | 0.81925 | 22 | 0.42279 | 1008.7322 | 27.5827 | 0.43346 | 48.3849 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2024: 0.81532; RTE_2025: 0.823; EFC_2024: 531.55; EFC_2025: 562.6; UTI_2024: 0.7257; UTI_2025: 0.62844
66285 | Condor Energy Storage LLC | CA | CISO | Condor Energy Storage LLC | Condor Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 200 | 800 | 4 | 2.5-4.5h | 2024 | 99 | A | UNATTRIBUTED | 0.97814 | 0.88913 | 1.3781 | -0.044816 |  |  | insufficient_history | 0.69402 | ok | 457.155 | 0.076192 | 0.92381 | 6000 | 4 | 0 | 1 | 0.90281 | 713.866 | 200 | 200 | 2.7563 | 0.89138 | 18 | 0.49526 | 6782.2231 | 1236.3526 | 151.2569 | 985.8084 | 0.051638 | 0.16199 | 0.016902 | 0.35714 | 0.0044183 | 0.014728 | 0.0014332 | 0.036819 | RTE_2024: 0.87944; RTE_2025: 0.89694; EFC_2024: 143.2562; EFC_2025: 313.8988; UTI_2024: 1.0311; UTI_2025: 1.0833 | ELEVATED_P_AUX
66286 | Peregrine Energy Storage LLC | CA | CISO | Peregrine Energy Storage, LLC | Peregrine Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 200 | 400 | 2 | 1.5-2.5h | 2025 |  |  | UNATTRIBUTED |  | 0.87277 |  |  |  |  | insufficient_history |  | insufficient_history | 182.67 | 0.030445 | 0.96955 | 6000 | 0 | 0 | 1 | 0.8718 | 0 | 200 | 200 |  |  |  |  | 43555.853 | 4.3273 | 5.4402 | 506.4737 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.87173; EFC_2025: 182.67; UTI_2025: 0.95339
66325 | Hemmingway BESS | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 116 | 464 | 4 | 2.5-4.5h | 2025 | 66 | A | UNDER_DISPATCH | 0.95398 | 0.85958 | 0.45809 | 0.62469 |  |  | insufficient_history |  | insufficient_history | 100.8901 | 0.016815 | 0.98318 | 6000 | 0 | 0 | 4 | 0.89774 | 39855.8115 | 29 | 116 | 0.53138 | 0.87806 | 10 | 0.54057 | 2457.8036 | 134.4122 | 166.3619 | 192.9129 | 0.081309 | 0.081309 | 0.076938 | 0.31725 | 0.0070671 | 0.0070671 | 0.0069576 | 0.031802 | RTE_2025: 0.87806; EFC_2025: 100.8901; UTI_2025: 0.52118 | THERMAL_AUX
66326 | Black Mesa BESS | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 40 | 160 | 4 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 0.91966 | 0.90588 | 0.1453 | -0.055582 |  |  | insufficient_history |  | insufficient_history | 274.3388 | 0.045723 | 0.95428 | 6000 | 0 | 0 | 4 | 0.91624 | 622.6098 | 10 | 40 | 0.058119 | 0.90799 | 10 | 0.37429 | 1810.4808 | 99.0115 | 60.0289 | 142.1046 | 0.081309 | 0.081309 | 0.039259 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034081 | 0.031802 | RTE_2025: 0.90799; EFC_2025: 195.9563; UTI_2025: 0.84032
66327 | Elmore BESS | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 4 | 16 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED | 0.90519 | 0.90331 | 0.030336 | 0.0040493 |  |  | insufficient_history |  | insufficient_history | 211.9375 | 0.035323 | 0.96468 | 6000 | 0 | 1 | 4 | 0.91418 | 776.1 | 1 | 4 | 0.0012134 | 0.90499 | 11 | 0.0052707 | 138.4897 | 7.5737 | 4.5594 | 10.8701 | 0.081309 | 0.081309 | 0.038994 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033841 | 0.031802 | RTE_2025: 0.90499; EFC_2025: 211.9375; UTI_2025: 0.81378
66328 | Filer BESS | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 2 | 4 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH | 0.90353 | 0.89765 | 0.074166 | 0.025784 |  |  | insufficient_history |  | insufficient_history | 383.25 | 0.063875 | 0.93612 | 6000 | 0 | 1 | 2 | 0.90875 | 250.9194 | 1 | 2 | 0.0014833 | 0.9023 | 10 | 0.020022 | 214.0669 | 5.8534 | 0.070645 | 3.7338 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2025: 0.90123; EFC_2025: 383.25; UTI_2025: 1.6232
66329 | Melba BESS | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 2 | 8 | 4 | 2.5-4.5h | 2025 | 108 | B | FULL_OUTAGE |  | 0.90792 |  |  |  |  | insufficient_history |  | insufficient_history | 117.5 | 0.019583 | 0.98042 | 6000 | 0 | 7 | 4 | 0.93802 | 699.4333 | 0.5 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.081309 | 0.081309 | 0.038994 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033841 | 0.031802 | RTE_2025: 0.90734; EFC_2025: 117.5; UTI_2025: 0 | FULL_OUTAGE
66330 | Weiser BESS | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 3 | 12 | 4 | 2.5-4.5h | 2025 | 104 | B | UNDER_DISPATCH | 0.89154 | 0.91658 | -0.30629 | 0.0065132 |  |  | insufficient_history |  | insufficient_history | 220.1667 | 0.036694 | 0.96331 | 6000 | 0 | 2 | 3.75 | 0.91406 | 893.9875 | 0.8 | 3 | -0.0091887 | 0.91419 | 10 | 0.16644 | 142.3799 | 7.7865 | 4.6875 | 11.1754 | 0.081309 | 0.081309 | 0.038994 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033841 | 0.031802 | RTE_2025: 0.91419; EFC_2025: 220.1667; UTI_2025: 0.96513 | FULL_OUTAGE
66333 | Superstition Energy Storage | AZ | SRP | Superstition Energy Storage, LLC | Superstition Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 90 | 360 | 4 | 2.5-4.5h | 2024 | 42 | A | UNATTRIBUTED | 0.94841 | 0.87463 | 1.1895 | 0.11142 |  |  | insufficient_history | 0.92107 | ok | 470.1278 | 0.078355 | 0.92165 | 6000 | 6 | 0 | 1 | 0.88951 | 3869.7378 | 90 | 90 | 1.0705 | 0.87861 | 18 | 0.84106 | 5434.8139 | 297.2188 | 175.2231 | 426.5784 | 0.081309 | 0.081309 | 0.038218 | 0.31725 | 0.0070671 | 0.0070671 | 0.003314 | 0.031802 | RTE_2024: 0.86762; RTE_2025: 0.88314; EFC_2024: 135.4472; EFC_2025: 334.6806; UTI_2024: 1.028; UTI_2025: 1.2236 | ELEVATED_P_AUX
66334 | Sierra Estrella Energy Storage | AZ | SRP | Sierra Estrella Energy Storage, LLC | Sierra Estrella Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 250 | 1000 | 4 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.88331 | 0.89401 | -0.15903 | 0.72527 |  |  | insufficient_history | -0.91949 | ok | 564.26 | 0.094043 | 0.90596 | 6000 | 7 | 0 | 1 | 0.90557 | 18953.75 | 250 | 250 | -0.39757 | 0.8918 | 20 | 0.5622 | 15578.7971 | 851.9722 | 498.8304 | 1222.7794 | 0.081309 | 0.081309 | 0.037966 | 0.31725 | 0.0070671 | 0.0070671 | 0.0032913 | 0.031802 | RTE_2024: 0.88349; RTE_2025: 0.8964; EFC_2024: 199.046; EFC_2025: 365.214; UTI_2024: 1.2346; UTI_2025: 1.2391
66336 | St. Gall Energy Storage I | TX | ERCO | St. Gall Energy Storage I | St. Gall Energy Storage I |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 102.6 | 200 | 1.9493 | 1.5-2.5h | 2024 |  |  | UNATTRIBUTED | 0.9049 | 0.85787 | 0.39363 | -0.0075361 |  |  | insufficient_history | -0.31128 | ok | 564.55 | 0.094092 | 0.90591 | 6000 | 0 | 0 | 1 | 0.88218 | 2539 | 100 | 100 | 0.40386 | 0.86063 | 22 | 0.32185 | 805.0445 | 176.1049 | 328.6891 | 393.1693 | 0.022471 | 0.086899 | 0.11864 | 0.47079 | 0.0018939 | 0.0075758 | 0.011247 | 0.05303 | RTE_2024: 0.84277; RTE_2025: 0.87279; EFC_2024: 223.865; EFC_2025: 340.685; UTI_2024: 1.0657; UTI_2025: 1.2154
66337 | Tidwell Prairie Storage 1 | TX | ERCO | Tidwell Prairie | Tidwell Prairie |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 200 | 400 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.83765 |  |  |  |  | insufficient_history |  | insufficient_history | 68.3675 | 0.011395 | 0.98861 | 6000 | 0 | 0 | 1 | 0.89195 | 6126.6667 | 200 | 200 |  |  |  |  | 1595.9105 | 349.1082 | 838.1143 | 779.414 | 0.022471 | 0.086899 | 0.14749 | 0.47079 | 0.0018939 | 0.0075758 | 0.014467 | 0.05303 | RTE_2025: 0.85921; EFC_2025: 68.3675; UTI_2025: 1.0658
66338 | Callisto I Energy Center | TX | ERCO | Callisto I Energy Center | Callisto I Energy Center |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 223.4 | 200 | 0.89526 | <1.5h | 2024 | 36 | B | UNATTRIBUTED | 0.84971 | 0.85797 | -0.053365 | -0.0081497 |  |  | insufficient_history | -2.0109 | ok | 815.275 | 0.13588 | 0.86412 | 6000 | 1 | 2 | 1 | 0.8595 | 4638.5575 | 100 | 100 | -0.11922 | 0.85676 | 17 | 0.053874 | 8137.864 | 381.4654 | 77.9462 | 729.9894 | 0.11369 | 0.098277 | 0.01653 | 0.46243 | 0.010057 | 0.0086207 | 0.0014011 | 0.051724 | RTE_2024: 0.86986; RTE_2025: 0.85444; EFC_2024: 124.955; EFC_2025: 690.32; UTI_2024: 1.6111; UTI_2025: 2.9448 | PARTIAL_AVAILABILITY
66357 | Yellow Pine Solar | NV | NEVP | Yellow Pine Solar, LLC | Yellow Pine Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 65 | 260 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.85444 | 0.87179 | -0.31458 | 0.091832 | 0.58251 | 51.05 | ok | -0.14225 | ok | 779.8808 | 0.12998 | 0.87002 | 6000 | 6 | 0 | 1 | 0.88114 | 0 | 65 | 65 | -0.20447 | 0.87092 | 30 | 0.07787 | 51.2256 | 890.1715 | 117.8909 | 66.8028 | 0.0011993 | 0.31703 | 0.038587 | 0.085813 | 0.0001 | 0.031776 | 0.0033474 | 0.0074766 | RTE_2023: 0.87658; RTE_2024: 0.86596; RTE_2025: 0.87297; EFC_2023: 163.3308; EFC_2024: 310.3846; EFC_2025: 306.1654; UTI_2023: 1.2021; UTI_2024: 1.2376; UTI_2025: 1.1097
66394 | Goleta Energy Storage, LLC | CA | CISO | Goleta Energy Storage, LLC | Goleta Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 60 | 160 | 2.6667 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 0.92039 | 0.8592 | 0.65207 | 0.020509 |  |  | insufficient_history | -0.099889 | ok | 581.6063 | 0.096934 | 0.90307 | 6000 | 0 | 0 | 1 | 0.88046 | 4945.3773 | 60 | 60 | 0.39124 | 0.86451 | 23 | 0.7995 | 1110.1573 | 202.374 | 24.5753 | 161.3634 | 0.051638 | 0.16199 | 0.016779 | 0.35714 | 0.0044183 | 0.014728 | 0.0014226 | 0.036819 | RTE_2024: 0.87364; RTE_2025: 0.85318; EFC_2024: 325.5625; EFC_2025: 256.0437; UTI_2024: 1.3411; UTI_2025: 0.85037
66408 | Buena Vista Energy Center | NM | EPE | Buena Vista Energy Center, LLC | Buena Vista Energy Center, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 50 | 200 | 4 | 2.5-4.5h | 2023 | 35 | C | HYBRID_ARTEFACT | 0.89416 | 0.90176 | -0.0050099 | 0.22486 | 1.6735 | 105.3878 | ok | 1.4151 | ok | 439.2625 | 0.07321 | 0.92679 | 6000 | 0 | 2 | 1 | 0.6575 | 4772 | 50 | 50 | -0.0025049 | 0.88924 | 31 | 4.1075e-05 | 24.2789 | 421.9052 | 55.6814 | 31.6618 | 0.0011993 | 0.31703 | 0.038458 | 0.085813 | 0.0001 | 0.031776 | 0.0033357 | 0.0074766 | RTE_2023: 0.80697; RTE_2024: 0.91769; RTE_2025: 0.92305; EFC_2023: 62.7375; EFC_2024: 177.215; EFC_2025: 199.31; UTI_2023: 6.0823; UTI_2024: 0.64187; UTI_2025: 0.7082 | PARTIAL_AVAILABILITY
66420 | Five Wells Solar Center - Hybrid | TX | ERCO | Five Wells Solar Center, LLC | Five Wells Solar Center, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 262.5 | 250 | 0.95238 | <1.5h | 2024 | 180 | C | HYBRID_ARTEFACT | 0.92487 | 0.84886 | 0.43673 | 0.077957 |  |  | insufficient_history |  | insufficient_history | 354.492 | 0.059082 | 0.94092 | 6000 | 0 | 2 | 1 | 0.863 | 141 | 125 | 125 | 1.1464 | 0.8501 | 10 | 0.69559 | 6109.7646 | 286.3975 | 59.1246 | 548.0632 | 0.11369 | 0.098277 | 0.016698 | 0.46243 | 0.010057 | 0.0086207 | 0.0014156 | 0.051724 | RTE_2025: 0.8501; EFC_2025: 354.492; UTI_2025: 1.8523 | PARTIAL_AVAILABILITY
66423 | Stanton Battery Energy Storage | CA | CISO | Wellhead Services, Inc | Wellhead Services, Inc |  |  | FALSE |  | LIB | CS | Frequency Regulation | 68.8 | 275.2 | 4 | 2.5-4.5h | 2023 | 403 | B | PARTIAL_AVAILABILITY | 0.91993 | 0.89792 | 0.40193 | 0.021311 | 1.7643 | 82.8427 | ok | -0.16392 | ok | 724.2078 | 0.1207 | 0.8793 | 6000 | 0 | 2 | 1 | 0.89599 | 97.283 | 68.8 | 68.8 | 0.27653 | 0.89807 | 26 | 0.10208 | 1376.2383 | 551.9333 | 850.1676 | 184.0356 | 0.03025 | 0.20169 | 0.21541 | 0.20982 | 0.0025597 | 0.018771 | 0.022999 | 0.019625 | RTE_2023: 0.90997; RTE_2024: 0.89753; RTE_2025: 0.89635; EFC_2023: 62.4346; EFC_2024: 346.1919; EFC_2025: 315.5814; UTI_2023: 1.4746; UTI_2024: 1.337; UTI_2025: 1.0768 | PARTIAL_AVAILABILITY
66461 | Beaumont BESS | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 116.6 | 400 | 3.4305 | 2.5-4.5h | 2024 | 77 | B | PARTIAL_AVAILABILITY | 0.94544 | 0.87938 | 0.87244 | -0.030556 |  |  | insufficient_history | -2.0997 | ok | 412.82 | 0.068803 | 0.9312 | 6000 | 2 | 2 | 1 | 0.90881 | 6587.3495 | 100 | 100 | 1.0173 | 0.88132 | 17 | 0.50905 | 3251.1867 | 592.669 | 72.6162 | 472.5658 | 0.051638 | 0.16199 | 0.016926 | 0.35714 | 0.0044183 | 0.014728 | 0.0014353 | 0.036819 | RTE_2024: 0.85662; RTE_2025: 0.89064; EFC_2024: 109.93; EFC_2025: 302.89; UTI_2024: 1.0214; UTI_2025: 1.0239 | PARTIAL_AVAILABILITY
66462 | Placerita ESS | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 88 | 320 | 3.6364 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.95421 | 0.88905 | 0.92739 | -0.55452 |  |  | insufficient_history |  | insufficient_history | 344.05 | 0.057342 | 0.94266 | 6000 | 0 | 0 | 1 | 0.90309 | 3296.4882 | 80 | 80 | 0.81611 | 0.88894 | 14 | 0.14135 | 2747.5867 | 500.8662 | 61.6446 | 399.3667 | 0.051638 | 0.16199 | 0.017001 | 0.35714 | 0.0044183 | 0.014728 | 0.0014418 | 0.036819 | RTE_2024: 0.81869; RTE_2025: 0.89911; EFC_2024: 40.075; EFC_2025: 303.975; UTI_2024: 0.86376; UTI_2025: 1.0795
66474 | MA Blackstone | MA | ISNE | Catalyze Blackstone 83 Federal Street Microgrid, LLC | Catalyze Blackstone 83 Federal Street Microgrid, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 3 | 6.4 | 2.1333 | 1.5-2.5h | 2022 | 323 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 8.5938 | 0.0014323 | 0.99857 | 6000 | 0 | 36 | 1 | 0.85591 | 31.8825 | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 0.17028 | 0.076884 | 0.024013 | 0.076884 | 0.015556 | 0.0066667 | 0.0020513 | 0.0066667 | RTE_2022: 0.83333; EFC_2022: 8.5938; EFC_2023: 0; EFC_2024: 0; EFC_2025: 0; UTI_2022: 0.08106; UTI_2023: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
66488 | Davis Solar | NY | NYIS | Generate NY Community Solar V | Generate Capital |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS | Excess Wind and Solar Generation | 2 | 4 | 2 | 1.5-2.5h | 2023 | 173 | C | HYBRID_ARTEFACT | 0.9022 | 0.81887 | 0.14504 | 0.002931 |  |  | insufficient_history |  | insufficient_history | 177.75 | 0.029625 | 0.97037 | 6000 | 0 | 12 | 1 | 0.90476 | 162.5 | 2 | 2 | 0.0029007 | 0.87346 | 13 | 0.74697 | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.028904 | 0.17213 | 0.016809 | 0.0082711 | 0.0024819 | 0.015742 | RTE_2023: 0.91089; RTE_2024: 0.87319; RTE_2025: 0.81065; EFC_2023: 23; EFC_2024: 120.5; EFC_2025: 34.25; UTI_2023: 0.48938; UTI_2024: 0.18293; UTI_2025: 0 | FULL_OUTAGE
66494 | Menifee Power Bank | CA | CISO | Nova Power, LLC | Nova Power, LLC |  |  | FALSE |  | LIB | CS |  | 680 | 2720 | 4 | 2.5-4.5h | 2024.0882 |  |  | UNDER_DISPATCH | 0.88288 | 0.87266 | 0.159 | -0.25472 |  |  | insufficient_history | 0.38365 | ok | 463.1224 | 0.077187 | 0.92281 | 6000 | 3 | 0 | 1 | 0.87143 | 36587.5 | 680 | 680 | 1.0812 | 0.87366 | 19 | 0.12073 | 23243.0986 | 4237.0569 | 517.5941 | 3378.4263 | 0.051638 | 0.16199 | 0.016877 | 0.35714 | 0.0044183 | 0.014728 | 0.001431 | 0.036819 | RTE_2024: 0.86394; RTE_2025: 0.87806; EFC_2024: 152.1746; EFC_2025: 310.9478; UTI_2024: 1.0678; UTI_2025: 1.0509
66499 | Federalsburg Energy Storage 1 LLC | MD | PJM | Convergent Energy and Power LP | Convergent Energy and Power LP |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CT | System Peak Shaving, Excess Wind and Solar Generation | 1.2 | 2.4 | 2 | 1.5-2.5h | 2021 | 187 | C | HYBRID_ARTEFACT | 0.84362 | 0.82409 | 0.03762 | -0.00092014 |  |  | ok | 8.2375 | ok | 578.75 | 0.096458 | 0.90354 | 6000 | 0 | 9 | 1 | 8.1 | 115.5 | 1.2 | 1.2 | 0.00045144 | 0.82105 | 13 | 0.032293 | 2.3214 | 0.076171 | 0.024208 | 0.044539 | 0.17285 | 0.10762 | 0.027963 | 0.1884 | 0.015814 | 0.0094887 | 0.0023987 | 0.017396 | RTE_2024: 0.82; RTE_2025: 0.78723; EFC_2023: 546.25; EFC_2024: 17.0833; EFC_2025: 15.4167; UTI_2023: 2.703; UTI_2024: 0.019976; UTI_2025: 0.034299 | LOW_ETA_AND_LOW_UTI
66500 | Valley Center 85 | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 85 | 212 | 2.4941 | 1.5-2.5h | 2021 | 21 | A | THERMAL_AUX | 0.80616 | 0.78686 | 0.2599 | 0.15161 | 4.5171 | 52.7818 | ok | 0.46639 | ok | 1169.73 | 0.19495 | 0.80505 | 6000 | 0 | 4 | 1 | 0.81028 | 8222.438 | 85 | 85 | 0.22091 | 0.78598 | 36 | 0.023129 | 3064.369 | 335.168 | 885.1131 | 80.1741 | 0.095923 | 0.18264 | 0.29597 | 0.14038 | 0.0084034 | 0.016807 | 0.035304 | 0.012605 | RTE_2023: 0.77652; RTE_2024: 0.77084; RTE_2025: 0.81188; EFC_2023: 294.8915; EFC_2024: 274.0377; EFC_2025: 281.3349; UTI_2023: 0.95009; UTI_2024: 0.89321; UTI_2025: 0.91098 | THERMAL_AUX
66501 | Cicero Energy Storage 1 LLC | NY | NYIS | Convergent Energy and Power LP | Convergent Energy and Power LP |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Transmission and Distribution Deferral, System Peak Shaving, Excess Wind and Solar Generation | 5 | 20 | 4 | 2.5-4.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 5 | 5
66502 | Valley Center 54 | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 54 | 216 | 4 | 2.5-4.5h | 2021 | 12 | A | THERMAL_AUX | 0.91079 | 0.80261 | 1.3324 | -0.15399 | 9.4843 | 35.6125 | ok | 0.5034 | ok | 919.8858 | 0.15331 | 0.84669 | 6000 | 0 | 0 | 1 | 0.84224 | 16005.7013 | 54 | 54 | 0.71948 | 0.8086 | 36 | 0.37658 | 1936.3236 | 282.3828 | 242.6029 | 118.2082 | 0.080762 | 0.20113 | 0.13269 | 0.25527 | 0.0070175 | 0.018713 | 0.012788 | 0.024561 | RTE_2023: 0.79381; RTE_2024: 0.79945; RTE_2025: 0.83678; EFC_2023: 235.5093; EFC_2024: 208.4815; EFC_2025: 201.1343; UTI_2023: 0.86049; UTI_2024: 0.76055; UTI_2025: 0.69071 | THERMAL_AUX
66503 | Cicero Energy Storage 2 LLC | NY | NYIS | Convergent Energy and Power LP | Convergent Energy and Power LP |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Transmission and Distribution Deferral, System Peak Shaving, Excess Wind and Solar Generation | 5 | 20 | 4 | 2.5-4.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 5 | 5
66505 | EnerSmart Chula Vista Sub Station | CA | CISO | EnerSmart Chula Vista Sub Station | EnerSmart Chula Vista Sub Station |  |  | FALSE |  | LIB | CS | Frequency Regulation | 6 | 12 | 2 | 1.5-2.5h | 2024 | 285 | A | UNATTRIBUTED | 0.81776 | 0.82255 | 0.052348 | 0.00030636 |  |  | insufficient_history |  | insufficient_history | 220.0833 | 0.036681 | 0.96332 | 6000 | 0 | 0 | 1 | 0.83028 | 26.3259 | 6 | 6 | 0.0031409 | 0.81116 | 13 | 0.046246 | 856.4921 | 0.085092 | 0.10698 | 9.9594 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2024: 0.79524; RTE_2025: 0.82217; EFC_2024: 27.8333; EFC_2025: 192.25; UTI_2024: 0.49017; UTI_2025: 0.75335 | LOW_ETA_AND_LOW_UTI
66509 | CA Manteca 730 Spreckels Ave | CA | CISO | Catalyze Manteca 730 Spreckels Avenue Microgrid LLC | Catalyze Manteca 730 Spreckels Avenue Microgrid LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Excess Wind and Solar Generation | 1.5 | 3 | 2 | 1.5-2.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.5 | 1.5
66517 | TX Houston 7080 Express Lane | TX | ERCO | Catalyze Houston Express Lane Microgrid, LLC | Catalyze Houston Express Lane Microgrid, LLC |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
66532 | BCE Los Alamitos 2 | CA | CISO | Bright Canyon Energy | Bright Canyon Energy |  |  | TRUE | pv_same_plant | LIB | CS |  | 10 | 2.9 | 0.29 | <1.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
66533 | BCE Los Alamitos 1 | CA | CISO | Bright Canyon Energy | Bright Canyon Energy |  |  | TRUE | pv_same_plant | LIB | CS |  | 10 | 20 | 2 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.90488 | 0.88445 | 0.1688 | -0.0009117 |  |  | insufficient_history |  | insufficient_history | 294.2 | 0.049033 | 0.95097 | 6000 | 0 | 0 | 1 | 0.88959 | 0 | 10 | 10 | 0.01688 | 0.88468 | 12 | 0.35853 |  |  |  |  | 0.066091 | 0.31344 | 0.031937 | 0.0011993 | 0.005698 | 0.031339 | 0.0027511 | 0.0001 | RTE_2024: 0.88468; EFC_2024: 294.2; UTI_2024: 0.9132
66540 | Shamrock Wind | TX | ERCO | Shamrock Wind LLC | Shamrock Wind LLC |  |  | TRUE | colocated_firming | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Co-Located Renewable Firming, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 100 | 100 | 1 | <1.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.84821 | 0.86178 | -0.20354 | 0.35321 |  |  | insufficient_history |  | insufficient_history | 1038.45 | 0.17308 | 0.82693 | 6000 | 0 | 0 | 1 | 0.87062 | 0 | 100 | 100 | -0.20354 | 0.86073 | 12 | 0.017339 | 6269.9457 | 293.906 | 60.4963 | 562.4319 | 0.11369 | 0.098277 | 0.016649 | 0.46243 | 0.010057 | 0.0086207 | 0.0014114 | 0.051724 | RTE_2025: 0.86073; EFC_2025: 1038.45; UTI_2025: 4.6187
66574 | San Juan Solar I | NM | PNM | San Juan Solar I, LLC | San Juan Solar I, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 100 | 561.4 | 5.614 | >4.5h | 2024 | 44 | C | HYBRID_ARTEFACT | 0.97164 | 0.86253 | 1.7547 | 1.2594 |  |  | insufficient_history |  | insufficient_history | 253.6106 | 0.042268 | 0.95773 | 6000 | 0 | 4 | 1 | 0.88999 | 3497 | 50 | 50 | 1.7547 | 0.86922 | 15 | 0.16204 | 78.6604 | 485.1627 | 5.4081 | 154.7382 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2024: 0.89926; RTE_2025: 0.86335; EFC_2024: 42.9302; EFC_2025: 210.6804; UTI_2024: 2.7432; UTI_2025: 1.9825 | ELEVATED_P_AUX
66575 | Sunlight Storage II | CA | CISO | Sunlight Storage II | Sunlight Storage II |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve | 230 | 920 | 4 | 2.5-4.5h | 2024 | 5 | A | UNATTRIBUTED | 0.99278 | 0.83553 | 2.7724 | -0.77643 |  |  | insufficient_history | -0.043013 | ok | 559.7185 | 0.093286 | 0.90671 | 6000 | 3 | 2 | 1 | 0.85567 | 20096.6592 | 230 | 230 | 6.3765 | 0.83573 | 21 | 0.14421 | 7833.8487 | 1428.0567 | 173.9313 | 1138.6641 | 0.051638 | 0.16199 | 0.016828 | 0.35714 | 0.0044183 | 0.014728 | 0.0014268 | 0.036819 | RTE_2024: 0.81007; RTE_2025: 0.85684; EFC_2024: 244.9565; EFC_2025: 314.762; UTI_2024: 1.2554; UTI_2025: 1.0414 | ELEVATED_P_AUX
66598 | Baldy Mesa Solar & Storage | CA | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 75 | 300 | 4 | 2.5-4.5h | 2024 | 357 | C | HYBRID_ARTEFACT | 0.85963 | 0.90964 | -0.37107 | -0.089125 |  |  | insufficient_history |  | insufficient_history | 190.2633 | 0.031711 | 0.96829 | 6000 | 2 | 0 | 1 | 0.91369 | 0 | 75 | 75 | -0.27831 | 0.90212 | 15 | 0.073738 | 1378.3332 | 251.2607 | 30.8778 | 200.3432 | 0.051638 | 0.16199 | 0.016976 | 0.35714 | 0.0044183 | 0.014728 | 0.0014396 | 0.036819 | RTE_2024: 0.94627; RTE_2025: 0.89642; EFC_2024: 22.8367; EFC_2025: 167.4267; UTI_2024: 0.30684; UTI_2025: 0.57031 | LOW_ETA_AND_LOW_UTI
66599 | Dark Sky Energy Center | CA | CISO | San Diego Gas & Electric Co | San Diego Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following | 7.3 | 7.1 | 0.9726 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.8189 |  |  |  |  | insufficient_history |  | insufficient_history | 193.3803 | 0.03223 | 0.96777 | 6000 | 0 | 0 | 1 | 0.81481 | 323.0583 | 7.1 | 7.1 |  |  |  |  | 497.3202 | 13.5987 | 0.2137 | 23.8545 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.85974; EFC_2025: 193.3803; UTI_2025: 1.0405
66606 | Cross Town Energy Storage | ME | ISNE | Cross Town Energy Storage LLC | Cross Town Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 175 | 350 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.79937 |  |  |  |  | insufficient_history |  | insufficient_history | 13.6743 | 0.002279 | 0.99772 | 6000 | 0 | 0 | 1 | 0.6974 | 6231.8998 | 175 | 175 |  |  |  |  | 2777.5338 | 91.1386 | 31.6535 | 53.291 | 0.17285 | 0.10762 | 0.030478 | 0.1884 | 0.015814 | 0.0094887 | 0.0026213 | 0.017396 | RTE_2025: 0.70872; EFC_2025: 13.6743; UTI_2025: 0.60822
66608 | Craighead Electric Solar One | AR | MISO | Today's Power, Inc. | Today's Power, Inc. |  |  | TRUE | pv_same_plant | LIB | BL | Excess Wind and Solar Generation | 1.2 | 7.2 | 6 | >4.5h | 2020 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.2 | 1.2
66616 | Wolf Tank Storage | TX | ERCO | Wolf Tank Storage LLC | Wolf Tank Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve | 150 | 150 | 1 | <1.5h | 2023 | 29 | A | CELL_DEGRADATION | 0.92115 | 0.70893 | 0.91911 | 0.32668 | -3.4166 | -18.2074 | ok | -1.6455 | ok | 742.12 | 0.12369 | 0.87631 | 6000 | 9 | 0 | 1 | 0.80326 | 26190.3473 | 150 | 150 | 1.3787 | 0.73634 | 30 | 0.9433 | 327.5927 | 89.5768 | 668.5 | 331.4087 | 0.010638 | 0.052071 | 0.23987 | 0.46223 | 0.00089127 | 0.0044563 | 0.026453 | 0.051693 | RTE_2023: 0.55826; RTE_2024: 0.7427; RTE_2025: 0.76905; EFC_2023: 59.0933; EFC_2024: 300.1533; EFC_2025: 382.8733; UTI_2023: 0.28111; UTI_2024: 1.3101; UTI_2025: 1.674 | THERMAL_AUX
66617 | Cald BESS | CA | CISO | Cald BESS LLC | Cald BESS LLC |  |  | FALSE |  | LIB | CT | Load Following, System Peak Shaving | 100 | 400 | 4 | 2.5-4.5h | 2024 | 71 | B | PARTIAL_AVAILABILITY | 0.92358 | 0.84151 | 0.84213 | 0.135 |  |  | insufficient_history | -0.18457 | ok | 458.2975 | 0.076383 | 0.92362 | 6000 | 0 | 2 | 1 | 0.88539 | 10603.0323 | 100 | 100 | 0.84213 | 0.87952 | 16 | 0.056591 | 3903.3048 | 711.5456 | 87.1815 | 567.3524 | 0.051638 | 0.16199 | 0.016926 | 0.35714 | 0.0044183 | 0.014728 | 0.0014353 | 0.036819 | RTE_2024: 0.86631; RTE_2025: 0.88045; EFC_2024: 102.3525; EFC_2025: 355.945; UTI_2024: 1.1118; UTI_2025: 1.2347 | PARTIAL_AVAILABILITY
66619 | Lakeview Battery Storage Facility | CA | CISO | AFTW Storage, LLC | AFTW Storage, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 1.2 | 4.6 | 3.8333 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.84789 |  |  |  |  | insufficient_history |  | insufficient_history | 157.3913 | 0.026232 | 0.97377 | 6000 | 0 | 0 | 1 | 0.84459 | 49.314 | 1.2 | 1.2 |  |  |  |  | 33.7247 | 6.1478 | 0.76468 | 4.9019 | 0.051638 | 0.16199 | 0.017179 | 0.35714 | 0.0044183 | 0.014728 | 0.0014571 | 0.036819 | RTE_2025: 0.84778; EFC_2025: 157.3913; UTI_2025: 0.84923
66620 | Resurgence Solar II | CA | CISO | Resurgence Solar II | Resurgence Solar II |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 40 | 300 | 7.5 | >4.5h | 2023 | 379 | C | HYBRID_ARTEFACT | 0.95123 | 0.85444 | 1.007 | -0.0061374 | -7.5137 | -308.0192 | ok | -1.7897 | ok | 328.32 | 0.05472 | 0.94528 | 6000 | 5 | 0 | 1 | 0.75894 | 0 | 10 | 10 | 0.40281 | 0.87812 | 28 | 0.26958 | 26.1981 | 161.5851 | 1.8012 | 51.5361 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2023: 0.67993; RTE_2024: 0.87835; RTE_2025: 0.87762; EFC_2023: 45.8; EFC_2024: 147.17; EFC_2025: 135.35; UTI_2023: 13.0398; UTI_2024: 1.6476; UTI_2025: 1.263 | ELEVATED_P_AUX
66627 | Sonoran Solar Energy | AZ | SRP | Sonoran Solar Energy, LLC | Sonoran Solar Energy, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation | 260 | 1040 | 4 | 2.5-4.5h | 2023 | 37 | C | HYBRID_ARTEFACT | 0.8886 | 0.88323 | 0.08226 | 1.163 | -3.9295 | -116.3642 | ok | 0.099462 | ok | 810.5596 | 0.13509 | 0.86491 | 6000 | 9 | 2 | 1 | 0.87159 | 4253 | 260 | 260 | 0.21388 | 0.8857 | 31 | 0.10385 | 191.3575 | 3325.3095 | 438.8613 | 249.5475 | 0.0011993 | 0.31703 | 0.038458 | 0.085813 | 0.0001 | 0.031776 | 0.0033357 | 0.0074766 | RTE_2023: 0.87658; RTE_2024: 0.89624; RTE_2025: 0.87801; EFC_2023: 131.6433; EFC_2024: 356.6615; EFC_2025: 322.2548; UTI_2023: 1.0022; UTI_2024: 1.356; UTI_2025: 0.95514 | PARTIAL_AVAILABILITY
66629 | Envoy Solar, LLC | MO | MISO | Birch Creek Development | Birch Creek Development |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
66636 | McFarland A Solar and Storage | AZ | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 100 | 400 | 4 | 2.5-4.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.94037 | 0.91486 | 0.22544 | -0.0096953 | -1.8823 | -272.2894 | ok | -0.84307 | ok | 535.26 | 0.08921 | 0.91079 | 6000 | 8 | 0 | 1 | 0.92273 | 0 | 100 | 100 | 0.22544 | 0.92353 | 25 | 0.89013 | 1809.9351 | 725.8652 | 554.1913 | 242.0311 | 0.03025 | 0.20169 | 0.12005 | 0.20982 | 0.0025597 | 0.018771 | 0.0114 | 0.019625 | RTE_2023: 0.87472; RTE_2024: 0.91836; RTE_2025: 0.93176; EFC_2023: 22.5; EFC_2024: 226.475; EFC_2025: 286.285; UTI_2023: 0.9713; UTI_2024: 0.96165; UTI_2025: 0.97036
66637 | McFarland B Solar and Storage | AZ | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 150 | 600 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.97108 | 0.86661 | 0.478 | 0.035816 |  |  | insufficient_history |  | insufficient_history | 248.1467 | 0.041358 | 0.95864 | 6000 | 4 | 0 | 1 | 0.92901 | 0 | 150 | 150 | 0.71701 | 0.92036 | 13 | 0.98035 | 4989.3036 | 909.5157 | 112.1079 | 725.2043 | 0.051638 | 0.16199 | 0.017026 | 0.35714 | 0.0044183 | 0.014728 | 0.001444 | 0.036819 | RTE_2024: 0.90912; RTE_2025: 0.92058; EFC_2024: 4.8183; EFC_2025: 243.3283; UTI_2024: 0.1961; UTI_2025: 1.0156
66648 | Blackwell?s Corner Storage Facility | CA | CISO | Blackwell Test Facility, LLC | Blackwell Test Facility, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve | 2 | 9 | 4.5 | >4.5h | 2025 | 296 | A | UNATTRIBUTED | 0.78002 | 0.79042 | -0.017603 | 2.2843e-06 |  |  | insufficient_history |  | insufficient_history | 59.4444 | 0.0099074 | 0.99009 | 6000 | 0 | 0 | 1 | 0.78189 | 25.5455 | 2 | 2 | -0.00035205 | 0.78446 | 10 | 0.4245 | 0.17615 | 1.0864 | 0.012111 | 0.34651 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2025: 0.78446; EFC_2025: 59.4444; UTI_2025: 0.23182 | LOW_ETA_AND_LOW_UTI
66650 | Bear Canyon | CA | CISO | Bear Canyon Energy Storage | Bear Canyon Energy Storage |  |  | FALSE |  | LIB | CS | Load Following, Ramping / Spinning Reserve | 13 | 52 | 4 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 1.0153 | 0.88124 | 1.8835 | 0.011303 |  |  | insufficient_history | 0.38373 | ok | 673.4533 | 0.11224 | 0.88776 | 6000 | 0 | 1 | 1 | 0.88942 | 583.29 | 13 | 13 | 0.24485 | 0.88338 | 17 | 0.85676 | 406.8037 | 74.1575 | 9.0861 | 59.1296 | 0.051638 | 0.16199 | 0.016926 | 0.35714 | 0.0044183 | 0.014728 | 0.0014353 | 0.036819 | RTE_2024: 0.87746; RTE_2025: 0.8856; EFC_2024: 382.8571; EFC_2025: 290.5962; UTI_2024: 1.3953; UTI_2025: 0.97402
66659 | Acid BESS | CA | CISO | Malaga BESS LLC | Malaga BESS LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 97 | 97 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH | 0.90493 | 0.87878 | 0.10333 | -0.0038983 |  |  | insufficient_history |  | insufficient_history | 259.7526 | 0.043292 | 0.95671 | 6000 | 0 | 0 | 1 | 0.88403 | 41093.9689 | 97 | 97 | 0.10023 | 0.88153 | 10 | 0.53623 | 3208.8017 | 87.7414 | 1.3788 | 153.9137 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.88153; EFC_2025: 259.7526; UTI_2025: 0.34262
66660 | Lead BESS 1 | CA | CISO | Hanford BESS LLC | Hanford BESS LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 99.4 | 99.4 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.93925 |  |  |  |  | insufficient_history |  | insufficient_history | 101.5594 | 0.016927 | 0.98307 | 6000 | 0 | 0 | 1 | 0.87943 | 21201.0795 | 99.4 | 99.4 |  |  |  |  | 2503.6286 | 68.4591 | 1.0758 | 120.0893 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.92999; EFC_2025: 101.5594; UTI_2025: 0.30972
66661 | Electrolyte BESS | CA | CISO | Henrietta BESS LLC | Henrietta BESS LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 99.4 | 99.4 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.82751 |  |  |  |  | insufficient_history |  | insufficient_history | 158.2797 | 0.02638 | 0.97362 | 6000 | 0 | 0 | 1 | 0.8609 | 40651.2253 | 99.4 | 99.4 |  |  |  |  | 2788.3988 | 76.2459 | 1.1982 | 133.7486 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.8445; EFC_2025: 158.2797; UTI_2025: 0.28523
66662 | Lead BESS 2 | CA | CISO | Hanford BESS LLC | Hanford BESS LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 32 | 32 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.94135 |  |  |  |  | insufficient_history |  | insufficient_history | 107.125 | 0.017854 | 0.98215 | 6000 | 0 | 0 | 1 | 0.91778 | 6647.1966 | 32 | 32 |  |  |  |  | 860.7691 | 23.5368 | 0.36988 | 41.2877 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.94539; EFC_2025: 107.125; UTI_2025: 0.34821
66666 | Tumbleweed Energy Storage | CA | CISO | Tumbleweed Energy Storage, LLC | Tumbleweed Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 125 | 500 | 4 | 2.5-4.5h | 2024 |  |  | CAPACITY_FADE | 0.86526 | 0.84993 | 0.18764 | 0.12438 |  |  | insufficient_history | -9.1012 | ok | 411.736 | 0.068623 | 0.93138 | 6000 | 1 | 0 | 1 | 0.8477 | 285.1897 | 125 | 125 | 0.23455 | 0.85471 | 18 | 0.76688 | 4069.496 | 741.8411 | 90.7577 | 591.5086 | 0.051638 | 0.16199 | 0.016902 | 0.35714 | 0.0044183 | 0.014728 | 0.0014332 | 0.036819 | RTE_2024: 0.8551; RTE_2025: 0.85454; EFC_2024: 121.806; EFC_2025: 289.93; UTI_2024: 0.96046; UTI_2025: 1.0258
66669 | West Ford Flat | CA | CISO | West Ford Flat Energy Storage | West Ford Flat Energy Storage |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, Ramping / Spinning Reserve | 25 | 100 | 4 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.91217 | 0.85214 | 0.71353 | 0.049278 |  |  | insufficient_history | 0.046782 | ok | 541.791 | 0.090299 | 0.9097 | 6000 | 0 | 0 | 1 | 0.86952 | 2023.9644 | 25 | 25 | 0.17838 | 0.86014 | 17 | 0.90619 | 707.0828 | 128.8963 | 15.7929 | 102.7758 | 0.051638 | 0.16199 | 0.016926 | 0.35714 | 0.0044183 | 0.014728 | 0.0014353 | 0.036819 | RTE_2024: 0.86211; RTE_2025: 0.85954; EFC_2024: 284.781; EFC_2025: 257.01; UTI_2024: 1.0392; UTI_2025: 0.85918
66688 | Bright Arrow Solar, LLC | TX | ERCO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation | 103.6 | 100 | 0.96525 | <1.5h | 2025 |  |  | HYBRID_ARTEFACT | 1.0822 | 0.83309 | 1.5348 | -0.13331 |  |  | insufficient_history |  | insufficient_history | 468.77 | 0.078128 | 0.92187 | 6000 | 0 | 1 | 1 | 0.86925 | 4509 | 100 | 100 | 1.59 | 0.83511 | 11 | 0.30741 | 2918.3224 | 136.7975 | 28.1578 | 261.7818 | 0.11369 | 0.098277 | 0.016649 | 0.46243 | 0.010057 | 0.0086207 | 0.0014114 | 0.051724 | RTE_2025: 0.83511; EFC_2025: 468.77; UTI_2025: 2.241
66690 | Brazos Bend BESS, LLC | TX | ERCO | Cypress Creek Renewables | Cypress Creek Renewables |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 100 | 100 | 1 | <1.5h | 2024 |  |  | UNATTRIBUTED | 1.0148 | 0.76087 | 1.2695 | -0.19218 |  |  | insufficient_history |  | insufficient_history | 466.02 | 0.07767 | 0.92233 | 6000 | 0 | 0 | 1 | 0.82078 | 5207.4791 | 100 | 100 | 1.2695 | 0.76661 | 16 | 0.69247 | 2079.7707 | 97.49 | 19.9496 | 186.5613 | 0.11369 | 0.098277 | 0.016554 | 0.46243 | 0.010057 | 0.0086207 | 0.0014032 | 0.051724 | RTE_2024: 0.77735; RTE_2025: 0.76318; EFC_2024: 114.31; EFC_2025: 351.71; UTI_2024: 1.793; UTI_2025: 1.4991
66694 | Atrisco Energy Storage | NM | PNM | Clenera LLC | Atrisco Energy Storage LLC |  |  | TRUE | rte_gt_1 | LIB | CS |  | 300 | 1200 | 4 | 2.5-4.5h | 2024 | 1 | C | HYBRID_ARTEFACT | 0.89201 | 0.90001 | -1.6343 | -1.469 |  |  | insufficient_history |  | insufficient_history | 287.5625 | 0.047927 | 0.95207 | 6000 | 0 | 3 | 1 | 0.89829 | 101856.5 | 300 | 300 | -4.9028 | 0.98246 | 11 | 0.48356 | 18025.4489 | 985.7746 | 589.2915 | 1414.817 | 0.081309 | 0.081309 | 0.038731 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033604 | 0.031802 | RTE_2024: 7.3265; RTE_2025: 0.90001; EFC_2024: 27.5108; EFC_2025: 260.0517; UTI_2024: 0.61352; UTI_2025: 1.1939 | FULL_OUTAGE
66699 | Lockhart Solar PV II | CA | CISO | Terra-Gen Operating Co-Solar | Terra-Gen Operating Co-Solar |  |  | TRUE | pv_same_plant | LIB | CS |  | 59.7 | 59.7 | 1 | <1.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.79219 |  |  |  |  | insufficient_history |  | insufficient_history | 250.4523 | 0.041742 | 0.95826 | 6000 | 0 | 0 | 1 | 0.84865 | 0 | 59.7 | 59.7 |  |  |  |  | 4821.1291 | 131.8288 | 2.0717 | 231.2507 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0.82185; EFC_2025: 250.4523; UTI_2025: 1.149
66716 | Saint Energy Storage II LLC | AZ | SRP | Saint Energy Storage II LLC | Saint Energy Storage II LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 100 | 400 | 4 | 2.5-4.5h | 2023 | 83 | B | UNDER_DISPATCH | 0.91542 | 0.83431 | 0.98823 | 0.3107 | -4.2588 | -64.8839 | ok | -0.15128 | ok | 479.7425 | 0.079957 | 0.92004 | 6000 | 6 | 0 | 1 | 0.8648 | 22992.3919 | 100 | 100 | 0.98823 | 0.83993 | 26 | 0.29626 | 53.3797 | 927.6048 | 254.3362 | 69.612 | 0.0011993 | 0.31703 | 0.076658 | 0.085813 | 0.0001 | 0.031776 | 0.0069301 | 0.0074766 | RTE_2023: 0.76944; RTE_2024: 0.84747; RTE_2025: 0.84051; EFC_2023: 24.595; EFC_2024: 235.7775; EFC_2025: 219.37; UTI_2023: 0.60722; UTI_2024: 0.9268; UTI_2025: 0.72995 | THERMAL_AUX
66717 | Eastover Solar | SC | CPLE | Eastover Solar, LLC | Eastover Solar, LLC |  |  | TRUE | pv_same_plant,dc_coupled | OTH | CS | Excess Wind and Solar Generation | 18 | 72 | 4 | 2.5-4.5h | 2023 | 317 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 21 | 1 | 0 | 0 | 18 | 18 |  |  |  |  | 0 | 0 | 0 | 0 | 0.12376 | 0.14367 | 0.0056493 | 0.12376 | 0.01101 | 0.012925 | 0.0004735 | 0.01101 | RTE_2024: 0; EFC_2024: 0; EFC_2025: 0; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
66726 | Inland Empire Energy Storage | CA | CISO | Inland Empire Energy Storage | Strata Manager, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 70 | 200 | 2.8571 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.87064 | 0.89537 | -0.29914 | 0.063504 |  |  | insufficient_history |  | insufficient_history | 446.565 | 0.074427 | 0.92557 | 6000 | 2 | 0 | 1 | 0.89026 | 3443.2776 | 60 | 60 | -0.2094 | 0.88912 | 14 | 0.88598 | 2376.9398 | 433.2998 | 53.3288 | 345.4925 | 0.051638 | 0.16199 | 0.017001 | 0.35714 | 0.0044183 | 0.014728 | 0.0014418 | 0.036819 | RTE_2024: 0.90972; RTE_2025: 0.88739; EFC_2024: 35.42; EFC_2025: 411.145; UTI_2024: 0.77527; UTI_2025: 1.4488
66727 | Georgia Ballard BESS | VT | ISNE | Strata Manager, LLC | Strata Manager, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 5 | 10 | 2 | 1.5-2.5h | 2023 |  |  | UNATTRIBUTED | 1.1576 | 0.74778 | 1.8078 | 0.0052602 |  |  | ok | 0.77943 | ok | 470 | 0.078333 | 0.92167 | 6000 | 0 | 0 | 1 | 0.76518 | 420.9186 | 3 | 3 | 0.090391 | 0.76841 | 23 | 0.29323 | 170.1118 | 3.987 | 1.5829 | 1.2716 | 0.17028 | 0.076884 | 0.024628 | 0.076884 | 0.015556 | 0.0066667 | 0.0021053 | 0.0066667 | RTE_2024: 0.76999; RTE_2025: 0.7301; EFC_2024: 179.1; EFC_2025: 171.5; UTI_2024: 1.0579; UTI_2025: 1.4421
66728 | Springfield BESS | VT | ISNE | Strata Manager, LLC | Strata Manager, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 5 | 10 | 2 | 1.5-2.5h | 2023 |  |  | UNATTRIBUTED | 1.3209 | 0.71756 | 2.3499 | 0.0058883 |  |  | ok | 1.4164 | ok | 452.2667 | 0.075378 | 0.92462 | 6000 | 0 | 0 | 1 | 0.84483 | 669.0472 | 3 | 3 | 0.11749 | 0.74311 | 23 | 0.48056 | 154.1282 | 3.6124 | 1.4342 | 1.1521 | 0.17028 | 0.076884 | 0.024628 | 0.076884 | 0.015556 | 0.0066667 | 0.0021053 | 0.0066667 | RTE_2024: 0.74881; RTE_2025: 0.69765; EFC_2024: 173.2; EFC_2025: 163.6; UTI_2024: 0.96406; UTI_2025: 1.2312
66757 | Bottleneck Energy Storage | CA | CISO | VESI 12 LLC | VESI 12 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 80 | 320 | 4 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 0.84287 | 0.85058 | -0.080837 | 0.10735 |  |  | insufficient_history |  | insufficient_history | 260.775 | 0.043462 | 0.95654 | 6000 | 0 | 0 | 1 | 0.87851 | 2572.5403 | 80 | 80 | -0.064669 | 0.84901 | 14 | 0.042824 | 2026.7222 | 369.4575 | 45.4714 | 294.5877 | 0.051638 | 0.16199 | 0.017001 | 0.35714 | 0.0044183 | 0.014728 | 0.0014418 | 0.036819 | RTE_2024: 0.86692; RTE_2025: 0.84678; EFC_2024: 29.4969; EFC_2025: 231.2781; UTI_2024: 0.6267; UTI_2025: 0.81447
66758 | Justin Court Energy Storage | NJ | PJM | VESI 23 LLC | VESI 23 LLC |  |  | FALSE |  | LIB | CS |  | 20 | 18.3 | 0.915 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.89892 | 0.88904 | 0.23178 | 0.052033 |  |  | insufficient_history | -0.080523 | ok | 3646.0656 | 0.60768 | 0.39232 | 6000 | 0 | 0 | 1 | 0.90067 | 1296.3357 | 20 | 20 | 0.046356 | 0.88975 | 23 | 0.10645 | 2900.0268 | 129.5205 | 79.3517 | 88.5201 | 0.13542 | 0.11205 | 0.05468 | 0.22481 | 0.012126 | 0.009903 | 0.004826 | 0.021221 | RTE_2024: 0.88663; RTE_2025: 0.89254; EFC_2024: 1717.1585; EFC_2025: 1928.9071; UTI_2024: 0.93547; UTI_2025: 1.0823
66764 | SCH - (2A) 156 Barhydt Rd Glenville | NY | NYIS | Distributed Solar Development, LLC | Distributed Solar Development, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming | 2.5 | 10 | 4 | 2.5-4.5h | 2021 | 336 | C | HYBRID_ARTEFACT | 0.7374 | 0.75225 | -0.039083 | -0.0048504 |  |  | insufficient_history |  | insufficient_history | 92.4 | 0.0154 | 0.9846 | 6000 | 0 | 0 | 1 | 0.87356 | 0 | 2.5 | 2.5 | -0.00097707 | 0.78213 | 15 | 0.040221 | 0 | 0 | 0 | 0 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2024: 0.78147; RTE_2025: 0.60905; EFC_2024: 77.6; EFC_2025: 14.8; UTI_2024: 0.29614; UTI_2025: 0 | LOW_ETA_AND_LOW_UTI
66765 | SCH County - (2B) 4982 Rynex Corners Rd | NY | NYIS | Distributed Solar Development, LLC | Distributed Solar Development, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 2.5 | 10 | 4 | 2.5-4.5h | 2020 |  |  | HYBRID_ARTEFACT | 0.99954 | 0.81679 | 0.42667 | -0.011436 |  |  | insufficient_history |  | insufficient_history | 111.2 | 0.018533 | 0.98147 | 6000 | 0 | 1 | 1 | 0.92593 | 52 | 2.5 | 2.5 | 0.010667 | 0.87728 | 16 | 0.62325 | 0 | 0 | 0 | 0 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2024: 0.87592; RTE_2025: 0.75; EFC_2024: 95.3; EFC_2025: 15.9; UTI_2024: 0.32964; UTI_2025: 0
66767 | Source Power Company - Richland | NY | NYIS | Distributed Solar Development, LLC | Distributed Solar Development, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 2.5 | 9.5 | 3.8 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.9498 | 0.9074 | 0.049598 | 0.00052139 | -0.044743 | -0.66082 | ok |  | insufficient_history | 76.3158 | 0.012719 | 0.98728 | 6000 | 0 | 0 | 1 | 0.95946 | 0 | 2.5 | 2.5 | 0.00124 | 0.9379 | 24 | 0.43455 | 57.5863 | 0.010235 | 0.012868 | 0.0032644 | 0.30873 | 0.0011993 | 0.0011985 | 0.0011993 | 0.030769 | 0.0001 | 0.0001 | 0.0001 | RTE_2024: 0.93814; RTE_2025: 0.93766; EFC_2024: 38.3158; EFC_2025: 38; UTI_2024: 0.12702; UTI_2025: 0.15989
66772 | Estrella Solar & Storage | CA | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 28 | 112 | 4 | 2.5-4.5h | 2023 | 181 | C | HYBRID_ARTEFACT | 0.89305 | 0.88887 | 0.038665 | 0.024124 |  |  | insufficient_history | -2.0591 | ok | 536.9196 | 0.089487 | 0.91051 | 6000 | 0 | 2 | 1 | 0.86108 | 140.5 | 28 | 28 | 0.010826 | 0.89044 | 22 | 0.28785 | 545.9489 | 218.95 | 173.3402 | 73.0063 | 0.03025 | 0.20169 | 0.12392 | 0.20982 | 0.0025597 | 0.018771 | 0.011821 | 0.019625 | RTE_2024: 0.89143; RTE_2025: 0.88965; EFC_2024: 238.6339; EFC_2025: 298.2857; UTI_2024: 0.99318; UTI_2025: 1.06 | PARTIAL_AVAILABILITY
66773 | Raceway Solar & Storage | CA | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 80 | 320 | 4 | 2.5-4.5h | 2024 | 75 | C | HYBRID_ARTEFACT | 0.89259 | 0.90151 | -0.072973 | -0.058502 |  |  | insufficient_history | 0.73899 | ok | 437.8406 | 0.072973 | 0.92703 | 6000 | 0 | 2 | 1 | 0.88284 | 1494 | 80 | 80 | -0.058378 | 0.89604 | 20 | 0.38093 | 2490.5984 | 454.0189 | 55.3799 | 362.013 | 0.051638 | 0.16199 | 0.016852 | 0.35714 | 0.0044183 | 0.014728 | 0.0014289 | 0.036819 | RTE_2024: 0.88987; RTE_2025: 0.90136; EFC_2024: 201.1875; EFC_2025: 236.6531; UTI_2024: 1.1453; UTI_2025: 1.0041 | PARTIAL_AVAILABILITY
66779 | Papago Energy Storage | AZ | AZPS | RE Papago LLC | RE Papago LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 300 | 1200 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 300 | 300
66782 | Hamilton BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.9648 | 0.84161 | 0.28132 | -0.0015998 | -9.2844 | -141.6554 | ok | -0.38162 | ok | 351.0101 | 0.058502 | 0.9415 | 6000 | 3 | 0 | 1 | 0.86842 | 323.1015 | 9.9 | 9.9 | 0.027851 | 0.84943 | 24 | 0.71486 | 128.8092 | 6.038 | 1.2213 | 11.5546 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.81989; RTE_2025: 0.86937; EFC_2024: 136.5657; EFC_2025: 214.4444; UTI_2024: 0.64547; UTI_2025: 0.95804
66783 | Weil Tract BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | CAPACITY_FADE | 0.92669 | 0.80174 | 0.17656 | 0.0029857 |  |  | insufficient_history | -4.7858 | ok | 173.6364 | 0.028939 | 0.97106 | 6000 | 3 | 0 | 1 | 0.83562 | 61.9218 | 9.9 | 9.9 | 0.017479 | 0.81392 | 20 | 0.92824 | 79.3524 | 3.7197 | 0.75674 | 7.1181 | 0.11369 | 0.098277 | 0.016459 | 0.46243 | 0.010057 | 0.0086207 | 0.001395 | 0.051724 | RTE_2024: 0.75458; RTE_2025: 0.83461; EFC_2024: 41.6162; EFC_2025: 132.0202; UTI_2024: 0.31913; UTI_2025: 0.59462
66784 | Pauline BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH | 0.91844 | 0.81984 | 0.15738 | 0.0034209 | -13.4803 | -169.0662 | ok | -2.3004 | ok | 234.0404 | 0.039007 | 0.96099 | 6000 | 0 | 0 | 1 | 0.84431 | 1207.935 | 9.9 | 9.9 | 0.015581 | 0.82809 | 24 | 0.61296 | 91.5321 | 4.2906 | 0.86785 | 8.2107 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.79644; RTE_2025: 0.84602; EFC_2024: 81.4141; EFC_2025: 152.6263; UTI_2024: 0.42494; UTI_2025: 0.68194
66788 | Mineral Wells East BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.94587 | 0.79254 | 0.2669 | -0.00017824 | -12.536 | -119.9429 | ok | -0.78783 | ok | 254.6465 | 0.042441 | 0.95756 | 6000 | 1 | 0 | 1 | 0.83607 | 1055.3967 | 9.9 | 9.9 | 0.026423 | 0.80543 | 24 | 0.89479 | 98.9137 | 4.6366 | 0.93784 | 8.8728 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.75966; RTE_2025: 0.83257; EFC_2024: 89.3939; EFC_2025: 165.2525; UTI_2024: 0.45285; UTI_2025: 0.73719
66789 | Lufkin South BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 | 228 | A | UNATTRIBUTED | 0.82512 | 0.80007 | 0.046313 | 0.0014141 |  |  | insufficient_history | 2.0567 | ok | 233.8384 | 0.038973 | 0.96103 | 6000 | 0 | 0 | 1 | 0.82759 | 95.0921 | 9.9 | 9.9 | 0.004585 | 0.80944 | 23 | 0.18259 | 93.7465 | 4.3944 | 0.89013 | 8.4093 | 0.11369 | 0.098277 | 0.016389 | 0.46243 | 0.010057 | 0.0086207 | 0.001389 | 0.051724 | RTE_2024: 0.7714; RTE_2025: 0.82967; EFC_2024: 77.3737; EFC_2025: 156.4646; UTI_2024: 0.44475; UTI_2025: 0.69852 | LOW_ETA_AND_LOW_UTI
66790 | Judkins BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | CAPACITY_FADE | 1.0313 | 0.89447 | 0.30696 | -0.0048336 |  |  | ok | -3.4792 | ok | 404.0404 | 0.06734 | 0.93266 | 6000 | 1 | 0 | 1 | 0.90323 | 16.2998 | 9.9 | 9.9 | 0.030389 | 0.90232 | 24 | 0.81544 | 145.4179 | 6.8165 | 1.3788 | 13.0444 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.89938; RTE_2025: 0.9043; EFC_2024: 161.6162; EFC_2025: 242.4242; UTI_2024: 0.8669; UTI_2025: 1.098
66791 | Garden City East BESS | TX | ERCO | HEN Infrastructure, L.L.C. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 | 198 | A | PARTIAL_AVAILABILITY | 0.92632 | 0.85988 | 0.10948 | 0.00066294 |  |  | insufficient_history | -1.2661 | ok | 357.3737 | 0.059562 | 0.94044 | 6000 | 1 | 3 | 1 | 0.91743 | 346.9117 | 9.9 | 9.9 | 0.010839 | 0.88425 | 23 | 0.28603 | 124.3803 | 5.8304 | 1.1793 | 11.1573 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.87759; RTE_2025: 0.88841; EFC_2024: 149.899; EFC_2025: 207.4747; UTI_2024: 0.70033; UTI_2025: 0.92489 | PARTIAL_AVAILABILITY
66792 | Falfurrias BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH | 0.968 | 0.80168 | 0.24392 | 0.00061503 |  |  | insufficient_history | -1.817 | ok | 155.9596 | 0.025993 | 0.97401 | 6000 | 2 | 0 | 1 | 0.81679 | 1534.085 | 9.9 | 9.9 | 0.024148 | 0.80711 | 18 | 0.78656 | 69.3872 | 3.2526 | 0.66364 | 6.2242 | 0.11369 | 0.098277 | 0.016506 | 0.46243 | 0.010057 | 0.0086207 | 0.0013991 | 0.051724 | RTE_2024: 0.78039; RTE_2025: 0.81682; EFC_2024: 40.202; EFC_2025: 115.7576; UTI_2024: 0.38402; UTI_2025: 0.52595
66794 | Diboll BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 | 172 | A | UNATTRIBUTED | 0.82266 | 0.78368 | 0.066072 | 0.0043098 | -30.457 | -280.7755 | ok | 0.55049 | ok | 202.4242 | 0.033737 | 0.96626 | 6000 | 0 | 0 | 1 | 0.78231 | 167.5913 | 9.9 | 9.9 | 0.0065412 | 0.78496 | 24 | 0.15356 | 74.5543 | 3.4948 | 0.70688 | 6.6877 | 0.11369 | 0.098277 | 0.016366 | 0.46243 | 0.010057 | 0.0086207 | 0.001387 | 0.051724 | RTE_2024: 0.79385; RTE_2025: 0.77947; EFC_2024: 78.1818; EFC_2025: 124.2424; UTI_2024: 0.40373; UTI_2025: 0.55461 | LOW_ETA_AND_LOW_UTI
66795 | CISCO BESS | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Arbitrage | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.97453 | 0.83336 | 0.32643 | 0.0020468 |  |  | insufficient_history | -0.51149 | ok | 237.1717 | 0.039529 | 0.96047 | 6000 | 1 | 0 | 1 | 0.84184 | 150.3345 | 9.9 | 9.9 | 0.032316 | 0.83499 | 17 | 0.47463 | 107.0335 | 5.0172 | 1.0237 | 9.6012 | 0.11369 | 0.098277 | 0.016506 | 0.46243 | 0.010057 | 0.0086207 | 0.0013991 | 0.051724 | RTE_2024: 0.81972; RTE_2025: 0.83935; EFC_2024: 58.7879; EFC_2025: 178.3838; UTI_2024: 0.66631; UTI_2025: 0.80994
66799 | Bishop Ranch - BR 1-Y | CA | CISO | Distributed Solar Development, LLC | Distributed Solar Development, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Load Following, System Peak Shaving, Excess Wind and Solar Generation | 0.7 | 1.3 | 1.8571 | 1.5-2.5h | 2022 | 265 | C | FULL_OUTAGE | 0.92678 | 0.84462 | 0.17602 | 0.00082074 |  |  | insufficient_history |  | insufficient_history | 68.4615 | 0.01141 | 0.98859 | 6000 | 0 | 14 | 1 | 0.93333 | 29 | 0.7 | 0.7 | 0.0012322 | 0.84762 | 10 | 0.16426 | 0 | 0 | 0 | 0 | 0.066091 | 0.31344 | 0.030909 | 0.0011993 | 0.005698 | 0.031339 | 0.0026596 | 0.0001 | RTE_2024: 0.84762; EFC_2024: 68.4615; EFC_2025: 0; UTI_2024: 0.2088; UTI_2025: 0 | FULL_OUTAGE
66800 | Bishop Ranch - BR 8-P | CA | CISO | Distributed Solar Development, LLC | Distributed Solar Development, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
66801 | Fence Post Solar Hybrid Project, LLC | TX | ERCO | Fence Post Solar Project, LLC | Fence Post Solar Project, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 72 | 115 | 1.5972 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.84929 | 0.86834 | -0.091286 | -0.067425 |  |  | insufficient_history |  | insufficient_history | 334 | 0.055667 | 0.94433 | 6000 | 0 | 0 | 1 | 0.88779 | 0 | 70 | 70 | -0.065726 | 0.86771 | 16 | 0.16007 | 318.8763 | 69.7547 | 140.0346 | 155.7335 | 0.022471 | 0.086899 | 0.12645 | 0.47079 | 0.0018939 | 0.0075758 | 0.012097 | 0.05303 | RTE_2024: 0.88085; RTE_2025: 0.86419; EFC_2024: 71.5478; EFC_2025: 262.4522; UTI_2024: 0.86613; UTI_2025: 0.85448
66804 | Borden County BESS | TX | ERCO | Borden County Battery Energy Storage System LLC | Borden County Battery Energy Storage System LLC |  |  | FALSE |  | LIB | CT | Frequency Regulation, Load Following, Ramping / Spinning Reserve | 150 | 300 | 2 | 1.5-2.5h | 2024 |  |  | UNATTRIBUTED | 0.84592 | 0.81637 | 0.38362 | 0.0077051 |  |  | insufficient_history | -0.60524 | ok | 576.8 | 0.096133 | 0.90387 | 6000 | 1 | 0 | 1 | 0.84172 | 1046.4622 | 150 | 150 | 0.57543 | 0.81751 | 17 | 0.15608 | 1502.2214 | 328.6136 | 651.493 | 733.658 | 0.022471 | 0.086899 | 0.12508 | 0.47079 | 0.0018939 | 0.0075758 | 0.011947 | 0.05303 | RTE_2024: 0.80132; RTE_2025: 0.82326; EFC_2024: 148.0333; EFC_2025: 428.7667; UTI_2024: 1.4091; UTI_2025: 1.5684
66807 | SEPV Cuyama Hybrid | CA | CISO | SEPV Cuyama, LLC | SEPV Cuyama, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 3 | 12 | 4 | 2.5-4.5h | 2023 | 186 | C | HYBRID_ARTEFACT | 0.95478 | 0.94183 | 0.18645 | 0.00011364 | 1.2316 | 134.3966 | ok | -0.99206 | ok | 635.4167 | 0.1059 | 0.8941 | 6000 | 0 | 2 | 1 | 0.95265 | 116 | 3 | 3 | 0.0055936 | 0.94334 | 24 | 0.22599 | 72.1419 | 28.9321 | 22.3548 | 9.6471 | 0.03025 | 0.20169 | 0.12131 | 0.20982 | 0.0025597 | 0.018771 | 0.011537 | 0.019625 | RTE_2024: 0.94114; RTE_2025: 0.94488; EFC_2024: 261.1667; EFC_2025: 374.25; UTI_2024: 1.0716; UTI_2025: 1.2736 | PARTIAL_AVAILABILITY
66814 | Sky Ranch Solar | NM | PNM | Sky Ranch Solar and Storage | Sky Ranch Solar and Storage |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 50 | 200 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.8828 | 0.86146 | 0.41652 | -0.021973 |  |  | insufficient_history | -0.15117 | ok | 581.74 | 0.096957 | 0.90304 | 6000 | 0 | 0 | 1 | 0.86957 | 0 | 50 | 50 | 0.20826 | 0.86177 | 21 | 0.20184 | 2948.4825 | 161.2464 | 94.0874 | 231.4263 | 0.081309 | 0.081309 | 0.037841 | 0.31725 | 0.0070671 | 0.0070671 | 0.0032801 | 0.031802 | RTE_2024: 0.86308; RTE_2025: 0.86069; EFC_2024: 262.065; EFC_2025: 319.675; UTI_2024: 1.2856; UTI_2025: 1.1865
66871 | GulfStar Power, LLC | TX | ERCO | GulfStar Power, LLC | GulfStar Power, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation | 300 | 467 | 1.5567 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.79094 |  |  |  |  | insufficient_history |  | insufficient_history | 127.6552 | 0.021276 | 0.97872 | 6000 | 0 | 0 | 1 | 0.77877 | 0 | 300 | 300 |  |  |  |  | 1345.0769 | 294.2379 | 675.8382 | 656.9114 | 0.022471 | 0.086899 | 0.14204 | 0.47079 | 0.0018939 | 0.0075758 | 0.013841 | 0.05303 | RTE_2025: 0.79064; EFC_2025: 127.6552; UTI_2025: 0.85272
66872 | Estonian Solar Project, LLC | TX | ERCO | Enel Green Power Estonian Solar Project, LLC | Enel Green Power Estonian Solar Project, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 100 | 158.3 | 1.583 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.92713 | 0.83968 | 0.61689 | 0.011875 |  |  | insufficient_history |  | insufficient_history | 305.5148 | 0.050919 | 0.94908 | 6000 | 0 | 0 | 1 | 0.8756 | 0 | 100 | 100 | 0.61689 | 0.84718 | 11 | 0.88171 | 616.3459 | 134.8267 | 288.8652 | 301.0123 | 0.022471 | 0.086899 | 0.13379 | 0.47079 | 0.0018939 | 0.0075758 | 0.012911 | 0.05303 | RTE_2025: 0.84718; EFC_2025: 305.5148; UTI_2025: 1.2119
66881 | Pike County Energy Storage | IN | MISO | AES Pike County Energy Storage | AES Pike County Energy Storage |  |  | FALSE |  | OTH | CS | Arbitrage | 200 | 877 | 4.385 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 200 | 200
66885 | Baldy Mesa 2_Silver Peak Hybrid | CA | CISO | AES Clean Energy | AES Clean Energy |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 25 | 100 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.89896 | 0.83046 | 0.044109 | 0.18464 |  |  | insufficient_history |  | insufficient_history | 171.35 | 0.028558 | 0.97144 | 6000 | 2 | 0 | 1 | 0.33163 | 0 | 25 | 25 | 0.011027 | 0.89571 | 11 | 0.00010514 | 500.8436 | 91.3003 | 11.2707 | 72.7985 | 0.051638 | 0.16199 | 0.017052 | 0.35714 | 0.0044183 | 0.014728 | 0.0014461 | 0.036819 | RTE_2025: 0.67495; EFC_2025: 171.35; UTI_2025: 0.60861
66890 | SF Azalea, LLC | CA | CISO | Idemitsu Renewables | Idemitsu Renewables |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 38 | 152 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | [8 empty] | insufficient_history | 0.026316 | 4.386e-06 | 1 | 6000 | 0 | 0 | 1 | 0.8 | 0 | 38 | 38 |  |  |  |  | 1.2971 | 0.23645 | 0.029681 | 0.18854 | 0.051638 | 0.16199 | 0.017334 | 0.35714 | 0.0044183 | 0.014728 | 0.0014705 | 0.036819 | RTE_2025: 0.8; EFC_2025: 0.026316; UTI_2025: 0.0011016
66905 | Ables Springs Solar & Storage | TX | ERCO | Ables Springs Storage, LLC | Ables Springs Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 100 | 157.7 | 1.577 | 1.5-2.5h | 2025 | 354 | C | HYBRID_ARTEFACT | 0.76825 | 0.78374 | -0.049502 | 0.47155 |  |  | insufficient_history |  | insufficient_history | 173.9759 | 0.028996 | 0.971 | 6000 | 0 | 0 | 1 | 0.82016 | 0 | 100 | 100 | -0.049502 | 0.78119 | 12 | 0.0038047 | 314.1501 | 68.7209 | 145.2806 | 153.4253 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.78119; EFC_2025: 173.9759; UTI_2025: 0.60855 | LOW_ETA_AND_LOW_UTI
66925 | SR McNeal | AZ | TEPC | SR McNeal, LLC | SR McNeal, LLC |  |  | TRUE | pv_same_plant | LIB | BL |  | 20 | 20 | 1 | <1.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.92885 | 0.90846 | 0.30134 | -0.0011924 |  |  | insufficient_history | -0.4099 | ok | 2391.8 | 0.39863 | 0.60137 | 6000 | 0 | 0 | 1 | 0.91025 | 0 | 20 | 20 | 0.060269 | 0.91073 | 23 | 0.82291 | 3088.068 | 0.90069 | 108.9277 | 53.8627 | 0.20148 | 0.0011993 | 0.10328 | 0.20148 | 0.01875 | 0.0001 | 0.0096197 | 0.01875 | RTE_2024: 0.90908; RTE_2025: 0.91203; EFC_2024: 1051.3; EFC_2025: 1340.5; UTI_2024: 2.6745; UTI_2025: 3.8898
66926 | SMT Mercedes LLC | TX | ERCO | SMT Mercedes LLC | SMT Mercedes LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.9194 | 0.82315 | 0.21353 | -0.0084933 | -4.1984 | -38.3643 | ok | 2.3782 | ok | 387.9917 | 0.064665 | 0.93533 | 6000 | 7 | 0 | 1 | 0.84984 | 808.8216 | 10 | 10 | 0.021353 | 0.84282 | 24 | 0.76771 | 10.5643 | 2.8887 | 5.4452 | 10.6874 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.84493; RTE_2025: 0.84046; EFC_2024: 196.7; EFC_2025: 174.9; UTI_2024: 1.0563; UTI_2025: 0.82644
66927 | SMT Mission LLC | TX | ERCO | SMT Mission LLC | SMT Mission LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.94817 | 0.77621 | 0.27631 | -0.0013899 | 1.3719 | -7.7209 | ok | 5.0452 | ok | 295.1417 | 0.04919 | 0.95081 | 6000 | 7 | 0 | 1 | 0.82971 | 1393.349 | 10 | 10 | 0.027631 | 0.81377 | 24 | 0.93279 | 4.9715 | 1.3594 | 2.5625 | 5.0294 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.82368; RTE_2025: 0.80014; EFC_2024: 164.9; EFC_2025: 116.5; UTI_2024: 0.94233; UTI_2025: 0.41016
66928 | SMT Santa Rosa LLC | TX | ERCO | SMT Santa Rosa LLC | SMT Santa Rosa LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.9436 | 0.77342 | 0.25259 | -0.0024679 | 0.99471 | 2.314 | ok | 2.4862 | ok | 273.5583 | 0.045593 | 0.95441 | 6000 | 3 | 0 | 1 | 0.84615 | 1472.9316 | 10 | 10 | 0.025259 | 0.81025 | 24 | 0.93174 | 5.3966 | 1.4757 | 2.7816 | 5.4595 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.82331; RTE_2025: 0.79273; EFC_2024: 151.9; EFC_2025: 109; UTI_2024: 0.80549; UTI_2025: 0.419
66929 | SMT Alamo LLC | TX | ERCO | SMT Alamo LLC | SMT Alamo LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.93529 | 0.80812 | 0.23306 | -0.0046924 | -0.75336 | -3.5886 | ok | 1.2234 | ok | 323.725 | 0.053954 | 0.94605 | 6000 | 7 | 0 | 1 | 0.85079 | 1223.7807 | 10 | 10 | 0.023306 | 0.83087 | 24 | 0.71645 | 6.6068 | 1.8066 | 3.4054 | 6.6838 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.84143; RTE_2025: 0.81717; EFC_2024: 176.7; EFC_2025: 132.3; UTI_2024: 1.0031; UTI_2025: 0.51911
66930 | SMT Bay City LLC | TX | ERCO | SMT Bay City LLC | SMT Bay City LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.94559 | 0.81133 | 0.26993 | 0.0092351 | 1.1007 | 2.0734 | ok | 1.7463 | ok | 356.5667 | 0.059428 | 0.94057 | 6000 | 0 | 0 | 1.25 | 0.87097 | 979.0437 | 8 | 10 | 0.026993 | 0.8327 | 24 | 0.85601 | 9.7467 | 2.6651 | 5.0238 | 9.8602 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.8299; RTE_2025: 0.83555; EFC_2024: 165.4; EFC_2025: 163.6; UTI_2024: 0.83922; UTI_2025: 0.79626
66931 | SMT Elsa LLC | TX | ERCO | SMT Elsa LLC | SMT Elsa LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.94217 | 0.8027 | 0.27081 | -0.00025932 | -0.52483 | -8.1783 | ok | 0.48079 | ok | 351.15 | 0.058525 | 0.94148 | 6000 | 7 | 0 | 1.6667 | 0.84967 | 1040.2527 | 6 | 10 | 0.027081 | 0.83019 | 24 | 0.96594 | 7.1628 | 1.9586 | 3.692 | 7.2463 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.84306; RTE_2025: 0.8129; EFC_2024: 195; EFC_2025: 139.9; UTI_2024: 1.1301; UTI_2025: 0.58928
66932 | SMT Los Fresnos LLC | TX | ERCO | SMT Los Fresnos LLC | SMT Los Fresnos LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.97296 | 0.78186 | 0.27173 | -0.0030289 | 3.6254 | 3.2176 | ok | 3.3836 | ok | 255.525 | 0.042588 | 0.95741 | 6000 | 3 | 0 | 1 | 0.87815 | 1643.7092 | 10 | 10 | 0.027173 | 0.81578 | 24 | 0.91042 | 5.0696 | 1.3862 | 2.613 | 5.1286 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.8198; RTE_2025: 0.81058; EFC_2024: 138.3; EFC_2025: 105.7; UTI_2024: 0.82444; UTI_2025: 0.39901
66933 | SMT Harlingen II LLC | TX | ERCO | SMT Harlingen II LLC | SMT Harlingen II LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.93709 | 0.79642 | 0.27638 | -0.0011566 | 0.97327 | -5.4992 | ok | 1.3171 | ok | 335.05 | 0.055842 | 0.94416 | 6000 | 3 | 0 | 1 | 0.86601 | 928.6076 | 10 | 10 | 0.027638 | 0.82177 | 24 | 0.907 | 9.5177 | 2.6025 | 4.9058 | 9.6286 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.80781; RTE_2025: 0.83481; EFC_2024: 153; EFC_2025: 169.3; UTI_2024: 0.78408; UTI_2025: 0.75841
66934 | SMT Rio Grande I LLC | TX | ERCO | SMT Rio Grande I LLC | SMT Rio Grande I LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.9345 | 0.7945 | 0.25258 | -0.0030473 | -0.47421 | -5.7138 | ok | 3.0753 | ok | 313.85 | 0.052308 | 0.94769 | 6000 | 7 | 0 | 1.1765 | 0.84364 | 1183.1147 | 8.5 | 10 | 0.025258 | 0.82162 | 24 | 0.89526 | 6.3779 | 1.744 | 3.2874 | 6.4521 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.83486; RTE_2025: 0.80408; EFC_2024: 173.4; EFC_2025: 126; UTI_2024: 1.0332; UTI_2025: 0.52911
66935 | SMT Rio Grande II LLC | TX | ERCO | SMT Rio Grande II LLC | SMT Rio Grande II LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2023 |  |  | UNDER_DISPATCH | 0.9302 | 0.78793 | 0.2446 | -0.00065901 | -2.0629 | -23.0395 | ok | 0.89903 | ok | 313.3333 | 0.052222 | 0.94778 | 6000 | 7 | 0 | 1 | 0.85813 | 1305.2176 | 10 | 10 | 0.02446 | 0.81863 | 24 | 0.88605 | 6.4433 | 1.7618 | 3.3211 | 6.5183 | 0.010638 | 0.052071 | 0.074118 | 0.46223 | 0.00089127 | 0.0044563 | 0.0066817 | 0.051693 | RTE_2024: 0.83008; RTE_2025: 0.8031; EFC_2024: 174.4; EFC_2025: 124.4; UTI_2024: 0.8825; UTI_2025: 0.48075
66946 | Lockhart ESS, LLC | CA | CISO | Terra-Gen Operating Co-Solar | Terra-Gen Operating Co-Solar |  |  | FALSE |  | LIB | CS |  | 45 | 180 | 4 | 2.5-4.5h | 2024 | 126 | B | PARTIAL_AVAILABILITY | 0.90952 | 0.87343 | 0.72673 | 0.097731 |  |  | insufficient_history | -0.32857 | ok | 534.0056 | 0.089001 | 0.911 | 6000 | 4 | 2 | 1 | 0.87928 | 415.5 | 45 | 45 | 0.32703 | 0.87397 | 18 | 0.17787 | 1835.0753 | 334.5216 | 40.9258 | 266.7315 | 0.051638 | 0.16199 | 0.016902 | 0.35714 | 0.0044183 | 0.014728 | 0.0014332 | 0.036819 | RTE_2024: 0.85818; RTE_2025: 0.88072; EFC_2024: 157.0667; EFC_2025: 376.9389; UTI_2024: 1.2008; UTI_2025: 1.2712 | PARTIAL_AVAILABILITY
66949 | Sagebrush Solar 2 ESS 40 | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 40 | 160 | 4 | 2.5-4.5h | 2024 | 107 | B | UNATTRIBUTED | 0.80962 | 0.82268 | -0.20312 | -0.11905 |  |  | insufficient_history |  | insufficient_history | 377.725 | 0.062954 | 0.93705 | 6000 | 0 | 2 | 1 | 0.84869 | 4070.6915 | 40 | 40 | -0.081248 | 0.82041 | 16 | 0.021263 | 1340.8794 | 244.4331 | 29.9938 | 194.8992 | 0.051638 | 0.16199 | 0.016951 | 0.35714 | 0.0044183 | 0.014728 | 0.0014375 | 0.036819 | RTE_2024: 0.78215; RTE_2025: 0.83006; EFC_2024: 72.5687; EFC_2025: 305.1562; UTI_2024: 0.84456; UTI_2025: 1.0165 | PARTIAL_AVAILABILITY
66950 | Sagebrush Solar 2 ESS 59 | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 59 | 236 | 4 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 1.0923 | 0.83666 | 3.8251 | -0.67737 |  |  | insufficient_history |  | insufficient_history | 400.1314 | 0.066689 | 0.93331 | 6000 | 0 | 0 | 1 | 0.77763 | 6107.4834 | 59 | 59 | 2.2568 | 0.83764 | 16 | 0.26524 | 2118.9786 | 386.2752 | 47.3989 | 307.9974 | 0.051638 | 0.16199 | 0.016951 | 0.35714 | 0.0044183 | 0.014728 | 0.0014375 | 0.036819 | RTE_2024: 0.76436; RTE_2025: 0.86086; EFC_2024: 87.8686; EFC_2025: 312.2627; UTI_2024: 0.90607; UTI_2025: 1.0881
66951 | Scarlet II Hybrid | CA | CISO | EDPR Scarlet II LLC | EDPR Scarlet II LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 150 | 600 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.88298 | 0.78552 | 0.44627 | -0.15761 |  |  | insufficient_history |  | insufficient_history | 173.7133 | 0.028952 | 0.97105 | 6000 | 0 | 0 | 1 | 0.87272 | 0 | 150 | 150 | 0.66941 | 0.84415 | 12 | 0.49789 | 2946.6919 | 537.1617 | 66.2111 | 428.307 | 0.051638 | 0.16199 | 0.017026 | 0.35714 | 0.0044183 | 0.014728 | 0.001444 | 0.036819 | RTE_2024: 0.7958; RTE_2025: 0.84224; EFC_2024: 10.165; EFC_2025: 163.5483; UTI_2024: 0.4137; UTI_2025: 0.59421
66966 | Acton-Boxborough Schools BESS | MA | ISNE | MSS Energy Holdings, LLC (d.b.a. Calibrant Energy) | MSS Energy Holdings, LLC (d.b.a. Calibrant Energy) |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 2.1 | 4.3 | 2.0476 | 1.5-2.5h | 2021 | 283 | A | THERMAL_AUX | 0.85079 | 0.80049 | 0.17904 | -1.6102e-05 | 8.261 | 153.8496 | ok | -2.4797 | ok | 527.9845 | 0.087997 | 0.912 | 6000 | 0 | 2 | 1 | 0.82178 | 10.5 | 2.1 | 2.1 | 0.0037599 | 0.80518 | 24 | 0.44082 | 38.4924 | 1.1695 | 1.2902 | 0.1119 | 0.14392 | 0.082709 | 0.070323 | 0.025567 | 0.01295 | 0.0071942 | 0.0063132 | 0.0021583 | RTE_2024: 0.82363; RTE_2025: 0.79037; EFC_2024: 108.6047; EFC_2025: 129.7674; UTI_2024: 1.1618; UTI_2025: 1.4067 | THERMAL_AUX
66967 | Gateway BESS | NY | NYIS | Enel X North America, Inc | Enel X North America, Inc |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 4.8 | 16.4 | 3.4167 | 2.5-4.5h | 2019 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 2.5 |  |  | 1.6 | 4
67019 | Copperhead Solar, LLC | TX | ERCO | Geronimo Power | Geronimo Power |  |  | TRUE | pv_same_plant | LIB | CS | Ramping / Spinning Reserve, Voltage or Reactive Power Support | 100 | 100 | 1 | <1.5h | 2024 | 103 | C | HYBRID_ARTEFACT | 1.1024 | 0.83318 | 0.74848 | -0.14251 |  |  | insufficient_history |  | insufficient_history | 311.69 | 0.051948 | 0.94805 | 6000 | 0 | 2 | 1 | 0.88991 | 658 | 100 | 100 | 0.74848 | 0.84172 | 16 | 0.80508 | 1652.0059 | 77.4384 | 15.8464 | 148.1896 | 0.11369 | 0.098277 | 0.016554 | 0.46243 | 0.010057 | 0.0086207 | 0.0014032 | 0.051724 | RTE_2024: 0.7444; RTE_2025: 0.86428; EFC_2024: 51.87; EFC_2025: 259.82; UTI_2024: 0.88852; UTI_2025: 1.1652 | PARTIAL_AVAILABILITY
67036 | Davistown-Mercer | NC | PJM | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 2.5 | 5 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | 0.87008 | 0.80422 | 0.28957 | 0.00082743 |  |  | insufficient_history |  | insufficient_history | 192.4 | 0.032067 | 0.96793 | 6000 | 0 | 0 | 1 | 0.84834 | 595.746 | 2.5 | 2.5 | 0.0072393 | 0.82222 | 13 | 0.25244 | 93.7599 | 2.5231 | 0.98755 | 1.5315 | 0.18267 | 0.094486 | 0.029956 | 0.17213 | 0.016809 | 0.0082711 | 0.0025751 | 0.015742 | RTE_2024: 0.6; RTE_2025: 0.83111; EFC_2024: 5.4; EFC_2025: 187; UTI_2024: 0.24305; UTI_2025: 0.53552
67037 | Medoc | NC | PJM | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 2.5 | 5 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | 0.88561 | 0.78764 | 0.42192 | 0.0092264 |  |  | insufficient_history |  | insufficient_history | 206.8 | 0.034467 | 0.96553 | 6000 | 0 | 0 | 1 | 0.84043 | 552.4474 | 2.5 | 2.5 | 0.010548 | 0.82129 | 13 | 0.68881 | 104.8631 | 2.8219 | 1.1045 | 1.7129 | 0.18267 | 0.094486 | 0.029956 | 0.17213 | 0.016809 | 0.0082711 | 0.0025751 | 0.015742 | RTE_2024: 0.61702; RTE_2025: 0.82921; EFC_2024: 5.8; EFC_2025: 201; UTI_2024: 0.26106; UTI_2025: 0.69614
67039 | Northern Orchard Solar PV, LLC | CA | CISO | RWE Clean Energy | RWE Clean Energy |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 92 | 368 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.9483 |  |  |  |  | insufficient_history |  | insufficient_history | 161.4049 | 0.026901 | 0.9731 | 6000 | 0 | 0 | 1 | 0.94758 | 0 | 92 | 92 |  |  |  |  | 3727.2232 | 679.4471 | 84.6404 | 541.7586 | 0.051638 | 0.16199 | 0.017204 | 0.35714 | 0.0044183 | 0.014728 | 0.0014593 | 0.036819 | RTE_2025: 0.95078; EFC_2025: 161.4049; UTI_2025: 1.1828
67040 | Archie Horne | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 10 | 20 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | 0.87959 | 0.70122 | 0.38116 | 0.0059262 |  |  | insufficient_history |  | insufficient_history | 68.8 | 0.011467 | 0.98853 | 6000 | 0 | 0 | 1 | 0.76692 | 3370.1559 | 10 | 10 | 0.038116 | 0.71222 | 13 | 0.57768 | 29.1877 | 0.041342 | 0.051975 | 8.6547 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.71631; RTE_2025: 0.71189; EFC_2024: 5.05; EFC_2025: 63.75; UTI_2024: 0.2273; UTI_2025: 0.23934
67041 | McLauchin | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 15 | 30 | 2 | 1.5-2.5h | 2024 | 166 | A | UNATTRIBUTED | 0.78017 | 0.73534 | 0.1001 | 0.012813 |  |  | insufficient_history |  | insufficient_history | 60.9333 | 0.010156 | 0.98984 | 6000 | 0 | 0 | 1 | 0.77108 | 238.2556 | 15 | 15 | 0.015015 | 0.73532 | 13 | 0.077617 | 41.2312 | 0.058401 | 0.073421 | 12.2258 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.70886; RTE_2025: 0.73711; EFC_2024: 3.7333; EFC_2025: 57.2; UTI_2024: 0.16804; UTI_2025: 0.22934 | LOW_ETA_AND_LOW_UTI
67042 | Butler | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 10 | 20 | 2 | 1.5-2.5h | 2024 | 183 | A | UNATTRIBUTED | 0.83723 | 0.70263 | 0.27067 | 0.0033616 |  |  | insufficient_history |  | insufficient_history | 63.85 | 0.010642 | 0.98936 | 6000 | 0 | 0 | 1 | 0.77186 | 208.584 | 10 | 10 | 0.027067 | 0.71461 | 13 | 0.51491 | 25.9289 | 0.036726 | 0.046172 | 7.6884 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.73759; RTE_2025: 0.71264; EFC_2024: 5.2; EFC_2025: 58.65; UTI_2024: 0.23405; UTI_2025: 0.20858 | LOW_ETA_AND_LOW_UTI
67043 | Double Creek | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 | 210 | A | UNATTRIBUTED | 0.85318 | 0.6966 | 0.33538 | 0.00052362 |  |  | insufficient_history |  | insufficient_history | 71.4 | 0.0119 | 0.9881 | 6000 | 0 | 0 | 1 | 0.78417 | 110.9537 | 5 | 5 | 0.016769 | 0.71687 | 13 | 0.77898 | 13.602 | 0.019266 | 0.024221 | 4.0332 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.74468; RTE_2025: 0.71397; EFC_2024: 7; EFC_2025: 64.4; UTI_2024: 0.31507; UTI_2025: 0.21698 | LOW_ETA_AND_LOW_UTI
67044 | Fairfield Harbor | NC | CPLE | North Carolina El Member Corp | North Carolina El Member Corp |  |  | FALSE |  | LIB | CS | System Peak Shaving | 5 | 10 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | 0.88707 | 0.71586 | 0.35496 | 0.0013472 |  |  | insufficient_history |  | insufficient_history | 73.6 | 0.012267 | 0.98773 | 6000 | 0 | 0 | 1 | 0.77612 | 1764.5215 | 5 | 5 | 0.017748 | 0.73307 | 13 | 0.72503 | 16.5775 | 0.023481 | 0.02952 | 4.9155 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2024: 0.73239; RTE_2025: 0.73312; EFC_2024: 5.2; EFC_2025: 68.4; UTI_2024: 0.23405; UTI_2025: 0.25724
67083 | Longbow BESS, LLC | TX | ERCO | Longbow BESS, LLC | Longbow BESS, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 174 | 407.4 | 2.3414 | 1.5-2.5h | 2024 | 86 | A | UNATTRIBUTED | 0.85775 | 0.6415 | 0.26371 | -0.18753 |  |  | insufficient_history |  | insufficient_history | 238.3235 | 0.039721 | 0.96028 | 6000 | 0 | 0 | 1 | 0.83404 | 1094.3987 | 174 | 174 | 0.45886 | 0.82964 | 12 | 0.90637 | 1299.5529 | 284.2795 | 570.6991 | 634.6783 | 0.022471 | 0.086899 | 0.12645 | 0.47079 | 0.0018939 | 0.0075758 | 0.012097 | 0.05303 | RTE_2024: 0.13473; RTE_2025: 0.82964; EFC_2024: 0.26755; EFC_2025: 238.056; UTI_2024: 0.0017211; UTI_2025: 1.0014 | LOW_ETA_AND_LOW_UTI
67091 | Yellow Pine II | NV | NEVP | Yellow Pine Solar II, LLC | Yellow Pine Solar II, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Load Management | 85 | 340 | 4 | 2.5-4.5h | 2024 | 93 | C | HYBRID_ARTEFACT | 0.89506 | 0.88608 | 0.17304 | 0.21916 |  |  | insufficient_history | 1.07 | ok | 537.3118 | 0.089552 | 0.91045 | 6000 | 5 | 2 | 1 | 0.8876 | 945 | 65.8 | 65.8 | 0.14709 | 0.8862 | 19 | 0.03284 | 5226.3013 | 285.8156 | 167.9209 | 410.2123 | 0.081309 | 0.081309 | 0.038091 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033026 | 0.031802 | RTE_2024: 0.8859; RTE_2025: 0.88637; EFC_2024: 194.4029; EFC_2025: 342.9088; UTI_2024: 1.278; UTI_2025: 1.2302 | PARTIAL_AVAILABILITY
67092 | Paulsell | CA | CISO | Crow Creek Solar, LLC | Crow Creek Solar, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Ramping / Spinning Reserve | 15 | 60 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.91618 | 0.85461 | 0.69088 | 0.036714 |  |  | insufficient_history | 0.88963 | ok | 399.45 | 0.066575 | 0.93342 | 6000 | 0 | 0 | 1 | 0.88778 | 0 | 15 | 15 | 0.10363 | 0.86799 | 18 | 0.6771 | 492.4124 | 89.7634 | 10.9818 | 71.573 | 0.051638 | 0.16199 | 0.016902 | 0.35714 | 0.0044183 | 0.014728 | 0.0014332 | 0.036819 | RTE_2024: 0.85376; RTE_2025: 0.87257; EFC_2024: 95.55; EFC_2025: 303.9; UTI_2024: 0.59558; UTI_2025: 0.97383
67093 | Mojave 16/17/18 BESS | CA | CISO | Terra-Gen Operating Co-BESS 2 | Terra-Gen Operating Co-BESS 2 |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 77 | 77 | 1 | <1.5h | 2020 |  |  | UNDER_DISPATCH | 0.96233 | 0.87206 | 0.34267 | 0.043297 |  |  | insufficient_history | 0.38692 | ok | 1547.2974 | 0.25788 | 0.74212 | 6000 | 1 | 0 | 1 | 0.87347 | 90675.4089 | 77 | 77 | 0.26386 | 0.87318 | 22 | 0.31035 | 3820.1768 | 87.049 | 0.8755 | 5.5527 | 0.30232 | 0.13929 | 0.0011985 | 0.029554 | 0.03 | 0.0125 | 0.0001 | 0.0025 | RTE_2024: 0.8759; RTE_2025: 0.87067; EFC_2024: 250.2468; EFC_2025: 271.039; UTI_2024: 0.29182; UTI_2025: 0.31769
67119 | Ring Road | MA | ISNE | Greenbacker Renewable Energy Corporation | Greenbacker Renewable Energy Corporation |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 2 | 13.5 | 6.75 | >4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2 | 2
67122 | BRIGHT Battery | NE | SWPP | Omaha Public Power District | Omaha Public Power District |  |  | FALSE |  | LIB | CS | Voltage or Reactive Power Support | 1 | 2.4 | 2.4 | 1.5-2.5h | 2023 | 312 | A | UNATTRIBUTED | 0.81408 | 0.86429 | -0.24064 | -0.0010518 | -13.9563 | 11.9836 | ok | -0.45094 | ok | 433.3333 | 0.072222 | 0.92778 | 6000 | 0 | 0 | 1 | 0.88571 | 16.2748 | 1 | 1 | -0.0024064 | 0.84485 | 24 | 0.076424 | 19.5019 | 6.3991 | 0.023464 | 1.0205 | 0.066273 | 0.3373 | 0.0011985 | 0.18593 | 0.0057143 | 0.034286 | 0.0001 | 0.017143 | RTE_2024: 0.92453; RTE_2025: 0.80417; EFC_2024: 122.5; EFC_2025: 208.75; UTI_2024: 0.49362; UTI_2025: 0.86509 | LOW_ETA_AND_LOW_UTI
67162 | Groton BESS 2 | MA | ISNE | Groton BESS 2 LLC | Groton BESS 2 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 2 | 8.9 | 4.45 | 2.5-4.5h | 2024 | 200 | A | CAPACITY_FADE | 0.84758 | 0.74783 | 0.7353 | -0.0093476 |  |  | insufficient_history | -5.1021 | ok | 209.6629 | 0.034944 | 0.96506 | 6000 | 0 | 0 | 1 | 0.84 | 232.6436 | 2 | 2 | 0.014706 | 0.78043 | 19 | 0.89708 | 102.0772 | 11.1648 | 0.061058 | 0.01549 | 0.12884 | 0.24108 | 0.0011985 | 0.0011993 | 0.011494 | 0.022989 | 0.0001 | 0.0001 | RTE_2024: 0.72053; RTE_2025: 0.79732; EFC_2024: 42.5843; EFC_2025: 167.0787; UTI_2024: 0.23286; UTI_2025: 0.75971 | LOW_ETA_AND_LOW_UTI
67170 | Amazon SAN3 Solar Project | CA | CISO | Solar Star Prime 4 LLC | Solar Star Prime 4 LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 2.4 | 8.9 | 3.7083 | 2.5-4.5h | 2024 | 221 | C | HYBRID_ARTEFACT | 0.8399 | 0.8381 | -0.20728 | 0.0039716 |  |  | insufficient_history | -1.9757 | ok | 208.5393 | 0.034757 | 0.96524 | 6000 | 0 | 5 | 1 | 0.86243 | 71 | 2.4 | 2.4 | -0.0049746 | 0.86845 | 18 | 0.46071 | 37.616 | 6.8571 | 0.83393 | 5.4675 | 0.051638 | 0.16199 | 0.016803 | 0.35714 | 0.0044183 | 0.014728 | 0.0014247 | 0.036819 | RTE_2024: 0.85538; RTE_2025: 0.87048; EFC_2024: 54.4944; EFC_2025: 154.0449; UTI_2024: 0.20406; UTI_2025: 0.54863 | LOW_ETA_AND_LOW_UTI
67175 | Rodeo Ranch Energy Storage | TX | ERCO | Rodeo Ranch Energy Storage, LLC | Rodeo Ranch Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Voltage or Reactive Power Support | 300 | 600 | 2 | 1.5-2.5h | 2023 | 65 | A | UNATTRIBUTED | 0.83772 | 0.81511 | 0.18649 | 0.27522 |  |  | insufficient_history | -1.2615 | ok | 527.1586 | 0.08786 | 0.91214 | 6000 | 2 | 0 | 1 | 0.81522 | 2007.825 | 300 | 300 | 0.55946 | 0.81664 | 23 | 0.24682 | 2734.1874 | 448.5812 | 2190.5315 | 763.0446 | 0.031828 | 0.092476 | 0.27236 | 0.404 | 0.0026954 | 0.0080863 | 0.031409 | 0.043127 | RTE_2024: 0.81908; RTE_2025: 0.81466; EFC_2024: 227.135; EFC_2025: 279.375; UTI_2024: 1.0254; UTI_2025: 0.96259 | THERMAL_AUX
67178 | Mohave Energy - Hybrid | AZ | WALC | Mohave Energy | Mohave Energy |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Frequency Regulation, Co-Located Renewable Firming, Transmission and Distribution Deferral, System Peak Shaving, Load Management | 15 | 60 | 4 | 2.5-4.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 15 | 15
67183 | Franklin Battery Storage | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Backup Power | 60 | 240 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | 0.90515 | 0.88736 | 0.27636 | 0.222 |  |  | insufficient_history |  | insufficient_history | 342.7958 | 0.057133 | 0.94287 | 6000 | 0 | 0 | 4 | 0.89658 | 0 | 15 | 60 | 0.16582 | 0.88909 | 14 | 0.18962 | 3054.0355 | 167.0189 | 99.8431 | 239.7112 | 0.081309 | 0.081309 | 0.038731 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033604 | 0.031802 | RTE_2024: 0.91322; RTE_2025: 0.88448; EFC_2024: 56.475; EFC_2025: 286.3208; UTI_2024: 1.2523; UTI_2025: 1.1124
67185 | Groton BESS 1 | MA | ISNE | Groton BESS 1 LLC | Groton BESS 1 LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 2 | 8.9 | 4.45 | 2.5-4.5h | 2024 | 165 | B | CAPACITY_FADE | 0.86999 | 0.82364 | 0.41104 | 0.012093 |  |  | insufficient_history | -9.8387 | ok | 276.4045 | 0.046067 | 0.95393 | 6000 | 0 | 2 | 1 | 0.841 | 224.3438 | 2 | 2 | 0.0082207 | 0.84218 | 18 | 0.65298 | 138.7744 | 15.1786 | 0.083008 | 0.021059 | 0.12884 | 0.24108 | 0.0011985 | 0.0011993 | 0.011494 | 0.022989 | 0.0001 | 0.0001 | RTE_2024: 0.83636; RTE_2025: 0.84406; EFC_2024: 67.191; EFC_2025: 209.2135; UTI_2024: 0.96101; UTI_2025: 0.86572 | PARTIAL_AVAILABILITY
67186 | Holden BESS 1 | MA | ISNE | Holden BESS 1 LLC | Holden BESS 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 5 | 22.4 | 4.48 | 2.5-4.5h | 2024 |  |  | CAPACITY_FADE | 0.88289 | 0.85564 | 0.14157 | 0.0033982 |  |  | insufficient_history | -10.8663 | ok | 255.8036 | 0.042634 | 0.95737 | 6000 | 0 | 0 | 1 | 0.87478 | 22.5018 | 5 | 5 | 0.0070787 | 0.87082 | 17 | 0.93814 | 352.6304 | 38.5693 | 0.21093 | 0.053511 | 0.12884 | 0.24108 | 0.0011985 | 0.0011993 | 0.011494 | 0.022989 | 0.0001 | 0.0001 | RTE_2024: 0.85038; RTE_2025: 0.87308; EFC_2024: 24.8661; EFC_2025: 230.9375; UTI_2024: 0.56217; UTI_2025: 1.2207
67187 | Paxton BESS 1 | MA | ISNE | Paxton BESS 1 LLC | Paxton BESS 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 3 | 8.9 | 2.9667 | 2.5-4.5h | 2024 | 278 | A | PARTIAL_AVAILABILITY | 0.90261 | 0.85437 | 0.5418 | 0.0038524 |  |  | insufficient_history |  | insufficient_history | 295.9551 | 0.049326 | 0.95067 | 6000 | 0 | 4 | 1 | 0.875 | 14 | 3 | 3 | 0.016254 | 0.8577 | 13 | 0.65818 | 179.2678 | 19.6076 | 0.10723 | 0.027203 | 0.12884 | 0.24108 | 0.0011985 | 0.0011993 | 0.011494 | 0.022989 | 0.0001 | 0.0001 | RTE_2024: 0.82332; RTE_2025: 0.86119; EFC_2024: 26.1798; EFC_2025: 269.7753; UTI_2024: 1.2091; UTI_2025: 1.4454 | PARTIAL_AVAILABILITY
67236 | Anemoi Energy Storage | TX | ERCO | Anemoi Energy Storage, LLC | Anemoi Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Backup Power | 200 | 400 | 2 | 1.5-2.5h | 2024 | 45 | A | UNATTRIBUTED | 0.83064 | 0.7805 | 0.39797 | 0.2792 |  |  | insufficient_history | 0.11386 | ok | 398.85 | 0.066475 | 0.93352 | 6000 | 6 | 2 | 1 | 0.81692 | 4614.322 | 200 | 200 | 0.79594 | 0.78667 | 19 | 0.65538 | 1292.5332 | 282.7439 | 1686.1796 | 631.25 | 0.022471 | 0.086899 | 0.29966 | 0.47079 | 0.0018939 | 0.0075758 | 0.035937 | 0.05303 | RTE_2024: 0.76641; RTE_2025: 0.79616; EFC_2024: 123.83; EFC_2025: 275.02; UTI_2024: 0.83517; UTI_2025: 0.96524 | THERMAL_AUX
67237 | Ebony Energy Storage | TX | ERCO | Ebony Energy Storage, LLC | Ebony Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Backup Power | 207.9 | 400 | 1.924 | 1.5-2.5h | 2024 | 76 | A | UNATTRIBUTED | 0.7669 | 0.80266 | -0.32787 | 0.25505 |  |  | insufficient_history | -1.1593 | ok | 449.145 | 0.074857 | 0.92514 | 6000 | 1 | 0 | 1 | 0.81555 | 2910.4212 | 200 | 200 | -0.68163 | 0.80018 | 19 | 0.29956 | 1465.2462 | 320.5252 | 1911.4931 | 715.6 | 0.022471 | 0.086899 | 0.29966 | 0.47079 | 0.0018939 | 0.0075758 | 0.035937 | 0.05303 | RTE_2024: 0.79464; RTE_2025: 0.80291; EFC_2024: 146.915; EFC_2025: 302.23; UTI_2024: 1.0114; UTI_2025: 1.1044 | THERMAL_AUX
67241 | 401 South | MA | SOCO | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 1 | 2 | 2 | 1.5-2.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
67242 | 5 Berry | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 3 | 7.5 | 2.5 | 2.5-4.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
67275 | White Plains_RFP-Gedney Way Landfill | NY | NYIS | Distributed Solar Development, LLC | Distributed Solar Development, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 1.3 | 5.1 | 3.9231 | 2.5-4.5h | 2022 | 308 | C | HYBRID_ARTEFACT | 0.76887 | 0.71082 | -0.021177 | 0.00019487 |  |  | ok |  | insufficient_history | 66.5196 | 0.011087 | 0.98891 | 6000 | 0 | 6 | 1 | 0.87179 | 5.5 | 1.3 | 1.3 | -0.0002753 | 0.86641 | 12 | 0.089488 | 0 | 0 | 0 | 0 | 0.26632 | 0.0011993 | 0.0011985 | 0.20726 | 0.025806 | 0.0001 | 0.0001 | 0.019355 | RTE_2023: 0.86667; RTE_2024: 0.5625; RTE_2025: 0.61111; EFC_2023: 28.0392; EFC_2024: 8.8235; EFC_2025: 8.6275; UTI_2023: 0.0085739; UTI_2024: 0; UTI_2025: 0 | LOW_ETA_AND_LOW_UTI
67276 | Upland | MA | ISNE | Greenbacker Renewable Energy Corporation | Greenbacker Renewable Energy Corporation |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 2.3 | 5.4 | 2.3478 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2.3 | 2.3
67277 | Bishop Ranch - BR 15-DD | CA | CISO | Alcosta Boulevard BR 15-DD Solar Project 2020, LLC | Alcosta Boulevard BR 15-DD Solar Project 2020, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
67278 | Bishop Ranch - BR 2600 | CA | CISO | Camino Ramon BR 2600 Solar Project 2020, LLC | Camino Ramon BR 2600 Solar Project 2020, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 1.1 | 2.1 | 1.9091 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.67857 |  |  |  |  | insufficient_history |  | insufficient_history | 6.6667 | 0.0011111 | 0.99889 | 6000 | 0 | 1 | 1 | 0.85714 | 0 | 1.1 | 1.1 |  |  |  |  | 8.0801 | 0.00080276 | 0.0010092 | 0.093957 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.77778; EFC_2025: 6.6667; UTI_2025: 0.034664
67281 | FFP - NY Urbanski | NY | NYIS | FFP NY Goshen Project1, LLC | FFP NY Goshen Project1, LLC |  |  | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming | 4 | 10.5 | 2.625 | 2.5-4.5h | 2024 | 313 | C | HYBRID_ARTEFACT |  | 0.56885 |  |  |  |  | insufficient_history |  | insufficient_history | 7.4286 | 0.0012381 | 0.99876 | 6000 | 0 | 5 | 1 | 0.63043 | 1.5 | 4 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 0.38122 | 0.0011993 | 0.0011985 | 0.27385 | 0.04 | 0.0001 | 0.0001 | 0.026667 | RTE_2024: 0.66055; RTE_2025: 0.3; EFC_2024: 6.8571; EFC_2025: 0.57143; UTI_2024: 0.02285; UTI_2025: 0 | FULL_OUTAGE
67282 | FFP - NY Varano | NY | NYIS | FFP NY Goshen Project2, LLC | FFP NY Goshen Project2, LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming | 5 | 10.5 | 2.1 | 1.5-2.5h | 2024 | 300 | C | HYBRID_ARTEFACT |  | 0.62752 |  |  |  |  | insufficient_history |  | insufficient_history | 24.6667 | 0.0041111 | 0.99589 | 6000 | 0 | 7 | 1 | 0.88235 | 4 | 5 | 5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.18267 | 0.094486 | 0.029572 | 0.17213 | 0.016809 | 0.0082711 | 0.002541 | 0.015742 | RTE_2024: 0.61345; RTE_2025: 0.82301; EFC_2024: 6.9524; EFC_2025: 17.7143; UTI_2024: 0.0070589; UTI_2025: 0 | FULL_OUTAGE
67284 | Ganado Solar | TX | ERCO | Enel Green Power NA, Inc. | Enel Green Power NA, Inc. |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 70.5 | 115 | 1.6312 | 1.5-2.5h | 2024 | 125 | C | HYBRID_ARTEFACT | 0.83054 | 0.78471 | 0.25202 | 0.20721 |  |  | insufficient_history | -3.4281 | ok | 473.2261 | 0.078871 | 0.92113 | 6000 | 0 | 2 | 1 | 0.85403 | 427.5 | 70 | 70 | 0.17767 | 0.80889 | 22 | 0.58328 | 425.8402 | 93.1533 | 173.865 | 207.9727 | 0.022471 | 0.086899 | 0.11864 | 0.47079 | 0.0018939 | 0.0075758 | 0.011247 | 0.05303 | RTE_2024: 0.79295; RTE_2025: 0.8181; EFC_2024: 170.0087; EFC_2025: 303.2174; UTI_2024: 0.69183; UTI_2025: 1.1522 | LOW_ETA_AND_LOW_UTI
67285 | Sun Streams 3 | AZ | AZPS | Sun Streams PVS, LLC | Sun Streams PVS, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Load Following, Co-Located Renewable Firming | 215 | 860 | 4 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.8991 | 0.85891 | 0.60648 | 1.2399 |  |  | insufficient_history | -2.6585 | ok | 507.4221 | 0.08457 | 0.91543 | 6000 | 7 | 0 | 1 | 0.88605 | 0 | 215 | 215 | 1.3039 | 0.86713 | 19 | 0.81546 | 173.7685 | 9.503 | 11.9471 | 770.5698 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2024: 0.84678; RTE_2025: 0.87859; EFC_2024: 178.4407; EFC_2025: 328.9814; UTI_2024: 1.3296; UTI_2025: 0.99068
67288 | Foster Clean Power A | CA | CISO | Foster Clean Power A, LLC | Foster Clean Power A, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, Frequency Regulation, System Peak Shaving | 1.3 | 5.2 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.3 | 1.3
67291 | Sun Streams 4 | AZ | AZPS | Sun Streams Expansion, LLC | Sun Streams Expansion, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming | 300 | 1200 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.83528 | 0.88079 | -0.82576 | 1.7011 |  |  | insufficient_history |  | insufficient_history | 258.5217 | 0.043087 | 0.95691 | 6000 | 3 | 0 | 1 | 0.88698 | 0 | 300 | 300 | -2.4773 | 0.87832 | 10 | 0.22795 | 248.5757 | 13.5941 | 17.0903 | 1102.2995 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.87832; EFC_2025: 258.5217; UTI_2025: 0.94594
67296 | CVEC Round 4 Brewster Captn Golf Course | MA | ISNE | Freemans Way Solar Project 2019, LLC | Freemans Way Solar Project 2019, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, System Peak Shaving, Excess Wind and Solar Generation | 0.4 | 0.9 | 2.25 | 1.5-2.5h | 2022 | 297 | C | HYBRID_ARTEFACT | 0.85246 | 0.85338 | 0.040113 | -0.0001502 |  |  | ok | 0 | ok | 160 | 0.026667 | 0.97333 | 6000 | 0 | 2 | 1 | 0.90909 | 4.5 | 0.4 | 0.4 | 0.00016045 | 0.832 | 33 | 0.016332 | 1.1417 | 0.026759 | 0.010351 | 0.0085344 | 0.17028 | 0.076884 | 0.024013 | 0.076884 | 0.015556 | 0.0066667 | 0.0020513 | 0.0066667 | RTE_2023: 0.87273; RTE_2024: 0.81132; RTE_2025: 0.72222; EFC_2023: 53.3333; EFC_2024: 47.7778; EFC_2025: 14.4444; UTI_2023: 0.17664; UTI_2024: 0.43104; UTI_2025: 0.14334 | LOW_ETA_AND_LOW_UTI
67299 | Pome BESS | CA | CISO | Pome BESS LLC | MN8 Energy LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 100 | 400 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.75286 |  |  |  |  | insufficient_history |  | insufficient_history | 64.7125 | 0.010785 | 0.98921 | 6000 | 0 | 0 | 1 | 0.89522 | 5505.875 | 100 | 100 |  |  |  |  | 3342.9566 | 609.398 | 76.2619 | 485.9048 | 0.051638 | 0.16199 | 0.017282 | 0.35714 | 0.0044183 | 0.014728 | 0.001466 | 0.036819 | RTE_2025: 0.7661; EFC_2025: 64.7125; UTI_2025: 1.0702
67300 | Rattlesnake Ridge Battery Storage | CO | WACM | Ameresco | Rattlesnake Ridge Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 11.8 | 47 | 3.9831 | 2.5-4.5h | 2024 |  |  | CAPACITY_FADE | 0.87957 | 0.82995 | 0.74213 | 0.017123 |  |  | insufficient_history | -5.0444 | ok | 379.3404 | 0.063223 | 0.93678 | 6000 | 0 | 0 | 1 | 0.53119 | 1337.6307 | 11.8 | 11.8 | 0.087571 | 0.82611 | 19 | 0.12737 | 545.9192 | 29.8552 | 17.5404 | 42.8492 | 0.081309 | 0.081309 | 0.038091 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033026 | 0.031802 | RTE_2024: 0.87294; RTE_2025: 0.79785; EFC_2024: 150.8511; EFC_2025: 228.4894; UTI_2024: 0.97375; UTI_2025: 0.97941
67301 | Parkway Battery Storage | CO | PSCO | Ameresco | Parkway Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 7.8 | 31.3 | 4.0128 | 2.5-4.5h | 2024 |  |  | CAPACITY_FADE | 0.87973 | 0.88239 | -0.0089037 | 0.024673 |  |  | insufficient_history | -6.5818 | ok | 456.4217 | 0.07607 | 0.92393 | 6000 | 0 | 0 | 1 | 0.89979 | 32.5545 | 7.8 | 7.8 | -0.00069449 | 0.88711 | 20 | 0.0035878 | 427.1397 | 23.3594 | 13.6769 | 33.5262 | 0.081309 | 0.081309 | 0.037966 | 0.31725 | 0.0070671 | 0.0070671 | 0.0032913 | 0.031802 | RTE_2024: 0.88229; RTE_2025: 0.88984; EFC_2024: 164.2812; EFC_2025: 292.1406; UTI_2024: 1.1237; UTI_2025: 1.1256
67302 | Frederick Battery Storage | CO | WACM | Ameresco | Frederick Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 7.8 | 31.3 | 4.0128 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.88253 | 0.82586 | 0.17196 | -0.003649 |  |  | insufficient_history |  | insufficient_history | 286.9968 | 0.047833 | 0.95217 | 6000 | 0 | 0 | 1 | 0.90057 | 1645.727 | 7.8 | 7.8 | 0.013412 | 0.8765 | 14 | 0.25751 | 375.2708 | 20.5228 | 12.2256 | 29.455 | 0.081309 | 0.081309 | 0.038602 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033487 | 0.031802 | RTE_2024: 0.87624; RTE_2025: 0.87126; EFC_2024: 70.3514; EFC_2025: 216.6454; UTI_2024: 1.0003; UTI_2025: 0.96086
67303 | Mead Battery Storage | CO | WACM | Ameresco | Mead Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 7.8 | 31.3 | 4.0128 | 2.5-4.5h | 2024 | 81 | A | UNATTRIBUTED | 0.95589 | 0.83089 | 1.0896 | 0.016152 |  |  | insufficient_history | 0.20382 | ok | 392.5559 | 0.065426 | 0.93457 | 6000 | 0 | 0 | 1 | 0.889 | 1200.106 | 7.8 | 7.8 | 0.084987 | 0.87765 | 18 | 0.81563 | 391.0908 | 21.3879 | 12.5657 | 30.6967 | 0.081309 | 0.081309 | 0.038091 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033026 | 0.031802 | RTE_2024: 0.88012; RTE_2025: 0.87157; EFC_2024: 162.0767; EFC_2025: 230.4792; UTI_2024: 0.9492; UTI_2025: 0.96142 | ELEVATED_P_AUX
67304 | Davis Battery Storage | CO | WACM | Ameresco | Davis UP Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 11.8 | 47 | 3.9831 | 2.5-4.5h | 2024 | 97 | A | UNATTRIBUTED | 0.98656 | 0.86829 | 1.5506 | 0.0022484 |  |  | insufficient_history |  | insufficient_history | 363.5957 | 0.060599 | 0.9394 | 6000 | 0 | 0 | 1 | 0.89714 | 782.2709 | 11.8 | 11.8 | 0.18298 | 0.87784 | 16 | 0.96496 | 575.2251 | 31.4579 | 18.6747 | 45.1494 | 0.081309 | 0.081309 | 0.038473 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033371 | 0.031802 | RTE_2024: 0.87708; RTE_2025: 0.87814; EFC_2024: 102.0213; EFC_2025: 261.5745; UTI_2024: 0.99911; UTI_2025: 1.0169 | ELEVATED_P_AUX
67305 | Bromley Battery Storage | CO | WACM | Ameresco | Bromley Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 11.8 | 47 | 3.9831 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.93195 | 0.87707 | 0.70664 | -0.014349 |  |  | insufficient_history | 1.046 | ok | 401.0638 | 0.066844 | 0.93316 | 6000 | 0 | 0 | 1 | 0.89441 | 1441.8112 | 11.8 | 11.8 | 0.083384 | 0.88323 | 18 | 0.78756 | 610.7552 | 33.4009 | 19.6913 | 47.9382 | 0.081309 | 0.081309 | 0.038218 | 0.31725 | 0.0070671 | 0.0070671 | 0.003314 | 0.031802 | RTE_2024: 0.88383; RTE_2025: 0.88292; EFC_2024: 140.0213; EFC_2025: 261.0426; UTI_2024: 0.99757; UTI_2025: 1.0193
67306 | Keenesburg Battery Storage | CO | WACM | Ameresco | Keenesburg Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 11.8 | 47 | 3.9831 | 2.5-4.5h | 2024 |  |  | UNATTRIBUTED | 0.92637 | 0.87424 | 0.68013 | -0.050444 |  |  | insufficient_history | 0.69225 | ok | 432.8298 | 0.072138 | 0.92786 | 6000 | 0 | 0 | 1 | 0.8863 | 1660.5488 | 11.8 | 11.8 | 0.080256 | 0.88199 | 19 | 0.61124 | 627.6126 | 34.3228 | 20.1652 | 49.2613 | 0.081309 | 0.081309 | 0.038091 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033026 | 0.031802 | RTE_2024: 0.88263; RTE_2025: 0.88152; EFC_2024: 181.1277; EFC_2025: 251.7021; UTI_2024: 1.0727; UTI_2025: 1.0418
67307 | Platte Valley Battery Storage | CO | PSCO | Ameresco | Platte Valley Energy Storage LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving | 7.8 | 31.3 | 4.0128 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.87847 | 0.89422 | -0.16848 | -0.0045098 |  |  | insufficient_history | -0.4685 | ok | 390.4473 | 0.065075 | 0.93493 | 6000 | 0 | 0 | 1 | 0.89059 | 1689.0599 | 7.8 | 7.8 | -0.013141 | 0.89003 | 17 | 0.52035 | 436.2167 | 23.8558 | 14.064 | 34.2386 | 0.081309 | 0.081309 | 0.038218 | 0.31725 | 0.0070671 | 0.0070671 | 0.003314 | 0.031802 | RTE_2024: 0.88313; RTE_2025: 0.89303; EFC_2024: 122.3962; EFC_2025: 268.0511; UTI_2024: 1.0649; UTI_2025: 1.0893
67321 | Yuma Solar + Storage | AZ | AZPS | Invenergy Services LLC | Invenergy Services LLC |  |  | TRUE | pv_same_plant | LIB | CS | Voltage or Reactive Power Support, Excess Wind and Solar Generation | 70 | 268 | 3.8286 | 2.5-4.5h | 2025 | 367 | C | HYBRID_ARTEFACT | 0.97884 | 0.89949 | 1.1406 | -0.019146 |  |  | insufficient_history |  | insufficient_history | 251.8619 | 0.041977 | 0.95802 | 6000 | 4 | 0 | 1 | 0.9269 | 0 | 67 | 67 | 0.79839 | 0.90341 | 10 | 0.16672 | 47.5889 | 2.6025 | 3.2719 | 211.0312 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.90341; EFC_2025: 251.8619; UTI_2025: 0.85264 | ELEVATED_P_AUX
67322 | Mamm Creek | CO | PSCO | AES Clean Energy | AES Clean Energy |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 11.2 | 20 | 1.7857 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
67323 | High Mesa CO | CO | PSCO | AES Clean Energy | AES Clean Energy |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 11.2 | 20 | 1.7857 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.86464 |  |  |  |  | insufficient_history |  | insufficient_history | 110 | 0.018333 | 0.98167 | 6000 | 0 | 0 | 1 | 0.89703 | 0 | 10 | 10 |  |  |  |  | 307.3389 | 8.4039 | 0.10143 | 5.3607 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2025: 0.85703; EFC_2025: 110; UTI_2025: 0.50459
67328 | Pluto Energy Storage | AZ | AZPS | Pluto Energy Storage, LLC | Pluto Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Load Management | 75 | 300 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.7766 |  |  |  |  | insufficient_history |  | insufficient_history | 143.5167 | 0.023919 | 0.97608 | 6000 | 2 | 0 | 1 | 0.83741 | 12370.2421 | 75 | 75 |  |  |  |  | 58.965 | 3.2247 | 4.054 | 261.4782 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.7797; EFC_2025: 143.5167; UTI_2025: 0.89682
67454 | Scatter Wash 1 | AZ | AZPS | Scatter Wash Energy Storage, LLC | Scatter Wash Energy Storage, LLC |  |  | FALSE |  | LIB | CS |  | 170 | 680 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.88122 |  |  |  |  | insufficient_history |  | insufficient_history | 237.8956 | 0.039649 | 0.96035 | 6000 | 3 | 0 | 1 | 0.89152 | 0 | 170 | 170 |  |  |  |  | 150.275 | 8.2182 | 10.3319 | 666.3886 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.88138; EFC_2025: 237.8956; UTI_2025: 1.1706
67455 | Scatter Wash 2 | AZ | AZPS | Scatter Wash Energy Storage, LLC | Scatter Wash Energy Storage, LLC |  |  | FALSE |  | LIB | CS |  | 85 | 340 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.88542 |  |  |  |  | insufficient_history |  | insufficient_history | 237.1706 | 0.039528 | 0.96047 | 6000 | 3 | 0 | 1 | 0.88848 | 0 | 85 | 85 |  |  |  |  | 74.7558 | 4.0882 | 5.1397 | 331.5019 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.88594; EFC_2025: 237.1706; UTI_2025: 1.1799
67457 | 665 Scenic Highway | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 1.5 | 31 | 20.6667 | >4.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
67464 | 1 Commercial | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 1 | 2 | 2 | 1.5-2.5h | 2023 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
67474 | Harquahala 2 | AZ | AZPS | Copia Power | Copia Power |  |  | TRUE | pv_same_plant | LIB | CS |  | 300 | 1200 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.89549 |  |  |  |  | insufficient_history |  | insufficient_history | 274.8667 | 0.045811 | 0.95419 | 6000 | 3 | 0 | 1.0108 | 0.8973 | 0 | 37.1 | 37.5 |  |  |  |  | 234.5831 | 12.8289 | 16.1283 | 1040.2497 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.89485; EFC_2025: 274.8667; UTI_2025: 0.93927
67489 | Cavalry Solar Hybrid | IN | MISO | Cavalry Energy Center LLC | Cavalry Energy Center LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Backup Power | 45 | 180 | 4 | 2.5-4.5h | 2024 | 63 | C | HYBRID_ARTEFACT | 0.89248 | 0.90451 | -0.11632 | 0.12071 |  |  | insufficient_history | -1.8859 | ok | 691.1944 | 0.1152 | 0.8848 | 6000 | 0 | 3 | 0.25111 | 0.88087 | 1925 | 45 | 11.3 | -0.052344 | 0.89832 | 20 | 0.014033 | 6660.7653 | 728.527 | 3.7094 | 348.5355 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2024: 0.95993; RTE_2025: 0.87283; EFC_2024: 216.1444; EFC_2025: 475.05; UTI_2024: 1.2826; UTI_2025: 1.7063 | PARTIAL_AVAILABILITY
67493 | Pavlov | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.93865 | 0.80435 | 0.2421 | -0.002368 |  |  | insufficient_history | -2.7719 | ok | 196.8687 | 0.032811 | 0.96719 | 6000 | 0 | 0 | 1 | 0.83051 | 414.8251 | 9.9 | 9.9 | 0.023968 | 0.82132 | 17 | 0.97835 | 95.5919 | 4.4809 | 0.9156 | 8.5749 | 0.11369 | 0.098277 | 0.01653 | 0.46243 | 0.010057 | 0.0086207 | 0.0014011 | 0.051724 | RTE_2024: 0.77292; RTE_2025: 0.8336; EFC_2024: 37.4747; EFC_2025: 159.3939; UTI_2024: 0.44875; UTI_2025: 0.72278
67494 | Mainland | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | CAPACITY_FADE | 0.94286 | 0.76826 | 0.267 | 0.0038629 |  |  | insufficient_history | -10.7117 | ok | 196.0606 | 0.032677 | 0.96732 | 6000 | 0 | 0 | 1 | 0.82759 | 131.4125 | 9.9 | 9.9 | 0.026433 | 0.79387 | 20 | 0.93971 | 93.3775 | 4.3771 | 0.89049 | 8.3762 | 0.11369 | 0.098277 | 0.016459 | 0.46243 | 0.010057 | 0.0086207 | 0.001395 | 0.051724 | RTE_2024: 0.68611; RTE_2025: 0.8276; EFC_2024: 40.404; EFC_2025: 155.6566; UTI_2024: 0.29138; UTI_2025: 0.698
67495 | Russek | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH | 0.90479 | 0.8504 | 0.071334 | -0.0099551 |  |  | insufficient_history |  | insufficient_history | 242.2222 | 0.04037 | 0.95963 | 6000 | 1 | 1 | 1 | 0.87225 | 305.5 | 9.9 | 9.9 | 0.0070621 | 0.87042 | 16 | 0.65852 | 128.8092 | 6.038 | 1.2338 | 11.5546 | 0.11369 | 0.098277 | 0.01653 | 0.46243 | 0.010057 | 0.0086207 | 0.0014011 | 0.051724 | RTE_2024: 0.82727; RTE_2025: 0.87629; EFC_2024: 27.5758; EFC_2025: 214.6465; UTI_2024: 0.1; UTI_2025: 0.98438
67496 | Sandlake | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2024 | 372 | A | PARTIAL_AVAILABILITY | 0.90067 | 0.89055 | 0.026213 | -0.0018094 |  |  | insufficient_history | -3.4927 | ok | 275.5556 | 0.045926 | 0.95407 | 6000 | 1 | 4 | 1 | 0.87838 | 0 | 9.9 | 9.9 | 0.0025951 | 0.89092 | 17 | 0.11316 | 121.4276 | 5.692 | 1.1631 | 10.8924 | 0.11369 | 0.098277 | 0.01653 | 0.46243 | 0.010057 | 0.0086207 | 0.0014011 | 0.051724 | RTE_2024: 0.87167; RTE_2025: 0.89803; EFC_2024: 72.7273; EFC_2025: 202.8283; UTI_2024: 1.0469; UTI_2025: 0.92248 | PARTIAL_AVAILABILITY
67498 | McFarland C | AZ | CISO | AES Clean Energy | AES Clean Energy |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 185 | 740 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.90235 |  |  |  |  | insufficient_history |  | insufficient_history | 154.4432 | 0.025741 | 0.97426 | 6000 | 4 | 0 | 1 | 0.94089 | 257.4251 | 185 | 185 |  |  |  |  | 5362.2205 | 977.4959 | 121.5843 | 779.4084 | 0.051638 | 0.16199 | 0.017179 | 0.35714 | 0.0044183 | 0.014728 | 0.0014571 | 0.036819 | RTE_2025: 0.90526; EFC_2025: 154.4432; UTI_2025: 0.8234
67503 | Serrano | AZ | AZPS | Serrano Solar, LLC | Serrano Solar, LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming | 213.8 | 855 | 3.9991 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.92667 |  |  |  |  | insufficient_history |  | insufficient_history | 230.8655 | 0.038478 | 0.96152 | 6000 | 2 | 0 | 2.138 | 0.91427 | 0 | 100 | 213.8 |  |  |  |  | 180.5061 | 9.8715 | 12.4103 | 800.4474 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2025: 0.92139; EFC_2025: 230.8655; UTI_2025: 0.97602
67528 | Milagro Solar I | NM | EPE | Milagro Solar I, LLC | Milagro Solar I, LLC |  |  | TRUE | pv_same_plant | LIB | CT | Frequency Regulation, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 75 | 300 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 15 | 15
67545 | Marshall Solar Plus LLC | MN | MISO | Western Minnesota Mun Pwr Agny | Western Minnesota Mun Pwr Agny |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 5 | 30.6 | 6.12 | >4.5h | 2024 | 360 | C | HYBRID_ARTEFACT | 0.97272 | 0.70073 | 2.8179 | 0.018856 |  |  | insufficient_history |  | insufficient_history | 196.732 | 0.032789 | 0.96721 | 6000 | 0 | 0 | 1 | 0.85836 | 0 | 5 | 5 | 0.1409 | 0.81192 | 12 | 0.96192 | 988.9258 | 9.0137 | 20.1333 | 8.6245 | 0.26681 | 0.050409 | 0.084021 | 0.14373 | 0.025862 | 0.0043103 | 0.0076581 | 0.012931 | RTE_2024: 0.46975; RTE_2025: 0.80735; EFC_2024: 4.3137; EFC_2025: 192.4183; UTI_2024: 0.3558; UTI_2025: 1.7743 | ELEVATED_P_AUX
67549 | Kuna BESS | ID | IPCO | Kuna BESS, LLC | Kuna BESS, LLC |  |  | FALSE |  | LIB | CT | Ramping / Spinning Reserve | 150 | 600 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.87285 |  |  |  |  | insufficient_history |  | insufficient_history | 169.7367 | 0.028289 | 0.97171 | 6000 | 0 | 0 | 1 | 0.8918 | 0 | 150 | 150 |  |  |  |  | 9037.6215 | 494.2489 | 302.8797 | 709.3627 | 0.081309 | 0.081309 | 0.039665 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034448 | 0.031802 | RTE_2025: 0.87979; EFC_2025: 169.7367; UTI_2025: 1.1975
67573 | Happy Valley Battery Storage | ID | IPCO | Idaho Power Co | Idaho Power Co |  |  | FALSE |  | FLB | CS | Load Following, Voltage or Reactive Power Support | 82 | 328 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.86638 |  |  |  |  | insufficient_history |  | insufficient_history | 146.6555 | 0.024443 | 0.97556 | 6000 | 0 | 0 | 5.4667 | 0.90204 | 289.9093 | 15 | 82 |  |  |  |  | 4806.6826 | 262.8675 | 161.6674 | 377.2764 | 0.081309 | 0.081309 | 0.039802 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034572 | 0.031802 | RTE_2025: 0.87603; EFC_2025: 146.6555; UTI_2025: 1.2784
67577 | Monument Valley | MA | ISNE | LSE Lepus LLC | LSE Lepus LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 1 | 2.2 | 2.2 | 1.5-2.5h | 2022 |  |  | HYBRID_ARTEFACT | 1.0035 | 0.98769 | 0.42165 | 6.7866e-05 |  |  | ok | 0.045956 | ok | 2862.2727 | 0.47705 | 0.52295 | 6000 | 0 | 0 | 1 | 0.99525 | 0 | 1 | 1 | 0.0042165 | 0.99181 | 24 | 0.80887 | 344.2196 | 8.0677 | 3.203 | 2.5731 | 0.17028 | 0.076884 | 0.024628 | 0.076884 | 0.015556 | 0.0066667 | 0.0021053 | 0.0066667 | RTE_2024: 0.99248; RTE_2025: 0.99113; EFC_2024: 1440.4545; EFC_2025: 1421.8182; UTI_2024: 11.7146; UTI_2025: 16.0659
67578 | Sandwich | MA | ISNE | LSE Ophiuchus LLC | LSE Ophiuchus LLC |  |  | TRUE | pv_same_plant,dc_tight | LIB | CS |  | 2 | 4.6 | 2.3 | 1.5-2.5h | 2023 | 199 | C | HYBRID_ARTEFACT | 0.99441 | 0.99587 | -0.025092 | 0.0034085 | -1.7109 | -70.5245 | ok | 0.25449 | ok | 1912.6087 | 0.31877 | 0.68123 | 6000 | 0 | 2 | 1 | 0.93833 | 102 | 2 | 2 | -0.00050183 | 0.99469 | 24 | 0.0062153 | 392.7414 | 9.205 | 3.6545 | 2.9358 | 0.17028 | 0.076884 | 0.024628 | 0.076884 | 0.015556 | 0.0066667 | 0.0021053 | 0.0066667 | RTE_2024: 0.99934; RTE_2025: 0.98972; EFC_2024: 991.7391; EFC_2025: 920.8696; UTI_2024: 6.2627; UTI_2025: 7.2258 | PARTIAL_AVAILABILITY
67579 | AES ES Alamitos 2 LLC | CA | CISO | AES Clean Energy | AES Clean Energy |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 82 | 328 | 4 | 2.5-4.5h | 2024 | 43 | B | UNDER_DISPATCH | 0.88869 | 0.87504 | 0.07077 | -0.11846 |  |  | insufficient_history |  | insufficient_history | 260.3628 | 0.043394 | 0.95661 | 6000 | 0 | 2 | 1 | 0.88771 | 24621.3779 | 82 | 82 | 0.058032 | 0.88456 | 12 | 0.41143 | 2619.3358 | 477.4869 | 58.8556 | 380.7252 | 0.051638 | 0.16199 | 0.017026 | 0.35714 | 0.0044183 | 0.014728 | 0.001444 | 0.036819 | RTE_2024: 0.8625; RTE_2025: 0.88481; EFC_2024: 2.9451; EFC_2025: 257.4177; UTI_2024: 0.12011; UTI_2025: 0.96718 | PARTIAL_AVAILABILITY
67598 | Desert Willow Energy Storage | TX | ERCO | Desert Willow Energy Storage | Desert Willow Energy Storage |  |  | FALSE |  | LIB | CS |  | 150 | 300 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.81009 |  |  |  |  | insufficient_history |  | insufficient_history | 239.3067 | 0.039884 | 0.96012 | 6000 | 0 | 0 | 1 | 0.8266 | 0 | 150 | 150 |  |  |  |  | 1281.4823 | 280.3265 | 625.8421 | 625.853 | 0.022471 | 0.086899 | 0.13862 | 0.47079 | 0.0018939 | 0.0075758 | 0.013453 | 0.05303 | RTE_2025: 0.8102; EFC_2025: 239.3067; UTI_2025: 1.2514
67680 | Kola Energy Center | CA | CISO | Kola Energy Storage, LLC | Kola Energy Storage, LLC |  |  | FALSE |  | LIB | CS |  | 400 | 1800 | 4.5 | >4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.82942 |  |  |  |  | insufficient_history |  | insufficient_history | 80.9272 | 0.013488 | 0.98651 | 6000 | 0 | 0 | 1 | 0.87747 | 18055.2906 | 425 | 425 |  |  |  |  | 152.341 | 939.6108 | 10.4739 | 299.6803 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2025: 0.84777; EFC_2025: 80.9272; UTI_2025: 1.1048
67695 | Holtville | CA | CISO | Greenbacker Renewable Energy Corporation | Greenbacker Renewable Energy Corporation |  |  | TRUE | rte_gt_1 | LIB | CS | Arbitrage | 30 | 127 | 4.2333 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.91447 | 0.87209 | 0.51826 | 0.080099 |  |  | insufficient_history |  | insufficient_history | 251.6063 | 0.041934 | 0.95807 | 6000 | 5 | 0 | 1 | 0.86733 | 0 | 30 | 30 | 0.15548 | 0.86667 | 16 | 0.038121 | 572.6706 | 104.3939 | 12.8099 | 83.2387 | 0.051638 | 0.16199 | 0.016951 | 0.35714 | 0.0044183 | 0.014728 | 0.0014375 | 0.036819 | RTE_2024: 0.84359; RTE_2025: 0.87751; EFC_2024: 78.2677; EFC_2025: 173.3386; UTI_2024: 0.83434; UTI_2025: 0.55639
67698 | Coffee Creek BESS | OR | PGE | Portland General Electric Co | Portland General Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation, Backup Power | 17 | 34 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | 0.89668 | 0.88567 | 0.060119 | 0.023469 |  |  | insufficient_history |  | insufficient_history | 256.5 | 0.04275 | 0.95725 | 6000 | 0 | 1 | 1 | 0.91073 | 1877 | 17 | 17 | 0.01022 | 0.88809 | 13 | 0.055948 | 1207.1844 | 33.0092 | 0.39839 | 21.056 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2024: 0.88594; RTE_2025: 0.88824; EFC_2024: 16.6765; EFC_2025: 239.8235; UTI_2024: 0.38556; UTI_2025: 1.1305
67710 | TAG | NM | PNM | Exus New Mexico | Exus New Mexico |  |  | TRUE | pv_same_plant | OTH | OT |  | 57.8 | 231.4 | 4.0035 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.89073 |  |  |  |  | insufficient_history |  | insufficient_history | 97.9041 | 0.016317 | 0.98368 | 6000 | 0 | 0 | 1 | 0.88379 | 0 | 57.8 | 57.8 |  |  |  |  | 2826.3315 | 154.5662 | 95.404 | 221.8387 | 0.081309 | 0.081309 | 0.03994 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034697 | 0.031802 | RTE_2025: 0.88496; EFC_2025: 97.9041; UTI_2025: 0.99731
67711 | Seaside BESS | OR | PGE | Portland General Electric Co | Portland General Electric Co |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, System Peak Shaving, Voltage or Reactive Power Support | 200 | 800 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.88981 |  |  |  |  | insufficient_history |  | insufficient_history | 109.9825 | 0.01833 | 0.98167 | 6000 | 0 | 0 | 1 | 0.8731 | 28764 | 200 | 200 |  |  |  |  | 8177.1179 | 447.1897 | 275.0282 | 641.8218 | 0.081309 | 0.081309 | 0.039802 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034572 | 0.031802 | RTE_2025: 0.89268; EFC_2025: 109.9825; UTI_2025: 0.81978
67712 | Constable BESS | OR | PGE | Portland General Electric Co | Portland General Electric Co |  |  | FALSE |  | LIB | CS | Arbitrage, System Peak Shaving, Voltage or Reactive Power Support | 75 | 300 | 4 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.87608 | 0.88552 | -0.10558 | 0.20306 |  |  | insufficient_history |  | insufficient_history | 278.1733 | 0.046362 | 0.95364 | 6000 | 0 | 0 | 1 | 0.89058 | 8768.6726 | 75 | 75 | -0.079184 | 0.88441 | 13 | 0.10809 | 3442.7923 | 188.2792 | 230.5778 | 270.2247 | 0.081309 | 0.081309 | 0.07619 | 0.31725 | 0.0070671 | 0.0070671 | 0.0068843 | 0.031802 | RTE_2024: 0.91591; RTE_2025: 0.88389; EFC_2024: 4.6833; EFC_2025: 273.49; UTI_2024: 0.2084; UTI_2025: 0.95305
67721 | Al Pastor Battery Storage Plant | TX | ERCO | Al Pastor BESS LLC | Al Pastor BESS LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 100.3 | 145 | 1.4457 | <1.5h | 2024 | 30 | A | UNATTRIBUTED | 0.90948 | 0.76477 | 1.0119 | -0.0071809 |  |  | insufficient_history |  | insufficient_history | 349.4621 | 0.058244 | 0.94176 | 6000 | 0 | 2 | 1 | 0.80313 | 5433.3289 | 100.3 | 100.3 | 1.015 | 0.76675 | 14 | 0.75861 | 2647.7861 | 124.116 | 25.4726 | 237.5139 | 0.11369 | 0.098277 | 0.016601 | 0.46243 | 0.010057 | 0.0086207 | 0.0014073 | 0.051724 | RTE_2024: 0.75057; RTE_2025: 0.76908; EFC_2024: 43.1448; EFC_2025: 306.3172; UTI_2024: 1.3474; UTI_2025: 1.4139 | ELEVATED_P_AUX
67734 | Silver State South Storage | NV | CISO | Silver State South Storage, LLC | Silver State South Storage, LLC |  |  | FALSE |  | LIB | CT | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, System Peak Shaving, Load Management, Voltage or Reactive Power Support | 200 | 800 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.84944 |  |  |  |  | insufficient_history |  | insufficient_history | 256.6275 | 0.042771 | 0.95723 | 6000 | 2 | 0 | 1 | 0.85493 | 3471.3344 | 200 | 200 |  |  |  |  | 7413.9119 | 1351.5051 | 167.5961 | 1077.6255 | 0.051638 | 0.16199 | 0.017128 | 0.35714 | 0.0044183 | 0.014728 | 0.0014527 | 0.036819 | RTE_2025: 0.84825; EFC_2025: 256.6275; UTI_2025: 1.1722
67736 | Silver Peak | NV | CISO | Silver Peak Solar, LLC | Silver Peak Solar, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 279 | 1116 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.90445 |  |  |  |  | insufficient_history |  | insufficient_history | 196.2151 | 0.032703 | 0.9673 | 6000 | 2 | 0 | 1 | 0.90483 | 0 | 279 | 279 |  |  |  |  | 10607.0532 | 1933.5928 | 240.5068 | 1541.7543 | 0.051638 | 0.16199 | 0.017179 | 0.35714 | 0.0044183 | 0.014728 | 0.0014571 | 0.036819 | RTE_2025: 0.90446; EFC_2025: 196.2151; UTI_2025: 1.1142
67737 | SMT Ironman Battery Storage Plant | TX | ERCO | SMT Ironman BESS LLC | SMT Ironman BESS LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 304 | 440.8 | 1.45 | <1.5h | 2025 |  |  | UNATTRIBUTED |  | 0.83494 |  |  |  |  | insufficient_history |  | insufficient_history | 158.3144 | 0.026386 | 0.97361 | 6000 | 0 | 0 | 1 | 0.83576 | 469.7652 | 304 | 304 |  |  |  |  | 7696.0742 | 360.7563 | 74.8062 | 690.3596 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.83964; EFC_2025: 158.3144; UTI_2025: 1.2126
67738 | Citadel Battery Storage Plant | TX | ERCO | Citadel BESS LLC | Citadel BESS LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 204 | 298 | 1.4608 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.78721 | 0.73385 | 0.34013 | -0.06109 |  |  | insufficient_history |  | insufficient_history | 278.8658 | 0.046478 | 0.95352 | 6000 | 0 | 0 | 1 | 0.80066 | 13160.1894 | 204 | 204 | 0.69386 | 0.74249 | 13 | 0.73198 | 5111.77 | 239.6161 | 49.2491 | 458.5402 | 0.11369 | 0.098277 | 0.016625 | 0.46243 | 0.010057 | 0.0086207 | 0.0014094 | 0.051724 | RTE_2024: 0.65619; RTE_2025: 0.74485; EFC_2024: 6.5839; EFC_2025: 272.2819; UTI_2024: 0.35521; UTI_2025: 1.309
67739 | Wigeon Whistle Battery Storage Plant | TX | ERCO | Wigeon Whistle BESS LLC | Wigeon Whistle BESS LLC |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 120 | 174 | 1.45 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.80276 | 0.73133 | 0.51737 | 0.025852 |  |  | insufficient_history |  | insufficient_history | 291.8276 | 0.048638 | 0.95136 | 6000 | 0 | 0 | 1 | 0.79368 | 8654.1624 | 120 | 120 | 0.62084 | 0.73573 | 13 | 0.4547 | 2975.5299 | 139.4791 | 28.6676 | 266.9134 | 0.11369 | 0.098277 | 0.016625 | 0.46243 | 0.010057 | 0.0086207 | 0.0014094 | 0.051724 | RTE_2024: 0.70775; RTE_2025: 0.73691; EFC_2024: 11.3851; EFC_2025: 280.4425; UTI_2024: 0.61423; UTI_2025: 1.2791
67740 | Anole Energy Storage | TX | ERCO | Anole Energy Storage, LLC | Anole Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 240 | 480 | 2 | 1.5-2.5h | 2025 |  |  | UNATTRIBUTED |  | 0.77531 |  |  |  |  | insufficient_history |  | insufficient_history | 152.525 | 0.025421 | 0.97458 | 6000 | 0 | 0 | 1 | 0.79035 | 2618.7689 | 240 | 240 |  |  |  |  | 1742.4212 | 381.1577 | 875.4852 | 850.9672 | 0.022471 | 0.086899 | 0.14204 | 0.47079 | 0.0018939 | 0.0075758 | 0.013841 | 0.05303 | RTE_2025: 0.77835; EFC_2025: 152.525; UTI_2025: 0.99425
67743 | Bishop Ranch BR 1-X | CA | CISO | Bollinger Canyon Road BR 1-X Solar Project 2020 | Bollinger Canyon Road BR 1-X Solar Project 2020 |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2022 | 263 | C | HYBRID_ARTEFACT | 0.97328 | 0.81511 | 0.69486 | 0.0010614 |  |  | ok |  | insufficient_history | 356.5152 | 0.059419 | 0.94058 | 6000 | 0 | 9 | 1 | 0.875 | 29.5 | 0.5 | 0.5 | 0.0034743 | 0.81858 | 14 | 0.43457 | 0 | 0 | 0 | 0 | 0.066091 | 0.31344 | 0.030909 | 0.0011993 | 0.005698 | 0.031339 | 0.0026596 | 0.0001 | RTE_2024: 0.77397; RTE_2025: 0.88889; EFC_2024: 102.7273; EFC_2025: 65.4545; UTI_2024: 0.36226; UTI_2025: 0 | FULL_OUTAGE
67745 | White Plains RFP Shapham Place | NY | NYIS | Shapham Place Solar Project 2020 LLC | Shapham Place Solar Project 2020 LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, Excess Wind and Solar Generation | 5 | 2 | 0.4 | <1.5h | 2022 | 328 | C | HYBRID_ARTEFACT |  | 0.68512 |  |  |  |  | insufficient_history |  | insufficient_history | 40.5 | 0.00675 | 0.99325 | 6000 | 0 | 3 | 1 | 0.8 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.15254 | 0.13124 | 0.023051 | 0.29943 | 0.013793 | 0.011724 | 0.0019672 | 0.029655 | RTE_2024: 0.61224; RTE_2025: 0.090909; EFC_2024: 15; EFC_2025: 0.5; UTI_2024: 0; UTI_2025: 0 | FULL_OUTAGE
67752 | Fort Duncan BESS | TX | ERCO | Fort Duncan BESS, LLC | Fort Duncan BESS, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Backup Power | 102.6 | 205.1 | 1.999 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.81848 |  |  |  |  | insufficient_history |  | insufficient_history | 228.8298 | 0.038138 | 0.96186 | 6000 | 2 | 0 | 1 | 0.81812 | 3138.5772 | 100 | 100 |  |  |  |  | 1083.2619 | 236.9654 | 536.5541 | 529.0457 | 0.022471 | 0.086899 | 0.14031 | 0.47079 | 0.0018939 | 0.0075758 | 0.013644 | 0.05303 | RTE_2025: 0.81803; EFC_2025: 228.8298; UTI_2025: 1.4914
67758 | Slocum Energy Storage | MI | MISO | DTE Electric Company | DTE Electric Company |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 14 | 56 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH | 0.86765 | 0.84146 | 0.30195 | 0.028989 |  |  | insufficient_history |  | insufficient_history | 157.7679 | 0.026295 | 0.97371 | 6000 | 0 | 0 | 1 | 0.87538 | 4194.5917 | 14 | 14 | 0.042273 | 0.84279 | 11 | 0.033165 | 756.5962 | 82.7534 | 0.42135 | 39.5901 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2025: 0.84279; EFC_2025: 157.7679; UTI_2025: 0.59328
67762 | Stampede Solar Hybrid | TX | ERCO | Stampede Solar Project LLC | Stampede Solar Project LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 72.2 | 115 | 1.5928 | 1.5-2.5h | 2024 | 380 | C | HYBRID_ARTEFACT | 0.81474 | 0.8387 | -0.11704 | 0.19507 |  |  | insufficient_history |  | insufficient_history | 340.313 | 0.056719 | 0.94328 | 6000 | 0 | 0 | 1 | 0.87622 | 0 | 70 | 70 | -0.084502 | 0.83963 | 15 | 0.077261 | 381.4283 | 83.4381 | 169.6416 | 186.2827 | 0.022471 | 0.086899 | 0.12785 | 0.47079 | 0.0018939 | 0.0075758 | 0.012252 | 0.05303 | RTE_2024: 0.8609; RTE_2025: 0.83587; EFC_2024: 52.4174; EFC_2025: 287.8957; UTI_2024: 0.99166; UTI_2025: 1.0592 | LOW_ETA_AND_LOW_UTI
67764 | Rosamond South 1 | CA | CISO | Golden Fields Solar IV, LLC | Golden Fields Solar IV, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 117 | 472 | 4.0342 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.8857 |  |  |  |  | insufficient_history |  | insufficient_history | 116.8962 | 0.019483 | 0.98052 | 6000 | 0 | 0 | 1 | 0.84722 | 0 | 117 | 117 |  |  |  |  | 3877.687 | 706.8757 | 88.1913 | 563.6288 | 0.051638 | 0.16199 | 0.01723 | 0.35714 | 0.0044183 | 0.014728 | 0.0014615 | 0.036819 | RTE_2025: 0.88317; EFC_2025: 116.8962; UTI_2025: 0.96222
67828 | Mordor ES1 | CA | CISO | Mordor ES1 LLC | Mordor ES1 LLC |  |  | FALSE |  | LIB | CS |  | 25 | 100 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.86759 |  |  |  |  | insufficient_history |  | insufficient_history | 188.99 | 0.031498 | 0.9685 | 6000 | 0 | 0 | 1 | 0.88606 | 2544.25 | 25 | 25 |  |  |  |  | 846.6835 | 154.3446 | 19.1688 | 123.067 | 0.051638 | 0.16199 | 0.017153 | 0.35714 | 0.0044183 | 0.014728 | 0.0014549 | 0.036819 | RTE_2025: 0.8737; EFC_2025: 188.99; UTI_2025: 1.0353
67829 | Mordor ES2 | CA | CISO | Mordor ES2 LLC | Mordor ES2 LLC |  |  | FALSE |  | LIB | CS |  | 20 | 80 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.89127 |  |  |  |  | insufficient_history |  | insufficient_history | 217.625 | 0.036271 | 0.96373 | 6000 | 0 | 0 | 1 | 0.90035 | 0 | 20 | 20 |  |  |  |  | 716.1626 | 130.5515 | 16.2138 | 104.0955 | 0.051638 | 0.16199 | 0.017153 | 0.35714 | 0.0044183 | 0.014728 | 0.0014549 | 0.036819 | RTE_2025: 0.89113; EFC_2025: 217.625; UTI_2025: 1.0558
67843 | Farmersville West | TX | ERCO | Adapture Solar Investments 6, LLC | SBESS TX7 LLC |  |  | TRUE | rte_gt_1 | LIB | CS |  | 9.9 | 24.7 | 2.4949 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.87609 | 0.90039 | -0.18749 | 0.015527 |  |  | insufficient_history |  | insufficient_history | 213.6842 | 0.035614 | 0.96439 | 6000 | 0 | 0 | 1 | 0.90555 | 0 | 9.9 | 9.9 | -0.018561 | 0.9122 | 12 | 0.3807 | 69.2242 | 15.1429 | 32.0131 | 33.8079 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.9122; EFC_2025: 213.6842; UTI_2025: 0.81805
67845 | Junction BESS | TX | ERCO | Adapture Solar Investments 6, LLC | SBESS TX5 LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 24.7 | 2.4949 | 1.5-2.5h | 2025 | 234 | A | UNATTRIBUTED | 0.80887 | 0.78036 | 0.12853 | 0.0093404 |  |  | insufficient_history |  | insufficient_history | 178.3401 | 0.029723 | 0.97028 | 6000 | 0 | 0 | 1 | 0.84691 | 94.408 | 9.9 | 9.9 | 0.012724 | 0.80648 | 12 | 0.22582 | 63.108 | 13.805 | 29.1847 | 30.8208 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.80648; EFC_2025: 178.3401; UTI_2025: 0.77924 | LOW_ETA_AND_LOW_UTI
67850 | Arrowleaf Solar and Storage | CA | IID | ORNI 30 LLC | ORNI 30 LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 35 | 140 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.87309 |  |  |  |  | insufficient_history |  | insufficient_history | 2.85 | 0.000475 | 0.99952 | 6000 | 0 | 0 | 1 | 0.87309 | 0 | 35 | 35 |  |  |  |  | 206.9566 | 11.318 | 7.0884 | 16.244 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.87309; EFC_2025: 2.85; UTI_2025: 0.12265
67851 | Montague Energy Storage | NJ | PJM | VESI 34 LLC | VESI 34 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 20 | 20 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH | 0.87725 | 0.80231 | 0.63165 | -0.019705 |  |  | insufficient_history |  | insufficient_history | 1526 | 0.25433 | 0.74567 | 6000 | 0 | 0 | 1 | 0.87978 | 8707.9762 | 20 | 20 | 0.12633 | 0.85704 | 14 | 0.98292 | 2458.5926 | 109.8052 | 70.4602 | 75.0458 | 0.13542 | 0.11205 | 0.05712 | 0.22481 | 0.012126 | 0.009903 | 0.0050546 | 0.021221 | RTE_2024: 0.52083; RTE_2025: 0.86257; EFC_2024: 15; EFC_2025: 1511; UTI_2024: 0.041839; UTI_2025: 0.81687
67855 | Westwing | AZ | AZPS | AES Clean Energy | AES Clean Energy |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 200 | 808.4 | 4.042 | 2.5-4.5h | 2024.59 | 70 | A | UNDER_DISPATCH | 0.94033 | 0.8631 | 0.68894 | -0.28521 |  |  | insufficient_history |  | insufficient_history | 268.8466 | 0.044808 | 0.95519 | 6000 | 3 | 0 | 1 | 0.89681 | 66854.4016 | 200 | 200 | 1.3779 | 0.87214 | 15 | 0.55593 | 86.0145 | 4.704 | 5.9138 | 381.4281 | 0.0011993 | 0.0011993 | 0.0011985 | 0.26294 | 0.0001 | 0.0001 | 0.0001 | 0.025424 | RTE_2024: 0.80486; RTE_2025: 0.8822; EFC_2024: 67.3968; EFC_2025: 201.4498; UTI_2024: 0.99112; UTI_2025: 0.53375 | ELEVATED_P_AUX
67859 | Foster Clean Power B | CA | CISO | Foster Clean Power B LLC | Foster Clean Power B LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Load Following | 1.2 | 5.4 | 4.5 | >4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.2 | 1.2
67860 | GFTX BESS | TX | ERCO | Giga Texas Energy LLC | Giga Texas Energy LLC |  |  | FALSE |  | OTH | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support, Backup Power | 125 | 250 | 2 | 1.5-2.5h | 2024 | 14 | A | UNATTRIBUTED | 0.95164 | 0.76733 | 1.0735 | -0.0055715 |  |  | insufficient_history | -0.35254 | ok | 509.012 | 0.084835 | 0.91516 | 6000 | 1 | 0 | 1 | 0.85265 | 8814.905 | 125 | 125 | 1.3419 | 0.83262 | 19 | 0.37352 | 938.2802 | 205.2504 | 387.6279 | 458.2392 | 0.022471 | 0.086899 | 0.11987 | 0.47079 | 0.0018939 | 0.0075758 | 0.01138 | 0.05303 | RTE_2024: 0.65857; RTE_2025: 0.83148; EFC_2024: 167.62; EFC_2025: 341.392; UTI_2024: 1.039; UTI_2025: 1.1975 | ELEVATED_P_AUX
67861 | Connolly BESS | TX | ERCO | BT Connolly Storage, LLC | BT Connolly Storage, LLC |  |  | FALSE |  | OTH | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 125 | 250 | 2 | 1.5-2.5h | 2024 | 147 | B | CAPACITY_FADE | 0.83155 | 0.83961 | -0.047533 | 0.07583 |  |  | insufficient_history | -7.0335 | ok | 412.584 | 0.068764 | 0.93124 | 6000 | 1 | 0 | 1 | 0.86222 | 381.5143 | 125 | 125 | -0.059416 | 0.84103 | 17 | 0.02412 | 889.9762 | 194.6838 | 385.9706 | 434.6484 | 0.022471 | 0.086899 | 0.12508 | 0.47079 | 0.0018939 | 0.0075758 | 0.011947 | 0.05303 | RTE_2024: 0.83325; RTE_2025: 0.84339; EFC_2024: 95.284; EFC_2025: 317.3; UTI_2024: 0.77067; UTI_2025: 1.1025 | LOW_ETA_AND_LOW_UTI
67867 | Liberty Hybrid Solar and Storage Project | TX | ERCO | Liberty 1 Solar LLC | Liberty 1 Solar LLC |  |  | TRUE | pv_same_plant | [10 empty] | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0
67869 | Sundial (Troutdale) BESS | OR | PGE | Troutdale Grid, LLC | Troutdale Grid, LLC |  |  | FALSE |  | LIB | CT | System Peak Shaving | 200 | 800 | 4 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | 0.88486 | 0.87996 | 0.090218 | -0.48826 |  |  | insufficient_history |  | insufficient_history | 337.2925 | 0.056215 | 0.94378 | 6000 | 0 | 0 | 1 | 0.87522 | 17928.8333 | 200 | 200 | 0.18044 | 0.87962 | 13 | 0.0077096 | 11370.9399 | 621.8532 | 373.0466 | 892.5048 | 0.081309 | 0.081309 | 0.038862 | 0.31725 | 0.0070671 | 0.0070671 | 0.0033722 | 0.031802 | RTE_2024: 0.86438; RTE_2025: 0.88103; EFC_2024: 27.9638; EFC_2025: 309.3288; UTI_2024: 1.2546; UTI_2025: 1.109
67880 | Arthur Kill Energy, LLC | NY | NYIS | NineDot Holdings, LLC | NineDot Holdings, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Transmission and Distribution Deferral | 5 | 21.7 | 4.34 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.49545 |  |  |  |  | insufficient_history |  | insufficient_history | 40.6452 | 0.0067742 | 0.99323 | 6000 | 0 | 0 | 2.1739 | 0.82641 | 4948.5823 | 2.3 | 5 |  |  |  |  | 30.8256 | 0.0042145 | 0.0052984 | 0.35844 | 0.38122 | 0.0011993 | 0.0011985 | 0.27385 | 0.04 | 0.0001 | 0.0001 | 0.026667 | RTE_2025: 0.59155; EFC_2025: 40.6452; UTI_2025: 0.019788
67882 | Empire Clean Energy, LLC | NY | NYIS | NineDot Holdings, LLC | NineDot Holdings, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Transmission and Distribution Deferral | 10 | 43.4 | 4.34 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.63218 |  |  |  |  | insufficient_history |  | insufficient_history | 32.6267 | 0.0054378 | 0.99456 | 6000 | 0 | 0 | 1.8519 | 0.83513 | 10052.5537 | 5.4 | 10 |  |  |  |  | 95.4127 | 0.013045 | 0.0164 | 1.1095 | 0.38122 | 0.0011993 | 0.0011985 | 0.27385 | 0.04 | 0.0001 | 0.0001 | 0.026667 | RTE_2025: 0.62655; EFC_2025: 32.6267; UTI_2025: 0.030872
67883 | Gabby Giffords Clean Energy, LLC | NY | NYIS | NineDot Holdings, LLC | NineDot Holdings, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Transmission and Distribution Deferral | 8 | 34.1 | 4.2625 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.48779 |  |  |  |  | insufficient_history |  | insufficient_history | 39.2375 | 0.0065396 | 0.99346 | 6000 | 0 | 0 | 1.8605 | 0.84644 | 9153.7942 | 4.3 | 8 |  |  |  |  | 111.5594 | 0.015252 | 0.019175 | 1.2972 | 0.38122 | 0.0011993 | 0.0011985 | 0.27385 | 0.04 | 0.0001 | 0.0001 | 0.026667 | RTE_2024: 0.076923; RTE_2025: 0.64632; EFC_2024: 0.1173; EFC_2025: 39.1202; UTI_2024: 0.0025934; UTI_2025: 0.046491
67886 | Gunther | NY | NYIS | NineDot Holdings, LLC | NineDot Holdings, LLC |  |  | FALSE |  | NIB | CS | Arbitrage, Transmission and Distribution Deferral | 3 | 12.4 | 4.1333 | 2.5-4.5h | 2023 | 141 | A | UNATTRIBUTED | 0.78267 | 0.45855 | 0.41601 | 0.0012029 |  |  | ok | -1.5084 | ok | 76.5054 | 0.012751 | 0.98725 | 6000 | 0 | 0 | 1 | 0.89326 | 313.4262 | 3 | 3 | 0.01248 | 0.71456 | 15 | 0.80966 | 15.1524 | 0.003211 | 0.0040369 | 0.19822 | 0.26632 | 0.0011993 | 0.0011985 | 0.20726 | 0.025806 | 0.0001 | 0.0001 | 0.019355 | RTE_2024: 0.71079; RTE_2025: 0.55556; EFC_2024: 39.8387; EFC_2025: 23.3871; UTI_2024: 0.058927; UTI_2025: 0.037246 | LOW_ETA_AND_LOW_UTI
67893 | Dunns Bridge II Solar | IN | MISO | Dunns Bridge II Solar and Storage Generation LLC | Dunns Bridge II Solar and Storage Generation LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support, Backup Power, Excess Wind and Solar Generation | 56.3 | 225 | 3.9964 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT | 0.8097 | 0.8764 | -1.5874 | 1.6033 |  |  | insufficient_history |  | insufficient_history | 455.4533 | 0.075909 | 0.92409 | 6000 | 0 | 0 | 1 | 0.81389 | 0 | 56.3 | 56.3 | -0.89369 | 0.86454 | 12 | 0.222 | 8699.9507 | 951.5647 | 4.845 | 455.2393 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2025: 0.86454; EFC_2025: 455.4533; UTI_2025: 1.747
67898 | Escape Solar Plant | NV | NEVP | Estuary Power LLC | Escape Solar LLC |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 100 | 400 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.87772 |  |  |  |  | insufficient_history |  | insufficient_history | 21.6775 | 0.0036129 | 0.99639 | 6000 | 0 | 0 | 1 | 0.87772 | 0 | 100 | 100 |  |  |  |  | 4497.5445 | 245.9614 | 154.0431 | 353.0122 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.87772; EFC_2025: 21.6775; UTI_2025: 0.93287
67899 | PNY BESS LLC | PA | PJM | Citizens Enterprises Corporation | Citizens Enterprises Corporation |  |  | FALSE |  | LIB | CS | System Peak Shaving | 6.2 | 6.2 | 1 | <1.5h | 2021 | 215 | A | THERMAL_AUX | 0.94369 | 0.92476 | 0.32956 | 0.0089398 | 3.292 | 184.801 | ok | -0.27387 | ok | 6119.3145 | 1.0199 | 0 | 6000 | 0 | 0 | 1 | 0.92429 | 92.0439 | 6.2 | 6.2 | 0.020433 | 0.92527 | 24 | 0.12355 | 744.5732 | 34.6113 | 30.1128 | 27.9221 | 0.15254 | 0.13124 | 0.088567 | 0.29943 | 0.013793 | 0.011724 | 0.0081136 | 0.029655 | RTE_2024: 0.92681; RTE_2025: 0.9237; EFC_2024: 1395; EFC_2025: 1353.0645; UTI_2024: 0.70726; UTI_2025: 0.76478 | THERMAL_AUX
67905 | Roadrunner Reserve Phase 1 | AZ | TEPC | Tucson Electric Power Co | Tucson Electric Power Co |  |  | FALSE |  | LIB | CS | Arbitrage, Voltage or Reactive Power Support | 200 | 800 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.87107 |  |  |  |  | insufficient_history |  | insufficient_history | 177.7688 | 0.029628 | 0.97037 | 6000 | 2 | 0 | 1 | 0.95142 | 0 | 200 | 200 |  |  |  |  | 12417.9118 | 679.11 | 417.6625 | 974.6816 | 0.081309 | 0.081309 | 0.039802 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034572 | 0.031802 | RTE_2025: 0.87239; EFC_2025: 177.7688; UTI_2025: 1.2401
67931 | Daggett 1 | CA | CISO | Daggett Solar Power 1 LLC | Daggett Solar Power 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 113.5 | 454 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.82163 |  |  |  |  | insufficient_history |  | insufficient_history | 64.7797 | 0.010797 | 0.9892 | 6000 | 0 | 0 | 1 | 0.82665 | 6169.1929 | 113.5 | 113.5 |  |  |  |  | 2449.4154 | 446.5116 | 55.7926 | 356.0269 | 0.051638 | 0.16199 | 0.017256 | 0.35714 | 0.0044183 | 0.014728 | 0.0014638 | 0.036819 | RTE_2025: 0.82153; EFC_2025: 64.7797; UTI_2025: 0.65951
67948 | Hampton Substation Energy Storage | IA | SWPP | Corn Belt Power Coop | Corn Belt Power Coop |  |  | FALSE |  | LIB | CS |  | 1.8 | 9.1 | 5.0556 | >4.5h | 2022 | 284 | A | THERMAL_AUX | 0.91104 | 0.90683 | 0.010585 | 0.00073255 | 2.0481 | 286.8802 | ok | 12.7184 | ok | 138.7729 | 0.023129 | 0.97687 | 6000 | 0 | 0 | 1 | 0.89552 | 10.2147 | 1.4 | 1.4 | 0.00019053 | 0.90675 | 24 | 0.014841 | 53.1476 | 0.48442 | 3.0894 | 0.46351 | 0.26681 | 0.050409 | 0.20703 | 0.14373 | 0.025862 | 0.0043103 | 0.021865 | 0.012931 | RTE_2024: 0.90891; RTE_2025: 0.90343; EFC_2024: 49.3407; EFC_2025: 31.8681; UTI_2024: 0.54192; UTI_2025: 0.27253 | THERMAL_AUX
67963 | Tynan | TX | ERCO | Manulife Infrastructure II Holdings A, L.P. | HEN Infrastructure, L.L.C. |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 9.9 | 1 | <1.5h | 2025 |  |  | UNATTRIBUTED |  | 0.89663 |  |  |  |  | insufficient_history |  | insufficient_history | 113.9394 | 0.01899 | 0.98101 | 6000 | 1 | 0 | 1 | 0.90132 | 0 | 9.9 | 9.9 |  |  |  |  | 92.2702 | 4.3252 | 0.89422 | 8.2769 | 0.11369 | 0.098277 | 0.016722 | 0.46243 | 0.010057 | 0.0086207 | 0.0014177 | 0.051724 | RTE_2025: 0.89666; EFC_2025: 113.9394; UTI_2025: 0.68605
67968 | Burksol Energy Storage | TX | ERCO | Burksol, LLC | Burksol, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 100 | 200 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.85704 |  |  |  |  | insufficient_history |  | insufficient_history | 184.65 | 0.030775 | 0.96923 | 6000 | 0 | 0 | 1 | 0.84128 | 7662.296 | 100 | 100 |  |  |  |  | 605.5035 | 132.4549 | 291.626 | 295.7171 | 0.022471 | 0.086899 | 0.13697 | 0.47079 | 0.0018939 | 0.0075758 | 0.013267 | 0.05303 | RTE_2025: 0.8512; EFC_2025: 184.65; UTI_2025: 1.0954
67973 | Sierra Pinta BESS | AZ | AZPS | Leeward Asset Management, LLC | Leeward Asset Management, LLC |  |  | FALSE |  | LIB | BL |  | 113 | 113 | 1 | <1.5h | 2025 |  |  | HEALTHY |  | 0.83771 |  |  |  |  | insufficient_history |  | insufficient_history | 235.7168 | 0.039286 | 0.96071 | 6000 | 0 | 0 | 1 | 0.84671 | 0 | 113 | 113 |  |  |  |  | 6372.6439 | 441.4419 | 201.899 | 385.3305 | 0.099307 | 0.12408 | 0.045937 | 0.30412 | 0.0087159 | 0.01104 | 0.0040164 | 0.030215 | RTE_2025: 1.0388; EFC_2025: 235.7168; UTI_2025: 3.5915
68012 | Caballero | CA | CISO | Caballero CA Storage LLC | Caballero CA Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 99.7 | 398.8 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.85118 |  |  |  |  | insufficient_history |  | insufficient_history | 257.1866 | 0.042864 | 0.95714 | 6000 | 0 | 0 | 1 | 0.86746 | 4161.4642 | 99.7 | 99.7 |  |  |  |  | 4079.7107 | 743.7032 | 92.2244 | 592.9933 | 0.051638 | 0.16199 | 0.017128 | 0.35714 | 0.0044183 | 0.014728 | 0.0014527 | 0.036819 | RTE_2025: 0.85696; EFC_2025: 257.1866; UTI_2025: 1.1771
68023 | BCE Seal Beach | CA | CISO | BCE Seal Beach | BCE Seal Beach |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Co-Located Renewable Firming, System Peak Shaving, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 16.7 | 64 | 3.8323 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.9197 |  |  |  |  | insufficient_history |  | insufficient_history | 29.8594 | 0.0049766 | 0.99502 | 6000 | 0 | 0 | 1 | 0.90216 | 0 | 16.7 | 16.7 |  |  |  |  | 309.8453 | 56.4827 | 7.0792 | 45.0366 | 0.051638 | 0.16199 | 0.017308 | 0.35714 | 0.0044183 | 0.014728 | 0.0014683 | 0.036819 | RTE_2025: 0.91392; EFC_2025: 29.8594; UTI_2025: 0.62324
68058 | Prairie Center Energy LLC | CO | WACM | Prairie Enhanced, LLC | Whetstone Power Operations LLC |  |  | FALSE |  | OTH | CS |  | 35.4 | 235 | 6.6384 | >4.5h | 2024 |  |  | UNDER_DISPATCH | 0.90552 | 0.85826 | 0.17892 | -0.47053 |  |  | insufficient_history |  | insufficient_history | 76.217 | 0.012703 | 0.9873 | 6000 | 0 | 0 | 1 | 0.92657 | 7102.5954 | 35.4 | 35.4 | 0.063336 | 0.91504 | 13 | 0.18114 | 12.3633 | 76.2544 | 0.85001 | 24.3206 | 0.0011993 | 0.12658 | 0.0011985 | 0.12658 | 0.0001 | 0.011278 | 0.0001 | 0.011278 | RTE_2024: 0.6; RTE_2025: 0.92569; EFC_2024: 1.634; EFC_2025: 74.583; UTI_2024: 0.27386; UTI_2025: 0.61245
68064 | CA- US Foods- Livermore | CA | CISO | EDPRNA DG CA Livermore LLC | EDPRNA DG CA Livermore LLC |  |  | TRUE | colocated_firming,pv_same_plant | LIB | CS | Arbitrage, Load Following, Co-Located Renewable Firming, Transmission and Distribution Deferral, Excess Wind and Solar Generation | 1.2 | 2.1 | 1.75 | 1.5-2.5h | 2024 |  |  | HYBRID_ARTEFACT | 3.8117 | 0.73863 | 20.1152 | 0.045939 |  |  | insufficient_history | -0.35271 | ok | 1302.381 | 0.21706 | 0.78294 | 6000 | 0 | 0 | 1 | 0.73986 | 0 | 0.6 | 0.6 | 0.24138 | 0.73246 | 17 | 0.72887 | 709.03 | 0.070442 | 0.088559 | 8.2447 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2024: 0.73766; RTE_2025: 0.73047; EFC_2024: 362.8571; EFC_2025: 939.5238; UTI_2024: 3.0729; UTI_2025: 3.0052
68069 | Old Frontier Solar III | MA | ISNE | Old Frontier Solar III PV, LLC | Old Frontier Solar III PV, LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CT |  | 2 | 2.2 | 1.1 | <1.5h | 2022 | 214 | C | HYBRID_ARTEFACT | 0.9135 | 0.92832 | -0.024802 | 0.00084058 | 8.1236 | 54.6238 | ok | 1.3764 | ok | 400.4545 | 0.066742 | 0.93326 | 6000 | 0 | 4 | 1 | 0.95455 | 81 | 2 | 2 | -0.00049603 | 0.92822 | 20 | 0.08245 | 23.3528 | 1.2771 | 0.015895 | 0.13577 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.89655; RTE_2025: 0.9517; EFC_2024: 106.3636; EFC_2025: 152.2727; UTI_2024: 0.22864; UTI_2025: 0.28246 | FULL_OUTAGE
68146 | Angelo Storage | TX | ERCO | Angelo Storage, LLC | Angelo Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 100 | 249.4 | 2.494 | 1.5-2.5h | 2025 |  |  | UNATTRIBUTED | 0.93176 | 0.83934 | 0.68411 | 0.12894 |  |  | insufficient_history |  | insufficient_history | 194.2863 | 0.032381 | 0.96762 | 6000 | 0 | 0 | 1 | 0.838 | 6160.6217 | 100 | 100 | 0.68411 | 0.8427 | 11 | 0.38337 | 637.0575 | 139.3574 | 298.5722 | 311.1275 | 0.022471 | 0.086899 | 0.13379 | 0.47079 | 0.0018939 | 0.0075758 | 0.012911 | 0.05303 | RTE_2025: 0.8427; EFC_2025: 194.2863; UTI_2025: 0.71695
68147 | Coffeen Solar BESS | IL | MISO | Vistra Corp | Vistra Corp |  |  | TRUE | pv_same_plant | LIB | CS |  | 2 | 8 | 4 | 2.5-4.5h | 2024 | 333 | C | HYBRID_ARTEFACT | 0.67817 | 0.68904 | 0.0034979 | -0.0069269 |  |  | insufficient_history |  | insufficient_history | 82.125 | 0.013688 | 0.98631 | 6000 | 0 | 0 | 1 | 0.61832 | 0 | 2 | 2 | 6.9958e-05 | 0.68012 | 13 | 0.00094893 | 41.2277 | 4.5093 | 0.02296 | 2.1573 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2024: 0.66667; RTE_2025: 0.68017; EFC_2024: 0.25; EFC_2025: 81.875; UTI_2024: 0.011176; UTI_2025: 0.26452 | LOW_ETA_AND_LOW_UTI
68148 | Baldwin Solar BESS | IL | MISO | Vistra Corp | Vistra Corp |  |  | TRUE | pv_same_plant | LIB | CS |  | 2 | 8 | 4 | 2.5-4.5h | 2024 | 164 | C | HYBRID_ARTEFACT | 0.57822 | 0.70479 | -0.63262 | -0.02454 |  |  | insufficient_history |  | insufficient_history | 64.625 | 0.010771 | 0.98923 | 6000 | 0 | 3 | 1 | 0.53472 | 200.0115 | 2 | 2 | -0.012652 | 0.65609 | 11 | 0.12487 | 38.9624 | 4.2616 | 0.021698 | 2.0388 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2024: 0.9375; RTE_2025: 0.64359; EFC_2024: 1.875; EFC_2025: 62.75; UTI_2024: 0.083819; UTI_2025: 0.22523 | LOW_ETA_AND_LOW_UTI
68189 | Great Kiskadee Storage | TX | ERCO | GridFlex Storage, LLC | Great Kiskadee Storage, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 100 | 249.4 | 2.494 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH | 0.8998 | 0.78602 | 0.50877 | 0.016006 |  |  | insufficient_history |  | insufficient_history | 110.3609 | 0.018393 | 0.98161 | 6000 | 3 | 0 | 1 | 0.7964 | 33756.1446 | 100 | 100 | 0.50877 | 0.79242 | 11 | 0.56119 | 313.3161 | 68.5384 | 146.8431 | 153.018 | 0.022471 | 0.086899 | 0.13379 | 0.47079 | 0.0018939 | 0.0075758 | 0.012911 | 0.05303 | RTE_2025: 0.79242; EFC_2025: 110.3609; UTI_2025: 0.41405
68266 | North Juvenile Detention Center Solar | CA | CISO | SoCore Energy LLC | SoCore Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2019 | 281 | C | HYBRID_ARTEFACT | 0.79297 | 0.74098 | 0.24381 | -0.0014626 | 17.401 | 178.1071 | ok | 0 | ok | 570.3333 | 0.095056 | 0.90494 | 6000 | 0 | 4 | 1 | 0.90909 | 12 | 0.3 | 0.3 | 0.00073143 | 0.75714 | 21 | 0.15243 | 10.8368 | 0.3704 | 0.0027753 | 0.094508 | 0.27541 | 0.18237 | 0.0011985 | 0.14877 | 0.026846 | 0.016779 | 0.0001 | 0.013423 | RTE_2024: 0.75439; RTE_2025: 0.75; EFC_2024: 86; EFC_2025: 126; UTI_2024: 0.19936; UTI_2025: 0.41775 | LOW_ETA_AND_LOW_UTI
68322 | Atlas VII | AZ | CISO | Atlas VII LLC | Atlas VII LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 300 | 1200 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.85219 |  |  |  |  | insufficient_history |  | insufficient_history | 15.1575 | 0.0025262 | 0.99747 | 6000 | 0 | 0 | 1 | 0.87851 | 71452.589 | 300 | 300 |  |  |  |  | 1088.9173 | 198.5021 | 24.8412 | 158.2761 | 0.051638 | 0.16199 | 0.017282 | 0.35714 | 0.0044183 | 0.014728 | 0.001466 | 0.036819 | RTE_2025: 0.84853; EFC_2025: 15.1575; UTI_2025: 0.11478
68324 | Atlas IX | AZ | CISO | Atlas IX LLC | Atlas IX LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 150 | 600 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.90609 |  |  |  |  | insufficient_history |  | insufficient_history | 17.995 | 0.0029992 | 0.997 | 6000 | 0 | 0 | 1 | 0.8765 | 34023.7945 | 150 | 150 |  |  |  |  | 594.3971 | 108.3545 | 13.5598 | 86.3967 | 0.051638 | 0.16199 | 0.017282 | 0.35714 | 0.0044183 | 0.014728 | 0.001466 | 0.036819 | RTE_2025: 0.87553; EFC_2025: 17.995; UTI_2025: 0.12531
68335 | Fairhaven | MD | PJM | Baltimore Gas & Electric Co | Baltimore Gas & Electric Co |  |  | FALSE |  | LIB | CS | Frequency Regulation | 2.5 | 7.1 | 2.84 | 2.5-4.5h | 2024 |  |  | UNDER_DISPATCH | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 0 | 0.17391 | 0 | 2693.6547 | 2.3 | 0.4 |  |  |  |  | 0 | 0 | 0 | 0 | 0.18053 | 0.18053 | 0.065968 | 0.25593 | 0.016591 | 0.016591 | 0.005894 | 0.024635 | RTE_2024: 0; RTE_2025: 0; EFC_2024: 0; EFC_2025: 0; UTI_2024: 0; UTI_2025: 0
68346 | Brownsville Energy Storage System | NY | NYIS | Consolidated Edison Co-NY Inc | Consolidated Edison Co-NY Inc |  |  | FALSE |  | LIB | CS | Arbitrage, Ramping / Spinning Reserve, Transmission and Distribution Deferral, Voltage or Reactive Power Support | 5.6 | 23.2 | 4.1429 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 5.6 | 5.6
68423 | St Gall Energy Storage II | TX | ERCO | St Gall Energy Storage II LLC | St Gall Energy Storage II LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 100 | 200 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.89221 |  |  |  |  | insufficient_history |  | insufficient_history | 115.6 | 0.019267 | 0.98073 | 6000 | 0 | 0 | 1 | 0.89386 | 0 | 100 | 100 |  |  |  |  | 787.2519 | 172.2127 | 407.2996 | 384.4797 | 0.022471 | 0.086899 | 0.14563 | 0.47079 | 0.0018939 | 0.0075758 | 0.014252 | 0.05303 | RTE_2025: 0.89194; EFC_2025: 115.6; UTI_2025: 1.1534
68424 | Tibbits Energy Storage | MI | MISO | Tibbits Energy Storage LLC | Tibbits Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 104.9 | 400 | 3.8132 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.85309 |  |  |  |  | insufficient_history |  | insufficient_history | 116.2975 | 0.019383 | 0.98062 | 6000 | 0 | 0 | 1 | 0.88151 | 14172.4817 | 100 | 100 |  |  |  |  | 6484.0751 | 709.2014 | 3.611 | 339.2899 | 0.1377 | 0.25643 | 0.0011985 | 0.35882 | 0.012346 | 0.024691 | 0.0001 | 0.037037 | RTE_2025: 0.85662; EFC_2025: 116.2975; UTI_2025: 0.72527
68460 | Roadrunner Crossing Energy Storage | TX | ERCO | Roadrunner Crossing Energy Storage LLC | Roadrunner Crossing Energy Storage LLC |  |  | TRUE | colocated_firming | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Co-Located Renewable Firming, Voltage or Reactive Power Support, Excess Wind and Solar Generation | 150 | 150 | 1 | <1.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1.0613 |  |  | 150 | 159.2
68475 | Kearsarge Riverpark I LLC | MA | ISNE | Kearsarge Riverpark I LLC | Kearsarge Riverpark I LLC |  |  | FALSE |  | LIB | CS |  | 5 | 11.2 | 2.24 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.80728 |  |  |  |  | insufficient_history |  | insufficient_history | 51.1607 | 0.0085268 | 0.99147 | 6000 | 0 | 0 | 1 | 0.83929 | 498.0933 | 5 | 5 |  |  |  |  | 67.3201 | 2.209 | 0.75483 | 1.2916 | 0.17285 | 0.10762 | 0.030002 | 0.1884 | 0.015814 | 0.0094887 | 0.0025791 | 0.017396 | RTE_2025: 0.81508; EFC_2025: 51.1607; UTI_2025: 0.46928
68476 | Kearsarge Riverpark II LLC | MA | ISNE | Kearsarge Riverpark I LLC | Kearsarge Riverpark I LLC |  |  | FALSE |  | LIB | CS |  | 5 | 11.2 | 2.24 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.81626 |  |  |  |  | insufficient_history |  | insufficient_history | 50.1786 | 0.0083631 | 0.99164 | 6000 | 0 | 0 | 1 | 0.89241 | 441.2133 | 5 | 5 |  |  |  |  | 67.3201 | 2.209 | 0.75483 | 1.2916 | 0.17285 | 0.10762 | 0.030002 | 0.1884 | 0.015814 | 0.0094887 | 0.0025791 | 0.017396 | RTE_2025: 0.83259; EFC_2025: 50.1786; UTI_2025: 0.46928
68493 | Central Heating Plant | MA | ISNE | Division of Capital Asset Management and Maintenance | University of Massachusetts Amherst |  |  | FALSE |  | LIB | CS | System Peak Shaving, Load Management, Backup Power | 3.3 | 3.3 | 1 | <1.5h | 2020.8182 |  |  | CELL_DEGRADATION | 0.85618 | 0.7215 | 0.95902 | -0.010215 | -4.0549 | -84.9089 | ok | 0.20354 | ok | 3589.697 | 0.59828 | 0.40172 | 6000 | 0 | 0 | 1 | 0.84553 | 439.8685 | 3.3 | 3.3 | 0.031648 | 0.75138 | 23 | 0.55798 | 24.3258 | 6.6516 | 0.044153 | 4.6673 | 0.044437 | 0.2033 | 0.0011985 | 0.39347 | 0.0037879 | 0.018939 | 0.0001 | 0.041667 | RTE_2024: 0.74424; RTE_2025: 0.75271; EFC_2024: 528.1818; EFC_2025: 420.6061; UTI_2024: 1.2251; UTI_2025: 0.82222
68496 | Lower Rio Energy Storage | TX | ERCO | VESI 38 LLC | VESI 38 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 60 | 120 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.80681 |  |  |  |  | insufficient_history |  | insufficient_history | 68.4917 | 0.011415 | 0.98858 | 6000 | 1 | 0 | 1 | 0.82497 | 4472.8619 | 60 | 60 |  |  |  |  | 239.3657 | 52.3617 | 122.0291 | 116.9019 | 0.022471 | 0.086899 | 0.14381 | 0.47079 | 0.0018939 | 0.0075758 | 0.014044 | 0.05303 | RTE_2025: 0.8183; EFC_2025: 68.4917; UTI_2025: 0.63676
68522 | Bishop Ranch - BR 8-O | CA | CISO | Executive Parkway BR8-O Solar Project 2020 LLC | Executive Parkway BR8-O Solar Project 2020 LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 | 322 | C | HYBRID_ARTEFACT |  | 1 |  |  |  |  | insufficient_history |  | insufficient_history | 0.90909 | 0.00015152 | 0.99985 | 6000 | 0 | 3 | 1 | 0.5 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.14286; EFC_2025: 0.90909; UTI_2025: 0 | FULL_OUTAGE
68523 | Bishop Ranch - BR 8-Q | CA | CISO | Executive Parkway BR8-Q Solar Project 2020 LLC | Executive Parkway BR8-Q Solar Project 2020 LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 | 318 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 5 | 1 | 0 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0; EFC_2025: 0; UTI_2025: 0 | FULL_OUTAGE
68524 | Bishop Ranch - BR 15-AA | CA | CISO | Alcosta Boulevard BR 15-AA Solar Project 2020 LLC | Alcosta Boulevard BR 15-AA Solar Project 2020 LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.82 |  |  |  |  | insufficient_history |  | insufficient_history | 13.6364 | 0.0022727 | 0.99773 | 6000 | 0 | 1 | 1 | 0.8 | 2 | 0.5 | 0.5 |  |  |  |  | 12.1202 | 0.0012041 | 0.0015138 | 0.14094 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0.83333; EFC_2025: 13.6364; UTI_2025: 0.1046
68525 | Bishop Ranch - BR 15-CC | CA | CISO | Alcosta Boulevard BR 15-CC Solar Project 2020, LLC | Alcosta Boulevard BR 15-CC Solar Project 2020, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 | 319 | C | FULL_OUTAGE | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 5 | 1 | 0 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2025: 0; EFC_2025: 0; UTI_2025: 0 | FULL_OUTAGE
68547 | Tipton 1 - (CA) | CA | CISO | CleanCapital Holdings | CleanCapital Holdings |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 1 | 3.9 | 3.9 | 2.5-4.5h | 2024 |  |  | HYBRID_ARTEFACT | 0.92136 | 0.7586 | 0.23341 | -0.00028407 |  |  | insufficient_history |  | insufficient_history | 229.2308 | 0.038205 | 0.96179 | 6000 | 0 | 0 | 1 | 0.925 | 0 | 1 | 1 | 0.0023341 | 0.90539 | 10 | 0.16303 | 30.4819 | 5.5566 | 0.68492 | 4.4306 | 0.051638 | 0.16199 | 0.017026 | 0.35714 | 0.0044183 | 0.014728 | 0.001444 | 0.036819 | RTE_2024: 0.33333; RTE_2025: 0.89749; EFC_2024: 0.25641; EFC_2025: 228.9744; UTI_2024: 0.010436; UTI_2025: 0.95056
68548 | Tipton 2 - (CA) | CA | CISO | CleanCapital Holdings | CleanCapital Holdings |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 0.7 | 2.9 | 4.1429 | 2.5-4.5h | 2024 | 351 | C | HYBRID_ARTEFACT |  | 0.85068 |  |  |  |  | insufficient_history |  | insufficient_history | 166.2069 | 0.027701 | 0.9723 | 6000 | 0 | 5 | 1 | 0.92941 | 0 | 0.7 | 0.7 |  |  |  |  | 16.8623 | 3.0739 | 0.37889 | 2.451 | 0.051638 | 0.16199 | 0.017026 | 0.35714 | 0.0044183 | 0.014728 | 0.001444 | 0.036819 | RTE_2024: 0.5; RTE_2025: 0.90584; EFC_2024: 0.34483; EFC_2025: 165.8621; UTI_2024: 0.014034; UTI_2025: 0.71627 | FULL_OUTAGE
68576 | Breckinridge Energy Storage | OK | SWPP | Breckinridge Energy Storage LLC | Breckinridge Energy Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 65 | 260 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.85242 |  |  |  |  | insufficient_history |  | insufficient_history | 190.7692 | 0.031795 | 0.96821 | 6000 | 0 | 0 | 1 | 0.86906 | 2789.914 | 65 | 65 |  |  |  |  | 3314.417 | 181.2586 | 110.6797 | 260.1485 | 0.081309 | 0.081309 | 0.039529 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034325 | 0.031802 | RTE_2025: 0.85538; EFC_2025: 190.7692; UTI_2025: 1.0302
68577 | Woodward Energy Storage | OK | SWPP | Woodward Energy Storage, LLC | Woodward Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 40 | 160 | 4 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.8435 |  |  |  |  | insufficient_history |  | insufficient_history | 206.5062 | 0.034418 | 0.96558 | 6000 | 0 | 0 | 1 | 0.86085 | 1490.5546 | 40 | 40 |  |  |  |  | 2252.9218 | 123.2076 | 75.2327 | 176.8318 | 0.081309 | 0.081309 | 0.039529 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034325 | 0.031802 | RTE_2025: 0.84755; EFC_2025: 206.5062; UTI_2025: 1.112
68596 | Dominguez Energy Storage | UT | PACE | Dominguez Grid, LLC | Dominguez Grid, LLC |  |  | FALSE |  | LIB | CS | System Peak Shaving | 200 | 800 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.92146 |  |  |  |  | insufficient_history |  | insufficient_history | 3.5638 | 0.00059396 | 0.99941 | 6000 | 0 | 0 | 1 | 0.92146 | 15795.6667 | 200 | 200 |  |  |  |  | 1478.7798 | 80.8714 | 50.6489 | 116.0694 | 0.081309 | 0.081309 | 0.040501 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035206 | 0.031802 | RTE_2025: 0.92146; EFC_2025: 3.5638; UTI_2025: 0.1529
68605 | Mauna Loa Macadamia Nut | HI | HECO | Macadamia Nut Road Solar Project 2019 | Macadamia Nut Road Solar Project 2019 |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.3 | 2.6 | 2.5-4.5h | 2021 |  |  | HYBRID_ARTEFACT | 0.86596 | 0.87 | -0.0026155 | -0.00065624 | 4.7219 | 211.87 | ok | -2.6952 | ok | 493.5256 | 0.082254 | 0.91775 | 6000 | 0 | 2 | 1 | 0.87879 | 29 | 0.5 | 0.5 | -1.3078e-05 | 0.87107 | 22 | 0.00019804 | 5.1605 | 0.47037 | 0.20929 | 0.0011521 | 0.08949 | 0.14465 | 0.052347 | 0.0011993 | 0.0078125 | 0.013021 | 0.0046084 | 0.0001 | RTE_2024: 0.86634; RTE_2025: 0.87931; EFC_2024: 134.6154; EFC_2025: 78.4615; UTI_2024: 0.55396; UTI_2025: 0.27996
68611 | International Battery Substation (IBSS) | AK | CEA | Chugach Electric Assn Inc | Chugach Electric Assn Inc |  |  | FALSE |  | LIB | CS | Ramping / Spinning Reserve | 40 | 80 | 2 | 1.5-2.5h | 2024 |  |  | UNDER_DISPATCH | [8 empty] | insufficient_history | 0.27625 | 4.6042e-05 | 0.99995 | 6000 | 1 | 0 | 1 | 0.029801 | 17888.0321 | 40 | 40 |  |  |  |  | 1.529 | 0.04181 | 0.00050461 | 0.02667 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2025: 0.0067568; EFC_2025: 0.2125; UTI_2025: 0.00056007
68613 | Guajillo Energy Storage | TX | ERCO | Guajillo Energy Storage, LLC | Guajillo Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Arbitrage | 228.7 | 228.7 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.89568 |  |  |  |  | insufficient_history |  | insufficient_history | 64.3201 | 0.01072 | 0.98928 | 6000 | 0 | 0 | 1 | 0.91633 | 2477.2172 | 65 | 65 |  |  |  |  | 4383.9425 | 205.4989 | 42.8661 | 393.252 | 0.11369 | 0.098277 | 0.016869 | 0.46243 | 0.010057 | 0.0086207 | 0.0014304 | 0.051724 | RTE_2025: 0.90234; EFC_2025: 64.3201; UTI_2025: 1.4979
68616 | Route 66 Energy Storage | NM | PNM | Route 66 Energy Storage | Route 66 Energy Storage |  |  | FALSE |  | LIB | CT |  | 49.5 | 198 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 49.5 | 49.5
68617 | Sky Ranch BESS II | NM | PNM | Sky Ranch Bess II | Sky Ranch Bess II |  |  | FALSE |  | LIB | CT |  | 100 | 400 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.88873 |  |  |  |  | insufficient_history |  | insufficient_history | 59.8725 | 0.0099787 | 0.99002 | 6000 | 0 | 0 | 1 | 0.89288 | 0 | 100 | 100 |  |  |  |  | 6211.0307 | 339.6684 | 211.9536 | 487.5036 | 0.081309 | 0.081309 | 0.040359 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035078 | 0.031802 | RTE_2025: 0.88878; EFC_2025: 59.8725; UTI_2025: 1.3089
68679 | Partridge Solar | MA | ISNE | SoCore Energy LLC | SoCore Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 3 | 3 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 1.0279 | 0.94563 | 0.13322 | 5.6724e-05 |  |  | ok | 1.152 | ok | 558.3333 | 0.093056 | 0.90694 | 6000 | 0 | 0 | 1 | 0.96774 | 0 | 3 | 3 | 0.0039967 | 0.95954 | 24 | 0.37767 | 33.7318 | 1.8447 | 0.02296 | 0.19612 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.96053; RTE_2025: 0.95888; EFC_2024: 146; EFC_2025: 217.6667; UTI_2024: 0.25408; UTI_2025: 0.31533
68680 | Saddleback Solar | MA | ISNE | SoCore Energy LLC | SoCore Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 2.5 | 2.5 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.99288 | 0.95898 | 0.06864 | 0.0012772 |  |  | ok | -0.60811 | ok | 918.9333 | 0.15316 | 0.84684 | 6000 | 0 | 0 | 1 | 0.96552 | 0 | 2.5 | 2.5 | 0.001716 | 0.96893 | 24 | 0.54247 | 37.0679 | 2.0272 | 0.02523 | 0.21552 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.96389; RTE_2025: 0.97414; EFC_2024: 277.6; EFC_2025: 271.2; UTI_2024: 0.41232; UTI_2025: 0.42731
68683 | Crockett BESS | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 10 | 24.8 | 2.48 | 1.5-2.5h | 2024 | 100 | B | UNATTRIBUTED |  | 0.61826 |  |  |  |  | insufficient_history |  | insufficient_history | 133.75 | 0.022292 | 0.97771 | 6000 | 0 | 2 | 1 | 0.63723 | 2939.4505 | 10 | 10 |  |  |  |  | 46.914 | 10.2625 | 21.6957 | 22.912 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.63703; EFC_2025: 133.75; UTI_2025: 0.61598 | FULL_OUTAGE
68684 | Century BESS | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 24.8 | 2.48 | 1.5-2.5h | 2024 | 356 | B | UNATTRIBUTED | 0.82852 | 0.83865 | -0.055303 | 0.040294 |  |  | insufficient_history |  | insufficient_history | 181.9355 | 0.030323 | 0.96968 | 6000 | 0 | 0 | 1 | 0.87542 | 20.9604 | 10 | 10 | -0.0055303 | 0.83866 | 12 | 0.0049744 | 53.7252 | 11.7525 | 24.8455 | 26.2384 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.83866; EFC_2025: 181.9355; UTI_2025: 0.64898 | LOW_ETA_AND_LOW_UTI
68685 | Liggett Switch | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 12.4 | 1.24 | <1.5h | 2024 |  |  | UNATTRIBUTED | 0.88787 | 0.80408 | 0.32395 | 0.0024064 |  |  | insufficient_history |  | insufficient_history | 202.8226 | 0.033804 | 0.9662 | 6000 | 0 | 0 | 1 | 0.86325 | 162.6987 | 10 | 10 | 0.032395 | 0.80764 | 12 | 0.55245 | 159.4429 | 7.4739 | 1.5384 | 14.3025 | 0.11369 | 0.098277 | 0.016649 | 0.46243 | 0.010057 | 0.0086207 | 0.0014114 | 0.051724 | RTE_2025: 0.80764; EFC_2025: 202.8226; UTI_2025: 0.93654
68686 | Citrus City BESS | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 9.9 | 24.7 | 2.4949 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.77002 |  |  |  |  | insufficient_history |  | insufficient_history | 90.9312 | 0.015155 | 0.98484 | 6000 | 3 | 0 | 2.475 | 0.83363 | 3859.4467 | 4 | 9.9 |  |  |  |  | 4.5871 | 1.0034 | 2.1214 | 2.2403 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.77932; EFC_2025: 90.9312; UTI_2025: 0.056179
68687 | Rio Grande City BESS 2 | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 9.9 | 24.7 | 2.4949 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.7747 |  |  |  |  | insufficient_history |  | insufficient_history | 77.2874 | 0.012881 | 0.98712 | 6000 | 3 | 0 | 4.95 | 0.82014 | 4509.4733 | 2 | 9.9 |  |  |  |  | 6.0467 | 1.3227 | 2.7963 | 2.9531 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.76914; EFC_2025: 77.2874; UTI_2025: 0.074054
68742 | Skyline Solar | MA | ISNE | SoCore Energy LLC | SoCore Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 3 | 3 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 0.99604 | 0.95961 | 0.056309 | 0.00084252 |  |  | ok | 0.084388 | ok | 554.2222 | 0.09237 | 0.90763 | 6000 | 0 | 0 | 1 | 0.95614 | 0 | 3 | 3 | 0.0016893 | 0.96916 | 24 | 0.58913 | 37.0679 | 2.0272 | 0.02523 | 0.21552 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.96128; RTE_2025: 0.97414; EFC_2024: 140.6667; EFC_2025: 226; UTI_2024: 0.23588; UTI_2025: 0.35609
68743 | Adams Grove Solar | MA | ISNE | SoCore Energy LLC | SoCore Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 3.3 | 3.3 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT | 1.0104 | 0.94352 | 0.25317 | 0.0033177 |  |  | ok | 0.32056 | ok | 1308.5859 | 0.2181 | 0.7819 | 6000 | 0 | 0 | 1 | 0.95455 | 0 | 3.3 | 3.3 | 0.0083547 | 0.95378 | 24 | 0.76396 | 88.2215 | 4.8247 | 0.060048 | 0.51293 | 0.11415 | 0.11415 | 0.0011985 | 0.039599 | 0.010101 | 0.010101 | 0.0001 | 0.003367 | RTE_2024: 0.95213; RTE_2025: 0.95535; EFC_2024: 385.7576; EFC_2025: 408.4848; UTI_2024: 0.56578; UTI_2025: 0.73038
68773 | Apollo | MA | ISNE | Sunrise on Wing Ln. LLC | Sunrise on Wing Ln. LLC |  |  | TRUE | colocated_firming,pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Co-Located Renewable Firming, System Peak Shaving | 1.3 | 2.8 | 2.1538 | 1.5-2.5h | 2021 | 204 | C | HYBRID_ARTEFACT | 0.9261 | 0.92075 | 0.0699 | 0.0056034 |  |  | insufficient_history | -0.56772 | ok | 1607.381 | 0.2679 | 0.7321 | 6000 | 0 | 3 | 1 | 0.9802 | 187 | 1.3 | 1.3 | 0.0009087 | 0.92832 | 19 | 0.074964 | 65.1045 | 1.978 | 0.70935 | 0.18926 | 0.14392 | 0.082709 | 0.024022 | 0.025567 | 0.01295 | 0.0071942 | 0.0020522 | 0.0021583 | RTE_2024: 0.95986; RTE_2025: 0.88187; EFC_2024: 401.4286; EFC_2025: 269.2857; UTI_2024: 3.3349; UTI_2025: 2.8924 | FULL_OUTAGE
68801 | Kingman Energy Storage | AZ | WALC | Kingman Energy Storage LLC | Kingman Energy Storage LLC |  |  | FALSE |  | LIB | CS |  | 50 | 200 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.73118 |  |  |  |  | insufficient_history |  | insufficient_history | 25.37 | 0.0042283 | 0.99577 | 6000 | 0 | 0 | 1 | 0.89059 | 9003.517 | 50 | 50 |  |  |  |  | 123.9665 | 6.7795 | 4.215 | 9.7301 | 0.081309 | 0.081309 | 0.040219 | 0.31725 | 0.0070671 | 0.0070671 | 0.003495 | 0.031802 | RTE_2025: 0.83139; EFC_2025: 25.37; UTI_2025: 0.052874
68802 | Minco II Energy Storage | OK | SWPP | Minco II Energy Storage LLC | Minco II Energy Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 65 | 65 | 1 | <1.5h | 2025 |  |  | HEALTHY |  | 0.86068 |  |  |  |  | insufficient_history |  | insufficient_history | 911.2615 | 0.15188 | 0.84812 | 6000 | 0 | 0 | 1 | 0.86593 | 0 | 65 | 65 |  |  |  |  | 7319.2636 | 326.8916 | 216.6022 | 223.4123 | 0.13542 | 0.11205 | 0.058871 | 0.22481 | 0.012126 | 0.009903 | 0.0052195 | 0.021221 | RTE_2025: 0.86275; EFC_2025: 911.2615; UTI_2025: 4.4039
68809 | Hidden Lakes Reliability Project | TX | ERCO | Evelyn Energy Storage LLC | Evelyn Energy Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 220 | 440 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.59607 |  |  |  |  | insufficient_history |  | insufficient_history | 1.9091 | 0.00031818 | 0.99968 | 6000 | 0 | 0 | 1 | 0.90291 | 32515.8491 | 220 | 220 |  |  |  |  | 26.2718 | 5.747 | 13.797 | 12.8307 | 0.022471 | 0.086899 | 0.14749 | 0.47079 | 0.0018939 | 0.0075758 | 0.014467 | 0.05303 | RTE_2025: 0.59072; EFC_2025: 1.9091; UTI_2025: 0.019061
68816 | Google Bayhill Solar PV and Microgrid | CA | CISO | Google, Inc. | Google, Inc. |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage, System Peak Shaving, Backup Power | 2.6 | 5.3 | 2.0385 | 1.5-2.5h | 2024 | 337 | C | HYBRID_ARTEFACT | 0.67247 | 0.68529 | 0.0066054 | -0.0059356 |  |  | insufficient_history | 8.3829 | ok | 93.2075 | 0.015535 | 0.98447 | 6000 | 0 | 1 | 0.88 | 0.83582 | 0 | 2.5 | 2.2 | 0.00017174 | 0.73393 | 18 | 0.0010258 | 86.8612 | 0.0086296 | 0.010849 | 1.01 | 0.48343 | 0.0011993 | 0.0011985 | 0.3562 | 0.055046 | 0.0001 | 0.0001 | 0.036697 | RTE_2024: 0.73123; RTE_2025: 0.72028; EFC_2024: 34.9057; EFC_2025: 58.3019; UTI_2024: 0.18265; UTI_2025: 0.17071 | LOW_ETA_AND_LOW_UTI
68842 | Chillingham Storage | TX | ERCO | Chillingham Storage LLC | Chillingham Storage LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Load Following, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 150 | 150 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.81658 |  |  |  |  | insufficient_history |  | insufficient_history | 261.1333 | 0.043522 | 0.95648 | 6000 | 0 | 0 | 1 | 0.83987 | 1951.3333 | 150 | 150 |  |  |  |  | 5663.1768 | 265.4635 | 55.128 | 508.003 | 0.11369 | 0.098277 | 0.016795 | 0.46243 | 0.010057 | 0.0086207 | 0.001424 | 0.051724 | RTE_2025: 0.83208; EFC_2025: 261.1333; UTI_2025: 2.8778
68868 | Shallow Basket | NM | PNM | Shallow Basket Energy, LLC | Shallow Basket Energy, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, System Peak Shaving | 50 | 200 | 4 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.90373 |  |  |  |  | insufficient_history |  | insufficient_history | 143.74 | 0.023957 | 0.97604 | 6000 | 0 | 0 | 1 | 0.90237 | 0 | 50 | 50 |  |  |  |  | 2984.5313 | 163.2179 | 100.7441 | 234.2558 | 0.081309 | 0.081309 | 0.03994 | 0.31725 | 0.0070671 | 0.0070671 | 0.0034697 | 0.031802 | RTE_2025: 0.90357; EFC_2025: 143.74; UTI_2025: 1.2381
68874 | Inertia Energy Storage | TX | ERCO | Inertia Energy Storage LLC | Inertia Energy Storage LLC |  |  | FALSE |  | LIB | CS | Excess Wind and Solar Generation | 13 | 45 | 3.4615 | 2.5-4.5h | 2025 |  |  | UNATTRIBUTED |  | 0.79769 |  |  |  |  | insufficient_history |  | insufficient_history | 195.6889 | 0.032615 | 0.96739 | 6000 | 0 | 0 | 1 | 0.80395 | 711.3066 | 13 | 13 |  |  |  |  | 955.9537 | 61.3712 | 2.8462 | 16.674 | 0.12376 | 0.14367 | 0.0056883 | 0.12376 | 0.01101 | 0.012925 | 0.0004768 | 0.01101 | RTE_2025: 0.79946; EFC_2025: 195.6889; UTI_2025: 1.0725
68875 | Wakefield MA BESS 1 | MA | ISNE | Wakefield MA BESS 1 LLC | Wakefield MA BESS 1 LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 5 | 22.4 | 4.48 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.88736 |  |  |  |  | insufficient_history |  | insufficient_history | 97.5 | 0.01625 | 0.98375 | 6000 | 0 | 0 | 1 | 0.89464 | 478.1124 | 5 | 5 |  |  |  |  | 281.7669 | 30.8185 | 0.16854 | 0.042757 | 0.12884 | 0.24108 | 0.0011985 | 0.0011993 | 0.011494 | 0.022989 | 0.0001 | 0.0001 | RTE_2025: 0.88961; EFC_2025: 97.5; UTI_2025: 0.75621
68878 | Longhorn Storage | TX | ERCO | Longhorn Storage LLC | Longhorn Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 165 | 165 | 1 | <1.5h | 2024 |  |  | HEALTHY |  | 0.86496 |  |  |  |  | insufficient_history |  | insufficient_history | 483.3899 | 0.080565 | 0.91944 | 6000 | 0 | 0 | 1 | 0.87939 | 0 | 150 | 150 |  |  |  |  | 4468.0929 | 209.4435 | 43.3019 | 400.8006 | 0.11369 | 0.098277 | 0.016722 | 0.46243 | 0.010057 | 0.0086207 | 0.0014177 | 0.051724 | RTE_2025: 0.86502; EFC_2025: 334.6545; UTI_2025: 1.914
68879 | Bocanova Energy Storage | TX | ERCO | Bocanova Power LLC | Bocanova Power LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Voltage or Reactive Power Support | 150 | 300 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.79185 |  |  |  |  | insufficient_history |  | insufficient_history | 88.5167 | 0.014753 | 0.98525 | 6000 | 0 | 0 | 1 | 0.79794 | 10709.8259 | 150 | 150 |  |  |  |  | 816.5123 | 178.6135 | 416.2596 | 398.77 | 0.022471 | 0.086899 | 0.14381 | 0.47079 | 0.0018939 | 0.0075758 | 0.014044 | 0.05303 | RTE_2025: 0.79435; EFC_2025: 88.5167; UTI_2025: 0.86884
68891 | Visalia - (CA) | CA | CISO | CleanCapital Holdings | CleanCapital Holdings |  |  | TRUE | pv_same_plant | LIB | CS | Excess Wind and Solar Generation | 1 | 3.9 | 3.9 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.88901 |  |  |  |  | insufficient_history |  | insufficient_history | 129.7436 | 0.021624 | 0.97838 | 6000 | 0 | 0 | 1 | 0.89423 | 0 | 1 | 1 |  |  |  |  | 27.2391 | 4.9655 | 0.61857 | 3.9593 | 0.051638 | 0.16199 | 0.017204 | 0.35714 | 0.0044183 | 0.014728 | 0.0014593 | 0.036819 | RTE_2025: 0.88928; EFC_2025: 129.7436; UTI_2025: 0.82219
68895 | Libra Storage | TX | ERCO | Libra Storage LLC | Libra Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 236.3 | 236.3 | 1 | <1.5h | 2023 |  |  | UNATTRIBUTED |  | 0.70107 |  |  |  |  | insufficient_history |  | insufficient_history | 435.7522 | 0.072625 | 0.92737 | 6000 | 1 | 0 | 1 | 0.73194 | 9208.9967 | 200 | 200 |  |  |  |  | 324.8126 | 88.8166 | 188.3959 | 328.5962 | 0.010638 | 0.052071 | 0.082622 | 0.46223 | 0.00089127 | 0.0044563 | 0.0075189 | 0.051693 | RTE_2025: 0.70285; EFC_2025: 166.0008; UTI_2025: 1.0735
68896 | Sun Valley Storage | TX | ERCO | Sun Valley Storage LLC | Sun Valley Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 123.3 | 123 | 0.99757 | <1.5h | 2024 |  |  | UNATTRIBUTED |  | 0.80026 |  |  |  |  | insufficient_history |  | insufficient_history | 525 | 0.0875 | 0.9125 | 6000 | 0 | 0 | 1 | 0.80965 | 544.7906 | 100 | 100 |  |  |  |  | 2406.7763 | 112.8185 | 23.3594 | 215.8946 | 0.11369 | 0.098277 | 0.016746 | 0.46243 | 0.010057 | 0.0086207 | 0.0014198 | 0.051724 | RTE_2025: 0.80098; EFC_2025: 210; UTI_2025: 1.3842
68906 | Pine Forest Solar I | TX | DOPD | Pine Forest Solar I, LLC | Pine Forest Solar I, LLC |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 200 | 200 | 1 | <1.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.97233 |  |  |  |  | insufficient_history |  | insufficient_history | 49.2 | 0.0082 | 0.9918 | 6000 | 0 | 0 | 1 | 0.97233 | 0 | 200 | 200 |  |  |  |  | 8757.4846 | 391.1251 | 269.4156 | 267.3124 | 0.13542 | 0.11205 | 0.061055 | 0.22481 | 0.012126 | 0.009903 | 0.0054259 | 0.021221 | RTE_2025: 0.97233; EFC_2025: 49.2; UTI_2025: 2.6472
68912 | Padua 1 | TX | ERCO | Padua 1 | Padua 1 |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation, Load Following, Ramping / Spinning Reserve, Backup Power | 50 | 200 | 4 | 2.5-4.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.7416 |  |  |  |  | insufficient_history |  | insufficient_history | 52.09 | 0.0086817 | 0.99132 | 6000 | 1 | 0 | 1 | 0.82651 | 18749.9032 | 50 | 50 |  |  |  |  | 1589.4852 | 102.0432 | 4.7372 | 27.7241 | 0.12376 | 0.14367 | 0.005694 | 0.12376 | 0.01101 | 0.012925 | 0.00047727 | 0.01101 | RTE_2025: 0.7943; EFC_2025: 52.09; UTI_2025: 0.39787
68950 | Marston Mills Solar | MA | ISNE | SoCore Energy LLC | SoCore Energy LLC |  |  | TRUE | pv_same_plant | LIB | CS | Load Management, Voltage or Reactive Power Support | 3 | 3 | 1 | <1.5h | 2021 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 3 | 3
68997 | Thermo Fisher Pleasanton | CA | CISO | TotalEnergies Renewables USA LLC | TotalEnergies Renewables USA LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Load Management, Excess Wind and Solar Generation | 0.7 | 2.6 | 3.7143 | 2.5-4.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.91285 |  |  |  |  | insufficient_history |  | insufficient_history | 141.1538 | 0.023526 | 0.97647 | 6000 | 0 | 0 | 1 | 0.90588 | 0 | 0.6 | 0.6 |  |  |  |  | 17.8352 | 3.2512 | 0.4044 | 2.5924 | 0.051638 | 0.16199 | 0.017179 | 0.35714 | 0.0044183 | 0.014728 | 0.0014571 | 0.036819 | RTE_2025: 0.89951; EFC_2025: 141.1538; UTI_2025: 0.88823
69023 | Knightdale Battery | NC | CPLE | Duke Energy Progress - (NC) | Duke Energy Progress - (NC) |  |  | FALSE |  | LIB | CS | Transmission and Distribution Deferral | 100 | 200 | 2 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.73705 |  |  |  |  | insufficient_history |  | insufficient_history | 29.005 | 0.0048342 | 0.99517 | 6000 | 0 | 0 | 1 | 0.83389 | 3207.3939 | 100 | 100 |  |  |  |  | 821.9319 | 1.1642 | 1.4636 | 243.7173 | 0.045275 | 0.0011993 | 0.0011985 | 0.54509 | 0.003861 | 0.0001 | 0.0001 | 0.065637 | RTE_2025: 0.79033; EFC_2025: 29.005; UTI_2025: 0.63077
69026 | Tanzanite Storage | TX | ERCO | Tanzanite Energy Storage LLC | Tanzanite Energy Storage LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Load Following, Ramping / Spinning Reserve, System Peak Shaving, Voltage or Reactive Power Support | 283.2 | 283.2 | 1 | <1.5h | 2025 |  |  | HEALTHY |  | 0.84301 |  |  |  |  | insufficient_history |  | insufficient_history | 96.4901 | 0.016082 | 0.98392 | 6000 | 0 | 0 | 0.97466 | 0.84689 | 0 | 264.4 | 257.7 |  |  |  |  | 10085.5037 | 472.7617 | 98.7629 | 904.6982 | 0.11369 | 0.098277 | 0.016894 | 0.46243 | 0.010057 | 0.0086207 | 0.0014325 | 0.051724 | RTE_2025: 0.8434; EFC_2025: 96.4901; UTI_2025: 2.9343
69042 | Kit Carson Co-Op | NM | PNM | Solar DG NM Amalia, LLC | Solar DG NM Amalia, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 12.9 | 25.9 | 2.0078 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 12.9 | 12.9
69045 | Sealy BESS | TX | ERCO | Sealy Power, LLC | Sealy Power, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 200 | 400 | 2 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.94784 |  |  |  |  | insufficient_history |  | insufficient_history | 135.06 | 0.02251 | 0.97749 | 6000 | 0 | 0 | 1 | 0.996 | 0 | 200 | 200 |  |  |  |  | 1437.0283 | 314.3524 | 732.5999 | 701.8189 | 0.022471 | 0.086899 | 0.14381 | 0.47079 | 0.0018939 | 0.0075758 | 0.014044 | 0.05303 | RTE_2025: 0.94972; EFC_2025: 135.06; UTI_2025: 1.0898
69072 | Fresno-Clovis RWRF | CA | CISO | Forefront Power, LLC | Forefront Power, LLC |  |  | TRUE | pv_same_plant | LIB | BL | System Peak Shaving | 2.3 | 2.3 | 1 | <1.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 2.3 | 2.3
69073 | 20 Bedford | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 1 | 1 | 1 | <1.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 0.66667 |  |  | 0.3 | 0.2
69075 | 376 Nash | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 0.5 | 2 | 4 | 2.5-4.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.3 | 0.3
69076 | 342 Circuit | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 1 | 1.1 | 1.1 | <1.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.4 | 0.4
69122 | Jackson Fuller Energy Storage | CO | PSCO | Jackson Fuller Energy Storage, LLC | Jackson Fuller Energy Storage, LLC |  |  | FALSE |  | LIB | CS | Load Following, System Peak Shaving | 100 | 100 | 1 | <1.5h | 2025 |  |  | HEALTHY |  | 0.8887 |  |  |  |  | insufficient_history |  | insufficient_history | 408.6 | 0.0681 | 0.9319 | 6000 | 0 | 0 | 1 | 0.85276 | 0 | 3.3 | 3.3 |  |  |  |  | 9978.5485 | 445.6601 | 301.8631 | 304.584 | 0.13542 | 0.11205 | 0.0601 | 0.22481 | 0.012126 | 0.009903 | 0.0053355 | 0.021221 | RTE_2025: 0.87884; EFC_2025: 408.6; UTI_2025: 4.423
69128 | Chesapeake Beach BESS | MD | PJM | Chesapeake Beach BESS LLC | Chesapeake Beach BESS LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation | 1.1 | 2.3 | 2.0909 | 1.5-2.5h | 2023 | 293 | B | PARTIAL_AVAILABILITY | 0.86819 | 0.73675 | 0.52348 | 0.00015405 |  |  | insufficient_history |  | insufficient_history | 773.4783 | 0.12891 | 0.87109 | 6000 | 0 | 2 | 1 | 0.83529 | 113.4947 | 1.1 | 1.1 | 0.0057582 | 0.81461 | 11 | 0.9868 | 67.3201 | 2.209 | 0.74681 | 1.2916 | 0.17285 | 0.10762 | 0.029692 | 0.1884 | 0.015814 | 0.0094887 | 0.0025517 | 0.017396 | RTE_2025: 0.76516; EFC_2025: 257.8261; UTI_2025: 1.1062 | PARTIAL_AVAILABILITY
69129 | Dudley Landfill Solar LLC | MA | ISNE | Dudley Landfill Solar LLC | Dudley Landfill Solar LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Frequency Regulation, Excess Wind and Solar Generation | 1.3 | 2.8 | 2.1538 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.3 | 1.3
69131 | Hampden Landfill Solar LLC | MA | ISNE | Hampden Landfill Solar LLC | Hampden Landfill Solar LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | System Peak Shaving, Backup Power | 3 | 6.7 | 2.2333 | 1.5-2.5h | 2024 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 3 | 3
69171 | Allen 1 Battery Energy Storage System | NC | DUK | Duke Energy Carolinas, LLC | Duke Energy Carolinas, LLC |  |  | FALSE |  | LIB | CS | Arbitrage, Frequency Regulation | 50 | 200 | 4 | 2.5-4.5h | 2025 |  |  | HEALTHY |  | 0.88505 |  |  |  |  | insufficient_history |  | insufficient_history | 58.395 | 0.0097325 | 0.99027 | 6000 | 0 | 0 | 1 | 0.89639 | 0 | 50 | 50 |  |  |  |  | 3028.8792 | 165.6431 | 103.3616 | 237.7366 | 0.081309 | 0.081309 | 0.040359 | 0.31725 | 0.0070671 | 0.0070671 | 0.0035078 | 0.031802 | RTE_2025: 0.88551; EFC_2025: 58.395; UTI_2025: 1.276
69187 | Big Bend 1 Solar and Battery Storage | FL | TEC | Tampa Electric Co | Tampa Electric Co |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, System Peak Shaving | 12.6 | 25.2 | 2 | 1.5-2.5h | 2019 |  |  | HYBRID_ARTEFACT |  | 0.6 |  |  |  |  | insufficient_history |  | insufficient_history | 59.0476 | 0.0098413 | 0.99016 | 6000 | 0 | 0 | 1 | 0.6 | 0 | 12.6 | 12.6 |  |  |  |  | 47.8659 | 0.78531 | 0.97897 | 0.0030724 | 0.27826 | 0.093193 | 0.088268 | 0.0011993 | 0.027174 | 0.0081522 | 0.0080835 | 0.0001 | RTE_2025: 0.6; EFC_2025: 0.95238; UTI_2025: 0.040151
69190 | GreenStruxure BBU004, LLC | CA | CISO | ClearGen LLC | ClearGen LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Arbitrage | 0.2 | 0.4 | 2 | 1.5-2.5h | 2023 | 370 | C | HYBRID_ARTEFACT | 0.79007 | 0.85492 | -0.13263 | -0.0013863 |  |  | insufficient_history |  | insufficient_history | 270.8333 | 0.045139 | 0.95486 | 6000 | 0 | 0 | 1 | 0.90909 | 0 | 0.2 | 0.2 | -0.00026526 | 0.83871 | 12 | 0.11366 | 1.6728 | 0.50315 | 0.055528 | 0.00051206 | 0.066091 | 0.31344 | 0.031937 | 0.0011993 | 0.005698 | 0.031339 | 0.0027511 | 0.0001 | RTE_2025: 0.83871; EFC_2025: 130; UTI_2025: 0.39457 | LOW_ETA_AND_LOW_UTI
69191 | GreenStruxure REP009, LLC | CA | CISO | ClearGen LLC | ClearGen LLC |  |  | TRUE | dc_coupled | LIB | CS | Ramping / Spinning Reserve | 0.2 | 0.4 | 2 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 1.0366 | 0.84421 | 1.0203 | 0.00026833 |  |  | insufficient_history |  | insufficient_history | 574.7917 | 0.095799 | 0.9042 | 6000 | 0 | 0 | 1 | 0.83333 | 0 | 0.2 | 0.2 | 0.0020407 | 0.84762 | 12 | 0.50663 | 3.3456 | 1.0063 | 0.11106 | 0.0010241 | 0.066091 | 0.31344 | 0.031937 | 0.0011993 | 0.005698 | 0.031339 | 0.0027511 | 0.0001 | RTE_2025: 0.84762; EFC_2025: 222.5; UTI_2025: 0.73648
69210 | Salem Henningsen | OR | PGE | Lineage Logistics Solar PV - Salem OR | Lineage Logistics Solar PV - Salem OR |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage | 1 | 2 | 2 | 1.5-2.5h | 2024 | 305 | C | HYBRID_ARTEFACT | 1 | 1 | 4.9103e-16 | -1.3801e-17 |  |  | insufficient_history |  | insufficient_history | 63.3333 | 0.010556 | 0.98944 | 6000 | 0 | 2 | 1 | 1 | 3 | 1 | 1 | 4.9103e-18 | 1 | 12 |  | 9.9388 | 0.27177 | 0.00328 | 0.17336 | 0.2212 | 0.1175 | 0.0011985 | 0.2212 | 0.020833 | 0.010417 | 0.0001 | 0.020833 | RTE_2025: 1; EFC_2025: 38; UTI_2025: 0.14539 | PARTIAL_AVAILABILITY
69244 | Cross Trails Energy Storage Project | TX | ERCO | Energy Vault, Inc. | Energy Vault, Inc. |  |  | FALSE |  | LIB | CS | Frequency Regulation | 58.3 | 114 | 1.9554 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.80537 |  |  |  |  | insufficient_history |  | insufficient_history | 122.4035 | 0.020401 | 0.9796 | 6000 | 0 | 0 | 1 | 0.83908 | 7306.7225 | 57 | 57 |  |  |  |  | 335.2093 | 73.3276 | 163.7074 | 163.7102 | 0.022471 | 0.086899 | 0.13862 | 0.47079 | 0.0018939 | 0.0075758 | 0.013453 | 0.05303 | RTE_2025: 0.81645; EFC_2025: 122.4035; UTI_2025: 0.89038
69250 | Suwannee | FL | FPC | Duke Energy Florida, LLC | Duke Energy Florida, LLC |  |  | FALSE |  | NAB | CS | Frequency Regulation | 5 | 5 | 1 | <1.5h | 2025 |  |  | UNATTRIBUTED |  | 0.58404 |  |  |  |  | insufficient_history |  | insufficient_history | 835 | 0.13917 | 0.86083 | 6000 | 0 | 0 | 1 | 0.72368 | 1268.0968 | 5 | 5 |  |  |  |  | 377.355 | 16.8534 | 11.1672 | 11.5183 | 0.13542 | 0.11205 | 0.058871 | 0.22481 | 0.012126 | 0.009903 | 0.0052195 | 0.021221 | RTE_2025: 0.68331; EFC_2025: 835; UTI_2025: 3.2952
69288 | Palm Springs DAC PV | CA | CISO | Palm Springs USD | Palm Springs USD |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage, Excess Wind and Solar Generation | 0.3 | 0.6 | 2 | 1.5-2.5h | 2023 |  |  | HYBRID_ARTEFACT | 0.91347 | 0.8241 | 0.33146 | 0.00014212 |  |  | insufficient_history |  | insufficient_history | 355 | 0.059167 | 0.94083 | 6000 | 1 | 0 | 1 | 0.84615 | 0 | 0.3 | 0.3 | 0.00099439 | 0.83529 | 10 | 0.45627 | 3.1365 | 0.94341 | 0.10472 | 0.00096012 | 0.066091 | 0.31344 | 0.032115 | 0.0011993 | 0.005698 | 0.031339 | 0.0027669 | 0.0001 | RTE_2025: 0.83529; EFC_2025: 118.3333; UTI_2025: 0.43567
69298 | PP Jaguar BESS LLC | TX | ERCO | PP Jaguar BESS LLC | PP Jaguar BESS LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Transmission and Distribution Deferral, System Peak Shaving, Voltage or Reactive Power Support | 300 | 680 | 2.2667 | 1.5-2.5h | 2025 |  |  | HEALTHY |  | 0.87599 |  |  |  |  | insufficient_history |  | insufficient_history | 33.9912 | 0.0056652 | 0.99433 | 6000 | 0 | 0 | 1 | 0.87599 | 0 | 300 | 300 |  |  |  |  | 3212.9496 | 702.8383 | 1739.7481 | 1569.1469 | 0.022471 | 0.086899 | 0.15137 | 0.47079 | 0.0018939 | 0.0075758 | 0.014916 | 0.05303 | RTE_2025: 0.87599; EFC_2025: 33.9912; UTI_2025: 1.2259
69300 | Regis Continental | TX | ERCO | Regis Continental LLC | Regis Continental LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 | 162 | B | FULL_OUTAGE |  | 0.85423 |  |  |  |  | insufficient_history |  | insufficient_history | 86.5152 | 0.014419 | 0.98558 | 6000 | 3 | 4 | 1 | 0.86398 | 288 | 9.9 | 9.9 |  |  |  |  | 0 | 0 | 0 | 0 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.85865; EFC_2025: 57.6768; UTI_2025: 0 | FULL_OUTAGE
69301 | Regis Gregory | TX | ERCO | Regis Gregory LLC | Regis Gregory LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.64933 |  |  |  |  | insufficient_history |  | insufficient_history | 59.6296 | 0.0099383 | 0.99006 | 6000 | 1 | 0 | 1 | 0.84099 | 828.027 | 9.9 | 9.9 |  |  |  |  | 14.7632 | 0.69203 | 0.1435 | 1.3243 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.77489; EFC_2025: 51.1111; UTI_2025: 0.11799
69302 | Regis Palacios | TX | ERCO | Regis Palacios LLC | Regis Palacios LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.71738 |  |  |  |  | insufficient_history |  | insufficient_history | 91.9192 | 0.01532 | 0.98468 | 6000 | 0 | 0 | 1 | 0.84375 | 583.5256 | 9.9 | 9.9 |  |  |  |  | 64.9582 | 3.0449 | 0.6314 | 5.8269 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.7943; EFC_2025: 78.7879; UTI_2025: 0.49446
69331 | Regis Carrizo Springs | TX | ERCO | Regis Carrizo Springs LLC | Regis Carrizo Springs LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.65647 |  |  |  |  | insufficient_history |  | insufficient_history | 34.4444 | 0.0057407 | 0.99426 | 6000 | 2 | 0 | 1 | 0.84291 | 926.5666 | 9.9 | 9.9 |  |  |  |  | 5.9053 | 0.27681 | 0.0574 | 0.52972 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.74292; EFC_2025: 34.4444; UTI_2025: 0.043524
69333 | Regis Goodwin LLC | TX | ERCO | Regis Goodwin LLC | Regis Goodwin LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.60955 |  |  |  |  | insufficient_history |  | insufficient_history | 27.8788 | 0.0046465 | 0.99535 | 6000 | 3 | 0 | 1 | 0.875 | 946.5666 | 9.9 | 9.9 |  |  |  |  | 14.7632 | 0.69203 | 0.1435 | 1.3243 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.70051; EFC_2025: 27.8788; UTI_2025: 0.10881
69334 | Johnson City BESS | TX | ERCO | Pedernales Electric Coop, Inc | Pedernales Electric Coop, Inc |  |  | FALSE |  | LIB | CS |  | 2.3 | 4.5 | 1.9565 | 1.5-2.5h | 2020 |  |  | UNDER_DISPATCH |  | 0.3602 |  |  |  |  | insufficient_history |  | insufficient_history | 225.1667 | 0.037528 | 0.96247 | 6000 | 0 | 0 | 1 | 0.43396 | 995.765 | 2.3 | 2.3 |  |  |  |  | 11.8484 | 1.2959 | 0.73251 | 1.0333 | 0.10203 | 0.19366 | 0.088081 | 0.41615 | 0.0089686 | 0.017937 | 0.0080647 | 0.044843 | RTE_2025: 0.37331; EFC_2025: 42.8889; UTI_2025: 0.16183
69344 | Regis Hearn | TX | ERCO | Regis Hearn LLC | Regis Hearn LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 | 301 | B | UNDER_DISPATCH |  | 0.51796 |  |  |  |  | insufficient_history |  | insufficient_history | 31.1953 | 0.0051992 | 0.9948 | 6000 | 1 | 2 | 1 | 0.72662 | 1255 | 9.9 | 9.9 |  |  |  |  | 1.4763 | 0.069203 | 0.014286 | 0.13243 | 0.11369 | 0.098277 | 0.016698 | 0.46243 | 0.010057 | 0.0086207 | 0.0014156 | 0.051724 | RTE_2025: 0.63743; EFC_2025: 22.0202; UTI_2025: 0.009901 | FULL_OUTAGE
69345 | Regis Mason | TX | ERCO | Regis Mason LLC | Regis Mason LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.74551 |  |  |  |  | insufficient_history |  | insufficient_history | 173.367 | 0.028895 | 0.97111 | 6000 | 0 | 0 | 1 | 0.87617 | 294 | 9.9 | 9.9 |  |  |  |  | 139.8816 | 6.557 | 1.3617 | 12.5478 | 0.11369 | 0.098277 | 0.016795 | 0.46243 | 0.010057 | 0.0086207 | 0.001424 | 0.051724 | RTE_2025: 0.82433; EFC_2025: 109.4949; UTI_2025: 0.9264
69346 | Regis Monte Cristo LLC | TX | ERCO | Regis Monte Cristo LLC | Regis Monte Cristo LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.78787 |  |  |  |  | insufficient_history |  | insufficient_history | 136.2374 | 0.022706 | 0.97729 | 6000 | 3 | 0 | 1 | 0.87195 | 372.17 | 9.9 | 9.9 |  |  |  |  | 138.0362 | 6.4705 | 1.3417 | 12.3822 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.82682; EFC_2025: 108.9899; UTI_2025: 0.92574
69347 | Regis Muenster | TX | ERCO | Regis Muenster LLC | Regis Muenster LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.81427 |  |  |  |  | insufficient_history |  | insufficient_history | 200.5051 | 0.033418 | 0.96658 | 6000 | 0 | 0 | 1 | 0.85385 | 220 | 9.9 | 9.9 |  |  |  |  | 163.5028 | 7.6643 | 1.5916 | 14.6667 | 0.11369 | 0.098277 | 0.016795 | 0.46243 | 0.010057 | 0.0086207 | 0.001424 | 0.051724 | RTE_2025: 0.8352; EFC_2025: 120.303; UTI_2025: 1.157
69348 | Regis Pirate | TX | ERCO | Regis Sinton-Pirate LLC | Regis Sinton-Pirate LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.6582 |  |  |  |  | insufficient_history |  | insufficient_history | 238.9394 | 0.039823 | 0.96018 | 6000 | 1 | 0 | 1 | 0.83632 | 966.9081 | 9.9 | 9.9 |  |  |  |  | 34.6936 | 1.6263 | 0.33524 | 3.1121 | 0.11369 | 0.098277 | 0.016674 | 0.46243 | 0.010057 | 0.0086207 | 0.0014135 | 0.051724 | RTE_2025: 0.80323; EFC_2025: 150.9091; UTI_2025: 0.26554
69349 | Regis Falfurrias | TX | ERCO | Regis Falfurrias LLC | Regis Falfurrias LLC |  |  | FALSE |  | LIB | CS |  | 9.9 | 9.9 | 1 | <1.5h | 2024 |  |  | UNDER_DISPATCH |  | 0.64373 |  |  |  |  | insufficient_history |  | insufficient_history | 115.1936 | 0.019199 | 0.9808 | 6000 | 1 | 0 | 1 | 0.86747 | 1206.585 | 9.9 | 9.9 |  |  |  |  | 28.7883 | 1.3495 | 0.27818 | 2.5824 | 0.11369 | 0.098277 | 0.016674 | 0.46243 | 0.010057 | 0.0086207 | 0.0014135 | 0.051724 | RTE_2025: 0.73248; EFC_2025: 81.3131; UTI_2025: 0.22034
69350 | Matta Power Station | TX | ERCO | NW NA | Matta Power Station LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 10 | 23.2 | 2.32 | 1.5-2.5h | 2023 |  |  | UNATTRIBUTED | 0.97351 | 0.89246 | 0.47571 | 0.018712 |  |  | insufficient_history |  | insufficient_history | 486.6379 | 0.081106 | 0.91889 | 6000 | 0 | 0 | 1 | 0.9044 | 1076.4315 | 10 | 10 | 0.047571 | 0.8932 | 12 | 0.14447 | 72.8998 | 11.9602 | 21.4479 | 20.3445 | 0.031828 | 0.092476 | 0.12129 | 0.404 | 0.0026954 | 0.0080863 | 0.011534 | 0.043127 | RTE_2025: 0.8932; EFC_2025: 194.6552; UTI_2025: 0.68195
69353 | Sunset Ridge Energy Center, LLC | TX | ERCO | East Point Energy, LLC | East Point Energy, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve | 9.9 | 19.8 | 2 | 1.5-2.5h | 2023 |  |  | UNDER_DISPATCH | 0.86283 | 0.76122 | 0.1414 | -0.020792 |  |  | insufficient_history |  | insufficient_history | 322.096 | 0.053683 | 0.94632 | 6000 | 1 | 0 | 1 | 0.9016 | 3309.0582 | 9.9 | 9.9 | 0.013998 | 0.83694 | 12 | 0.65504 | 21.6622 | 3.554 | 6.3733 | 6.0454 | 0.031828 | 0.092476 | 0.12129 | 0.404 | 0.0026954 | 0.0080863 | 0.011534 | 0.043127 | RTE_2025: 0.83694; EFC_2025: 128.8384; UTI_2025: 0.23518
69358 | Calistoga Resilency Center | CA | CISO | Calistoga Resiliency Center, LLC | Calistoga Resiliency Center, LLC |  |  | FALSE |  | LIB | CS |  | 11.3 | 11.9 | 1.0531 | <1.5h | 2025 |  |  | UNDER_DISPATCH | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 | 0 | 0 | 3.7667 | 0 | 2190.79 | 3 | 11.3 |  |  |  |  | 0 | 0 | 0 | 0 | 0.17469 | 0.091536 | 0.0011985 | 0.41022 | 0.016 | 0.008 | 0.0001 | 0.044 | RTE_2025: 0; EFC_2025: 0; UTI_2025: 0
69365 | SMT Dallas BESS | TX | ERCO | SMT Dallas LLC | SMT Dallas LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 10 | 1 | <1.5h | 2025 |  |  | HEALTHY |  | 0.85822 |  |  |  |  | insufficient_history |  | insufficient_history | 59.8 | 0.0099667 | 0.99003 | 6000 | 0 | 0 | 1 | 0.84643 | 0 | 10 | 10 |  |  |  |  | 152.0613 | 7.1279 | 1.4869 | 13.6403 | 0.11369 | 0.098277 | 0.016869 | 0.46243 | 0.010057 | 0.0086207 | 0.0014304 | 0.051724 | RTE_2025: 0.85796; EFC_2025: 59.8; UTI_2025: 1.255
69366 | SME Mission II BESS | TX | ERCO | SMT Mission II LLC | SMT Mission II LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 10 | 1 | <1.5h | 2025 |  |  | UNDER_DISPATCH | 0.88026 | 0.80195 | 0.15743 | -0.0055793 |  |  | insufficient_history |  | insufficient_history | 136.7 | 0.022783 | 0.97722 | 6000 | 3 | 0 | 1 | 0.8 | 520.4165 | 10 | 10 | 0.015743 | 0.80983 | 12 | 0.28151 | 90.0557 | 4.2214 | 0.86891 | 8.0783 | 0.11369 | 0.098277 | 0.016649 | 0.46243 | 0.010057 | 0.0086207 | 0.0014114 | 0.051724 | RTE_2025: 0.80983; EFC_2025: 136.7; UTI_2025: 0.68146
69407 | Dogfish BESS | TX | ERCO | Dogfish ESS Assets, LLC | Dogfish ESS Assets, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 75 | 75 | 1 | <1.5h | 2025 |  |  | UNATTRIBUTED |  | 0.72962 |  |  |  |  | insufficient_history |  | insufficient_history | 202.4267 | 0.033738 | 0.96626 | 6000 | 0 | 0 | 1 | 0.77371 | 2744.5846 | 75 | 75 |  |  |  |  | 1586.3096 | 74.3589 | 15.419 | 142.2965 | 0.11369 | 0.098277 | 0.016771 | 0.46243 | 0.010057 | 0.0086207 | 0.0014219 | 0.051724 | RTE_2025: 0.73057; EFC_2025: 202.4267; UTI_2025: 1.6026
69411 | Snyder BESS | TX | ERCO | Snyder ESS Assets, LLC | Snyder ESS Assets, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 20 | 2 | 1.5-2.5h | 2021 | 188 | B | UNATTRIBUTED | 0.89207 | 0.85255 | 0.21575 | 0.020239 |  |  | insufficient_history |  | insufficient_history | 763.75 | 0.12729 | 0.87271 | 6000 | 0 | 2 | 1 | 0.8613 | 864.6989 | 10 | 10 | 0.021575 | 0.85063 | 12 | 0.03336 | 197.4736 | 21.5989 | 12.2085 | 17.2219 | 0.10203 | 0.19366 | 0.088081 | 0.41615 | 0.0089686 | 0.017937 | 0.0080647 | 0.044843 | RTE_2025: 0.85063; EFC_2025: 176.25; UTI_2025: 0.63508 | PARTIAL_AVAILABILITY
69413 | Sweetwater BESS | TX | ERCO | Sweetwater ESS Assets, LLC | Sweetwater ESS Assets, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 20 | 2 | 1.5-2.5h | 2021 |  |  | UNDER_DISPATCH | 0.92267 | 0.86092 | 0.4044 | 0.0012772 |  |  | insufficient_history |  | insufficient_history | 1041.5167 | 0.17359 | 0.82641 | 6000 | 0 | 0 | 1 | 0.85041 | 498.1859 | 10 | 10 | 0.04044 | 0.86348 | 12 | 0.60067 | 257.374 | 28.1505 | 15.9118 | 22.4459 | 0.10203 | 0.19366 | 0.088081 | 0.41615 | 0.0089686 | 0.017937 | 0.0080647 | 0.044843 | RTE_2025: 0.86348; EFC_2025: 240.35; UTI_2025: 0.90969
69414 | Blevins Solar & Storage | TX | ERCO | Geronimo Power | Geronimo Power |  |  | TRUE | pv_same_plant | LIB | CS | Frequency Regulation | 180 | 360 | 2 | 1.5-2.5h | 2025 |  |  | HYBRID_ARTEFACT |  | 0.74021 |  |  |  |  | insufficient_history |  | insufficient_history | 10.0833 | 0.0016806 | 0.99832 | 6000 | 0 | 0 | 1 | 0.74021 | 0 | 180 | 180 |  |  |  |  | 504.5863 | 110.3791 | 273.2234 | 246.4309 | 0.022471 | 0.086899 | 0.15137 | 0.47079 | 0.0018939 | 0.0075758 | 0.014916 | 0.05303 | RTE_2025: 0.74021; EFC_2025: 10.0833; UTI_2025: 0.36306
69415 | Westover BESS | TX | ERCO | Westover ESS Assets, LLC | Westover ESS Assets, LLC |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 10 | 20 | 2 | 1.5-2.5h | 2021 |  |  | UNATTRIBUTED | 0.91568 | 0.86493 | 0.35524 | 0.0014688 |  |  | insufficient_history |  | insufficient_history | 1117.1333 | 0.18619 | 0.81381 | 6000 | 0 | 0 | 1 | 0.89148 | 267.2828 | 10 | 10 | 0.035524 | 0.86801 | 12 | 0.54787 | 287.6533 | 31.4623 | 17.7837 | 25.0866 | 0.10203 | 0.19366 | 0.088081 | 0.41615 | 0.0089686 | 0.017937 | 0.0080647 | 0.044843 | RTE_2025: 0.86801; EFC_2025: 257.8; UTI_2025: 0.96531
69454 | Crosby Clean Energy Center (BESS) | TX | ERCO | On Energy Storage | On Energy Storage |  |  | FALSE |  | LIB | OT | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 12 | 20.9 | 1.7417 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.92144 |  |  |  |  | insufficient_history |  | insufficient_history | 229.2344 | 0.038206 | 0.96179 | 6000 | 0 | 0 | 1 | 0.92244 | 319.1645 | 10 | 10 |  |  |  |  | 77.9815 | 17.0586 | 37.5579 | 38.0848 | 0.022471 | 0.086899 | 0.13697 | 0.47079 | 0.0018939 | 0.0075758 | 0.013267 | 0.05303 | RTE_2025: 0.92135; EFC_2025: 229.2344; UTI_2025: 1.0451
69456 | Maverick Clean Energy Center (BESS) | TX | ERCO | On Energy Storage | On Energy Storage |  |  | FALSE |  | LIB | OT | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 12 | 20.9 | 1.7417 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.86849 |  |  |  |  | insufficient_history |  | insufficient_history | 155.5502 | 0.025925 | 0.97407 | 6000 | 0 | 0 | 1 | 0.90253 | 311.0798 | 10 | 10 |  |  |  |  | 58.1039 | 12.7103 | 28.3764 | 28.3769 | 0.022471 | 0.086899 | 0.13862 | 0.47079 | 0.0018939 | 0.0075758 | 0.013453 | 0.05303 | RTE_2025: 0.87065; EFC_2025: 155.5502; UTI_2025: 0.85881
69459 | Spencer Clean Energy Center (BESS) | TX | ERCO | On Energy Storage | On Energy Storage |  |  | FALSE |  | LIB | OT | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 12 | 20.9 | 1.7417 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.81719 |  |  |  |  | insufficient_history |  | insufficient_history | 86.2679 | 0.014378 | 0.98562 | 6000 | 0 | 0 | 1 | 0.91011 | 714.8215 | 10 | 10 |  |  |  |  | 51.2927 | 11.2204 | 26.1491 | 25.0504 | 0.022471 | 0.086899 | 0.14381 | 0.47079 | 0.0018939 | 0.0075758 | 0.014044 | 0.05303 | RTE_2025: 0.83899; EFC_2025: 86.2679; UTI_2025: 0.77634
69460 | Winmil Clean Energy Center (BESS) | TX | ERCO | On Energy Storage | On Energy Storage |  |  | FALSE |  | LIB | OT | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 12 | 20.9 | 1.7417 | 1.5-2.5h | 2025 |  |  | UNDER_DISPATCH | 1.0108 | 0.90244 | 0.55896 | 0.013821 |  |  | insufficient_history |  | insufficient_history | 258.2297 | 0.043038 | 0.95696 | 6000 | 0 | 0 | 1 | 0.92212 | 658.4408 | 10 | 10 | 0.067076 | 0.9095 | 12 | 0.73242 | 66.4441 | 14.5348 | 30.7275 | 32.4501 | 0.022471 | 0.086899 | 0.13225 | 0.47079 | 0.0018939 | 0.0075758 | 0.012739 | 0.05303 | RTE_2025: 0.9095; EFC_2025: 258.2297; UTI_2025: 0.94674
69544 | 0 Middle | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS |  | 1.5 | 1.5 | 1 | <1.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.2 | 0.2
69545 | 15 Lincoln | MA | ISNE | Madison Energy Investments LLC | Madison Energy Investments LLC |  |  | TRUE | pv_same_plant,dc_coupled | NIB | CS |  | 0.5 | 0.5 | 1 | <1.5h | 2022 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.2 | 0.2
69568 | NL MA - Division | MA | ISNE | Standard Solar | Standard Solar |  |  | TRUE | pv_same_plant,dc_coupled | LIB | CS | Excess Wind and Solar Generation | 1 | 2.4 | 2.4 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1 | 1
69574 | BESS TX Top Gear - BSHOU002 | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 25.1 | 2.51 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
69575 | BESS TX Panda - BSHOU004 | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Arbitrage | 10 | 10 | 1 | <1.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 10 | 10
69576 | Non-PLD US-El Paso - BSSAT004 | TX | ERCO | Prologis Logistics Services Incorporated BESS | Prologis Logistics Services Incorporated BESS |  |  | FALSE |  | LIB | CS | Frequency Regulation, Ramping / Spinning Reserve, Voltage or Reactive Power Support | 9.9 | 13.7 | 1.3838 | <1.5h | 2025 |  |  | UNDER_DISPATCH |  | 0.81808 |  |  |  |  | insufficient_history |  | insufficient_history | 112.8467 | 0.018808 | 0.98119 | 6000 | 0 | 0 | 3.3 | 0.85552 | 438.2778 | 3 | 9.9 |  |  |  |  | 158.7048 | 7.4393 | 1.5403 | 14.2363 | 0.11369 | 0.098277 | 0.016746 | 0.46243 | 0.010057 | 0.0086207 | 0.0014198 | 0.051724 | RTE_2025: 0.84712; EFC_2025: 112.8467; UTI_2025: 0.92877
69680 | BHER Ravenswood Solar 1 | WV | PJM | BHER Ravenswood Solar 1, LLC | BHER Ravenswood Solar 1, LLC |  |  | TRUE | pv_same_plant | LIB | CS |  | 79 | 300.6 | 3.8051 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 54 | 54
69712 | San Diego Sockers | CA | CISO | Hero Drive Solar Project 2023, LLC | Hero Drive Solar Project 2023, LLC |  |  | TRUE | pv_same_plant | LIB | CS | System Peak Shaving, Excess Wind and Solar Generation | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.5 | 0.5
69727 | Martinsville BESS | VA | PJM | Onsite Partners, LLC | Onsite Partners, LLC |  |  | TRUE | rte_gt_1 | LIB | CS | Frequency Regulation, Load Management | 10.1 | 10.1 | 1 | <1.5h | 2022 |  |  | HYBRID_ARTEFACT |  | 0.27863 |  |  |  |  | insufficient_history |  | insufficient_history | 347.896 | 0.057983 | 0.94202 | 6000 | 0 | 1 | 1 | 0.13671 | 105 | 10.1 | 10.1 |  |  |  |  | 66.5986 | 7.2843 | 4.104 | 0.012546 | 0.10516 | 0.19926 | 0.090404 | 0.0011993 | 0.0092593 | 0.018519 | 0.0082989 | 0.0001 | RTE_2025: 0.16324; EFC_2025: 92.7723; UTI_2025: 0.058151
69803 | 55 Drive BESS | NY | NYIS | 55 Drive BESS, LLC | 55 Drive BESS, LLC |  |  | FALSE |  | LIB | CT | Load Management | 4.6 | 4.6 | 1 | <1.5h | 2025 | 116 | B | FULL_OUTAGE |  | 0.84521 |  |  |  |  | insufficient_history |  | insufficient_history | 230.4348 | 0.038406 | 0.96159 | 6000 | 0 | 3 | 1 | 0.86918 | 465.8103 | 4.6 | 4.6 |  |  |  |  | 127.5543 | 5.9293 | 1.2959 | 4.7834 | 0.15254 | 0.13124 | 0.023863 | 0.29943 | 0.013793 | 0.011724 | 0.0020382 | 0.029655 | RTE_2025: 0.85346; EFC_2025: 230.4348; UTI_2025: 1.1666 | FULL_OUTAGE
70111 | Kern Co Sheriff | CA | CISO | TotalEnergies Renewables USA LLC | TotalEnergies Renewables USA LLC |  |  | TRUE | pv_same_plant | LIB | BL | Backup Power | 0.4 | 1.5 | 3.75 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 0.4 | 0.4
70307 | Milk Street Solar, LLC | MA | ISNE | ClearGen LLC | ClearGen LLC |  |  | TRUE | pv_same_plant | LIB | CS | Arbitrage | 1.2 | 3 | 2.5 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.2 | 1.2
70384 | Yorktown NY 1, LLC | NY | NYIS | Valta Energy | Valta Energy |  |  | TRUE | pv_same_plant | LIB | CT | Backup Power | 1.5 | 5.9 | 3.9333 | 2.5-4.5h | 2025 |  |  | HEALTHY | [8 empty] | insufficient_history | 0 | 0 | 1 | 6000 |  | 0 | 1 |  |  | 1.5 | 1.5

## leads
rank | plant_id | flag_months | first_flag | last_flag | dominant_reason | mwh_at_stake | longest_run | mwh_at_stake_last24m | plant_name | state | ba | operator | nameplate_mw | e_rated_mwh | duration_h | dur_band | cod_year | chem | enclosure | hybrid | hybrid_reasons | eta_true | P_aux_mw | cum_efc | throughput_used | P_aux_pct_nameplate | warranty_headroom | implausible_e_rated | conviction_tier
1 | 66694 | 3 | 2025-10 | 2025-12 | FULL_OUTAGE | 101856.5 | 3 | 101856.5 | Atrisco Energy Storage | NM | PNM | Atrisco Energy Storage LLC | 300 | 1200 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | rte_gt_1 | 0.89201 | -4.9028 | 287.5625 | 0.047927 | -1.6343 | 0.95207 | FALSE | C
2 | 65857 | 30 | 2023-07 | 2025-12 | ELEVATED_P_AUX | 81894.0973 | 30 | 50325.3045 | Sunlight Storage | CA | CISO | Sunlight Storage, LLC | 230 | 920 | 4 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.93992 | 3.3807 | 652.2359 | 0.10871 | 1.4699 | 0.89129 | FALSE | A
3 | 260 | 31 | 2021-10 | 2025-12 | LOW_ETA_AND_LOW_UTI | 46934 | 12 | 26373.5 | Dynegy Moss Landing Power Plant Hybrid | CA | CISO | Dynegy -Moss Landing LLC | 750 | 3000 | 4 | 2.5-4.5h | 2021.9333 | LIB | BL | TRUE | rte_gt_1 | 0.79721 | -1.1221 | 849.7955 | 0.14163 | -0.14961 | 0.85837 | FALSE | C
4 | 63834 | 4 | 2023-05 | 2025-12 | PARTIAL_AVAILABILITY | 30385 | 2 | 25184 | Gateway Energy Storage System | CA | CISO | Gateway Energy Storage, LLC | 250 | 1000 | 4 | 2.5-4.5h | 2020 | LIB | BL | FALSE |  | 0.86801 | 0.40044 | 1994.9877 | 0.3325 | 0.16018 | 0.6675 | FALSE | B
5 | 66575 | 21 | 2024-04 | 2025-12 | ELEVATED_P_AUX | 20096.6592 | 21 | 20096.6592 | Sunlight Storage II | CA | CISO | Sunlight Storage II | 230 | 920 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.99278 | 6.3765 | 559.7185 | 0.093286 | 2.7724 | 0.90671 | FALSE | A
6 | 65980 | 17 | 2023-06 | 2025-09 | THERMAL_AUX | 19149.0803 | 4 | 16558.7202 | CED West Side Canal Battery Storage | CA | CISO | RWE Clean Energy | 131 | 524 | 4 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.84016 | 0.60833 | 632.2615 | 0.10538 | 0.46437 | 0.89462 | FALSE | A
7 | 65744 | 3 | 2024-12 | 2025-02 | PARTIAL_AVAILABILITY | 13366 | 3 | 13366 | Arica Solar | CA | CISO | Arica Solar, LLC | 136 | 544 | 4 | 2.5-4.5h | 2024 | LIB | CT | TRUE | pv_same_plant | 0.82595 | -0.3466 | 500.8989 | 0.083483 | -0.25485 | 0.91652 | FALSE | C
8 | 58462 | 4 | 2024-07 | 2024-11 | PARTIAL_AVAILABILITY | 12543.5 | 2 | 12543.5 | McCoy Solar Energy Project Hybrid | CA | CISO | McCoy Solar, LLC | 230 | 920 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.92817 | 0.6154 | 1076.6065 | 0.17943 | 0.26756 | 0.82057 | FALSE | C
9 | 65491 | 13 | 2024-12 | 2025-12 | ELEVATED_P_AUX | 12502.8421 | 13 | 12502.8421 | Paleo | TX | ERCO | Engie North America | 200 | 200 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.98965 | 2.0723 | 532.765 | 0.088794 | 1.0362 | 0.91121 | FALSE | A
10 | 64852 | 4 | 2024-04 | 2025-12 | PARTIAL_AVAILABILITY | 12343.5 | 2 | 12343.5 | Daggett 3 | CA | CISO | Daggett Solar Power 3 LLC | 149 | 4.6 | 0.030872 | <1.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.91085 | -0.20654 | 77804.3478 | 12.9674 | -0.13862 | 0 | TRUE | C
11 | 65672 | 3 | 2024-12 | 2025-02 | PARTIAL_AVAILABILITY | 10710 | 3 | 10710 | Sanborn BESS 3 | CA | CISO | Terra-Gen Operating Co-BESS | 169 | 676 | 4 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.87625 | 0.16185 | 710.4911 | 0.11842 | 0.095771 | 0.88158 | FALSE | A
12 | 66502 | 36 | 2023-01 | 2025-12 | THERMAL_AUX | 16005.7013 | 36 | 10675.3355 | Valley Center 54 | CA | CISO | Terra-Gen Operating Co-BESS 2 | 54 | 216 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.91079 | 0.71948 | 919.8858 | 0.15331 | 1.3324 | 0.84669 | FALSE | A
13 | 66067 | 4 | 2024-10 | 2025-02 | PARTIAL_AVAILABILITY | 9116 | 2 | 9116 | Kapolei Energy Storage | HI | HECO | Kapolei Energy Storage I, LLC | 185 | 565 | 3.0541 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.93927 | 0.84404 | 667.5274 | 0.11125 | 0.45624 | 0.88875 | FALSE | B
14 | 67860 | 21 | 2024-04 | 2025-12 | ELEVATED_P_AUX | 8814.905 | 21 | 8814.905 | GFTX BESS | TX | ERCO | Giga Texas Energy LLC | 125 | 250 | 2 | 1.5-2.5h | 2024 | OTH | CS | FALSE |  | 0.95164 | 1.3419 | 509.012 | 0.084835 | 1.0735 | 0.91516 | FALSE | A
15 | 63172 | 6 | 2024-04 | 2025-05 | PARTIAL_AVAILABILITY | 8531 | 2 | 8531 | Arroyo Solar Energy Storage Hybrid | NM | PNM | Arroyo Solar LLC | 150 | 600 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.96594 | 1.4481 | 745.405 | 0.12423 | 0.96542 | 0.87577 | FALSE | C
16 | 64312 | 51 | 2021-10 | 2025-12 | THERMAL_AUX | 18031.9146 | 51 | 8487.6559 | Bat Cave | TX | ERCO | Engie North America | 100 | 110 | 1.1 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.85162 | 0.68933 | 1779.8273 | 0.29664 | 0.68933 | 0.70336 | FALSE | A
17 | 61801 | 16 | 2024-09 | 2025-12 | ELEVATED_P_AUX | 7871.3737 | 16 | 7871.3737 | Cascade Energy Storage, LLC | CA | CISO | Engie North America | 25 | 100 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.94958 | 0.4177 | 315.5 | 0.052583 | 1.6708 | 0.94742 | FALSE | A
18 | 60641 | 24 | 2024-01 | 2025-12 | ELEVATED_P_AUX | 7858.1895 | 24 | 7858.1895 | Henrietta D Energy Storage LLC | CA | CISO | Convergent Energy and Power LP | 10 | 40 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.88452 | 0.10351 | 636.6208 | 0.1061 | 1.0351 | 0.8939 | FALSE | A
19 | 63737 | 8 | 2021-10 | 2025-12 | THERMAL_AUX | 7476.1117 | 3 | 7279.6867 | Chisholm Grid Energy Storage System | TX | ERCO | Chisholm Grid, LLC | 100 | 125 | 1.25 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.9422 | 0.2945 | 2070.704 | 0.34512 | 0.2945 | 0.65488 | FALSE | A
20 | 66050 | 4 | 2024-10 | 2025-12 | PARTIAL_AVAILABILITY | 7064 | 2 | 7064 | Lancaster Area Battery | CA | CISO | AES Distributed Energy | 127 | 508 | 4 | 2.5-4.5h | 2022 | LIB | CT | FALSE |  | 0.91274 | 0.85584 | 969.8839 | 0.16165 | 0.67389 | 0.83835 | FALSE | B
21 | 66500 | 36 | 2023-01 | 2025-12 | THERMAL_AUX | 8222.438 | 36 | 6894.3189 | Valley Center 85 | CA | CISO | Terra-Gen Operating Co-BESS 2 | 85 | 212 | 2.4941 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.80616 | 0.22091 | 1169.73 | 0.19495 | 0.2599 | 0.80505 | FALSE | A
22 | 65489 | 2 | 2025-01 | 2025-02 | FULL_OUTAGE | 6616.1616 | 2 | 6616.1616 | Dickens | TX | ERCO | Engie North America | 200 | 200 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.9098 | -0.26798 | 600.24 | 0.10004 | -0.13399 | 0.89996 | FALSE | B
23 | 65490 | 2 | 2025-01 | 2025-02 | FULL_OUTAGE | 6616.1616 | 2 | 6616.1616 | Hydra | TX | ERCO | Engie North America | 200 | 200 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.93013 | 0.73225 | 923.46 | 0.15391 | 0.36612 | 0.84609 | FALSE | B
24 | 65673 | 26 | 2023-11 | 2025-12 | ELEVATED_P_AUX | 6319.5133 | 26 | 6319.5133 | Sanborn BESS 4 | CA | CISO | Terra-Gen Operating Co-BESS | 47 | 188 | 4 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.95292 | 0.6339 | 675.0319 | 0.11251 | 1.3487 | 0.88749 | FALSE | A
25 | 63849 | 23 | 2024-02 | 2025-12 | ELEVATED_P_AUX | 6090.5 | 23 | 6090.5 | Chestnut | CA | CISO | Chestnut Westside LLC | 135 | 540 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.95066 | 1.6301 | 743.7838 | 0.12396 | 1.2075 | 0.87604 | FALSE | C
26 | 64317 | 51 | 2021-10 | 2025-12 | THERMAL_AUX | 11067.9758 | 51 | 5846.2358 | North Fork TX | TX | ERCO | Engie North America | 100 | 110 | 1.1 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.80552 | 0.40881 | 1796.1273 | 0.29935 | 0.40881 | 0.70065 | FALSE | A
27 | 65933 | 21 | 2023-05 | 2025-09 | THERMAL_AUX | 8629.9172 | 8 | 5834.6001 | Sagebrush ESS | CA | CISO | Terra-Gen Operating Co-BESS 2 | 80 | 320 | 4 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.8332 | 0.37173 | 557.2719 | 0.092879 | 0.46467 | 0.90712 | FALSE | A
28 | 62562 | 23 | 2023-06 | 2025-12 | FULL_OUTAGE | 6403.1536 | 19 | 5803.4645 | High Lonesome Wind Power, LLC Hybrid | TX | ERCO | High Lonesome Wind Power, LLC | 63.3 | 81 | 1.2796 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.86398 | 0.25519 | 223.2222 | 0.037204 | 0.40314 | 0.9628 | FALSE | A
29 | 66616 | 10 | 2023-07 | 2025-08 | THERMAL_AUX | 7860.629 | 4 | 5497.3026 | Wolf Tank Storage | TX | ERCO | Wolf Tank Storage LLC | 150 | 150 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.92115 | 1.3787 | 742.12 | 0.12369 | 0.91911 | 0.87631 | FALSE | A
30 | 67721 | 14 | 2024-11 | 2025-12 | ELEVATED_P_AUX | 5433.3289 | 14 | 5433.3289 | Al Pastor Battery Storage Plant | TX | ERCO | Al Pastor BESS LLC | 100.3 | 145 | 1.4457 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.90948 | 1.015 | 349.4621 | 0.058244 | 1.0119 | 0.94176 | FALSE | A
31 | 64164 | 12 | 2025-01 | 2025-12 | ELEVATED_P_AUX | 5173.0428 | 12 | 5173.0428 | Azure Sky Wind Project, LLC Hybrid | TX | ERCO | Azure Sky Wind Project, LLC | 120 | 190 | 1.5833 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.9122 | 1.3114 | 304.7053 | 0.050784 | 1.0928 | 0.94922 | FALSE | A
32 | 63685 | 2 | 2024-03 | 2024-04 | PARTIAL_AVAILABILITY | 5083 | 2 | 5083 | Luna Storage | CA | CISO | AES Distributed Energy | 100 | 400 | 4 | 2.5-4.5h | 2022 | LIB | CT | FALSE |  | 0.88704 | 0.54806 | 1072.15 | 0.17869 | 0.54806 | 0.82131 | FALSE | B
33 | 64713 | 50 | 2021-11 | 2025-12 | ELEVATED_P_AUX | 8546.1795 | 50 | 5079.9942 | Sanborn BESS 2 | CA | CISO | Terra-Gen Operating Co-BESS | 100 | 400 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.9207 | 1.2883 | 1397.955 | 0.23299 | 1.2883 | 0.76701 | FALSE | A
34 | 62734 | 36 | 2023-01 | 2025-12 | ELEVATED_P_AUX | 5206.6208 | 36 | 5026.3077 | Montauk Energy Storage Center | NY | NYIS | Montauk Energy Storage Center, LLC | 5 | 40 | 8 | >4.5h | 2019 | LIB | BL | FALSE |  | 0.9171 | 0.060909 | 698.95 | 0.11649 | 1.2182 | 0.88351 | FALSE | A
35 | 66408 | 2 | 2025-09 | 2025-10 | PARTIAL_AVAILABILITY | 4772 | 2 | 4772 | Buena Vista Energy Center | NM | EPE | Buena Vista Energy Center, LLC | 50 | 200 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.89416 | -0.0025049 | 439.2625 | 0.07321 | -0.0050099 | 0.92679 | FALSE | C
36 | 66338 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 4373 | 2 | 4373 | Callisto I Energy Center | TX | ERCO | Callisto I Energy Center | 223.4 | 200 | 0.89526 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.84971 | -0.11922 | 815.275 | 0.13588 | -0.053365 | 0.86412 | FALSE | B
37 | 66627 | 2 | 2024-08 | 2024-09 | PARTIAL_AVAILABILITY | 4253 | 2 | 4253 | Sonoran Solar Energy | AZ | SRP | Sonoran Solar Energy, LLC | 260 | 1040 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.8886 | 0.21388 | 810.5596 | 0.13509 | 0.08226 | 0.86491 | FALSE | C
38 | 63727 | 13 | 2022-04 | 2025-09 | FULL_OUTAGE | 19185.3144 | 9 | 4250 | Slate Hybrid | CA | CISO | MN8 Energy LLC | 140.3 | 561 | 3.9986 | 2.5-4.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.87239 | 0.47226 | 826.5045 | 0.13775 | 0.33661 | 0.86225 | FALSE | C
39 | 62561 | 21 | 2024-04 | 2025-12 | FULL_OUTAGE | 4124.5 | 21 | 4124.5 | Roadrunner, LLC Hybrid | TX | ERCO | Roadrunner Solar, LLC | 63.3 | 108.6 | 1.7156 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant |  |  | 94.6685 | 0.015778 |  | 0.98422 | FALSE | C
40 | 57242 | 9 | 2023-12 | 2025-12 | PARTIAL_AVAILABILITY | 4231.5 | 5 | 4006.5 | Mililani South Solar Farm | HI |  | Mililani I Solar LLC | 39 | 156 | 4 | 2.5-4.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.92127 | 0.067978 | 621.8462 | 0.10364 | 0.1743 | 0.89636 | FALSE | C
41 | 61365 | 2 | 2025-09 | 2025-10 | LOW_ETA_AND_LOW_UTI | 3914.4015 | 2 | 3914.4015 | Fallbrook Energy Storage | CA | CISO | San Diego Gas & Electric Co | 40 | 40 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.83293 | 0.20466 | 2347.275 | 0.39121 | 0.51164 | 0.60879 | FALSE | B
42 | 66333 | 18 | 2024-07 | 2025-12 | ELEVATED_P_AUX | 3869.7378 | 18 | 3869.7378 | Superstition Energy Storage | AZ | SRP | Superstition Energy Storage, LLC | 90 | 360 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.94841 | 1.0705 | 470.1278 | 0.078355 | 1.1895 | 0.92165 | FALSE | A
43 | 67579 | 2 | 2025-09 | 2025-10 | PARTIAL_AVAILABILITY | 3680 | 2 | 3680 | AES ES Alamitos 2 LLC | CA | CISO | AES Clean Energy | 82 | 328 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.88869 | 0.058032 | 260.3628 | 0.043394 | 0.07077 | 0.95661 | FALSE | B
44 | 66574 | 15 | 2024-10 | 2025-12 | ELEVATED_P_AUX | 3497 | 15 | 3497 | San Juan Solar I | NM | PNM | San Juan Solar I, LLC | 100 | 561.4 | 5.614 | >4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.97164 | 1.7547 | 253.6106 | 0.042268 | 1.7547 | 0.95773 | FALSE | C
45 | 67236 | 10 | 2024-06 | 2025-09 | THERMAL_AUX | 3099.2393 | 4 | 3099.2393 | Anemoi Energy Storage | TX | ERCO | Anemoi Energy Storage, LLC | 200 | 400 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.83064 | 0.79594 | 398.85 | 0.066475 | 0.39797 | 0.93352 | FALSE | A
46 | 65700 | 30 | 2023-07 | 2025-12 | THERMAL_AUX | 3476.1446 | 30 | 3097.7716 | TX21 River Valley Storage 2 | TX | ERCO | Key Capture Energy | 50 | 107 | 2.14 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.83567 | 0.18845 | 475.3645 | 0.079227 | 0.3769 | 0.92077 | FALSE | A
47 | 63458 | 4 | 2025-01 | 2025-04 | FULL_OUTAGE | 2868 | 4 | 2868 | Rush Springs Energy Storage (BA) | OK | SWPP | Rush Springs Energy Storage | 10 | 20 | 2 | 1.5-2.5h | 2020 | FLB | CS | FALSE |  | 0.90277 | 0.050926 | 1086.25 | 0.18104 | 0.50926 | 0.81896 | FALSE | A
48 | 61098 | 4 | 2023-12 | 2025-09 | PARTIAL_AVAILABILITY | 3277.5 | 2 | 2817.5 | Battle Mountain Solar Project | NV | NEVP | RWE Clean Energy | 25 | 25 | 1 | <1.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.92801 | -0.0040173 | 4850.76 | 0.80846 | -0.016069 | 0.19154 | FALSE | C
49 | 57447 | 78 | 2019-01 | 2025-06 | LOW_ETA_AND_LOW_UTI | 11268.0965 | 78 | 2618.1331 | Laurel Mountain Hybrid | WV | PJM | AES Distributed Energy | 16 | 16 | 1 | <1.5h | 2011 | LIB | CS | FALSE |  | 0.80524 | 0.21454 | 10103.2344 | 1.6839 | 1.3409 | 0 | FALSE | A
50 | 64528 | 55 | 2021-06 | 2025-12 | THERMAL_AUX | 5718.7137 | 55 | 2552.9134 | Gambit Energy Storage - Angleton Storage | TX | ERCO | Gambit Energy Storage LLC | 100 | 200 | 2 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.7849 | 0.34527 | 962.635 | 0.16044 | 0.34527 | 0.83956 | FALSE | A
51 | 2324 | 8 | 2024-06 | 2025-09 | THERMAL_AUX | 2522.5632 | 4 | 2522.5632 | Reid Gardner | NV | NEVP | Nevada Power Co | 220 | 220 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.81626 | -0.83654 | 1453.9901 | 0.24233 | -0.38025 | 0.75767 | FALSE | A
52 | 63943 | 45 | 2022-04 | 2025-12 | ELEVATED_P_AUX | 5206.002 | 45 | 2506.6578 | Coso Battery Storage | CA | CISO | Arevon Asset Management | 60 | 240 | 4 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.946 | 0.93635 | 1262.5542 | 0.21043 | 1.5606 | 0.78957 | FALSE | A
53 | 64878 | 4 | 2023-11 | 2025-12 | PARTIAL_AVAILABILITY | 4861.5 | 2 | 2478.5 | Edwards Sanborn E1A | CA | CISO | Terra-Gen Operating Co-Hybrid | 144 | 272 | 1.8889 | 1.5-2.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.81487 | -0.20823 | 992.7684 | 0.16546 | -0.14461 | 0.83454 | FALSE | C
54 | 64760 | 36 | 2023-01 | 2025-12 | ELEVATED_P_AUX | 3999.0489 | 36 | 2257.0712 | Ocean State BTM | RI | ISNE | Agilitas Energy, Inc. | 3 | 10 | 3.3333 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.92292 | 0.030392 | 1441.8 | 0.2403 | 1.0131 | 0.7597 | FALSE | A
55 | 64712 | 50 | 2021-11 | 2025-12 | ELEVATED_P_AUX | 2243.8001 | 50 | 2243.8001 | Sanborn BESS 1 | CA | CISO | Terra-Gen Operating Co-BESS | 100 | 200 | 2 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.93574 | 1.2689 | 1583.645 | 0.26394 | 1.2689 | 0.73606 | FALSE | A
56 | 64423 | 9 | 2024-10 | 2025-09 | FULL_OUTAGE | 2231.2653 | 5 | 2231.2653 | TX7 Flat Top | TX | ERCO | Key Capture Energy | 9.9 | 16.5 | 1.6667 | 1.5-2.5h | 2020 | LIB | CS | FALSE |  | 0.85489 | -0.00038398 | 1334.202 | 0.22237 | -0.0038786 | 0.77763 | FALSE | A
57 | 65457 | 6 | 2025-02 | 2025-09 | THERMAL_AUX | 2228.9662 | 4 | 2228.9662 | Cathode (Hinson) BESS | CA | CISO | Southern California Edison Co | 200 | 800 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.84594 | 0.63173 | 229.0888 | 0.038181 | 0.31586 | 0.96182 | FALSE | A
58 | 64197 | 28 | 2023-09 | 2025-12 | ELEVATED_P_AUX | 2203 | 28 | 2203 | Fifth Standard Solar PV, LLC (Hybrid) | CA | CISO | RWE Clean Energy | 137 | 137 | 1 | <1.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.93238 | 1.5425 | 2488.9927 | 0.41483 | 1.1259 | 0.58517 | FALSE | C
59 | 63721 | 6 | 2024-04 | 2025-03 | PARTIAL_AVAILABILITY | 2177.5 | 2 | 2177.5 | Cool Springs Solar (Hybrid) | GA | SOCO | Cool Springs Solar, LLC | 40 | 80 | 2 | 1.5-2.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 1.0376 | 0.23648 | 1377.7875 | 0.22963 | 0.5912 | 0.77037 | FALSE | C
60 | 63735 | 2 | 2025-11 | 2025-12 | FULL_OUTAGE | 2172.5 | 2 | 2172.5 | Silverstrand Grid Energy Storage System | CA | CISO | Silverstrand Grid, LLC | 11 | 44 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.85423 | -0.016932 | 1310.9091 | 0.21848 | -0.15393 | 0.78152 | FALSE | B
61 | 65472 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 2129.6654 | 24 | 2129.6654 | Chukar Battery Energy Storage System | NV | NEVP | Nevada Power Co | 10 | 40 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.93037 | 0.15973 | 1329.5625 | 0.22159 | 1.5973 | 0.77841 | FALSE | A
62 | 62175 | 9 | 2022-06 | 2024-09 | THERMAL_AUX | 15102.8879 | 4 | 2056.8652 | Diablo Energy Storage | CA | CISO | Diablo Energy Storage, LLC | 200 | 800 | 4 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.86028 | 0.44396 | 891.1838 | 0.14853 | 0.22198 | 0.85147 | FALSE | A
63 | 67489 | 3 | 2025-04 | 2025-06 | PARTIAL_AVAILABILITY | 1925 | 3 | 1925 | Cavalry Solar Hybrid | IN | MISO | Cavalry Energy Center LLC | 45 | 180 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.89248 | -0.052344 | 691.1944 | 0.1152 | -0.11632 | 0.8848 | FALSE | C
64 | 66279 | 2 | 2025-11 | 2025-12 | FULL_OUTAGE | 1925 | 2 | 1925 | Boulevard Energy Storage | CA | CISO | San Diego Gas & Electric Co | 10 | 10 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.93662 | 0.088994 | 1215.3 | 0.20255 | 0.88994 | 0.79745 | FALSE | B
65 | 67175 | 10 | 2024-04 | 2025-09 | THERMAL_AUX | 1875.9101 | 6 | 1875.9101 | Rodeo Ranch Energy Storage | TX | ERCO | Rodeo Ranch Energy Storage, LLC | 300 | 600 | 2 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.83772 | 0.55946 | 527.1586 | 0.08786 | 0.18649 | 0.91214 | FALSE | A
66 | 66325 | 4 | 2025-06 | 2025-09 | THERMAL_AUX | 1829.0899 | 4 | 1829.0899 | Hemmingway BESS | ID | IPCO | Idaho Power Co | 116 | 464 | 4 | 2.5-4.5h | 2025 | FLB | CS | FALSE |  | 0.95398 | 0.53138 | 100.8901 | 0.016815 | 0.45809 | 0.98318 | FALSE | A
67 | 65699 | 30 | 2023-07 | 2025-12 | THERMAL_AUX | 2218.3354 | 30 | 1772.2439 | TX19 River Valley Storage 1 | TX | ERCO | Key Capture Energy | 50 | 111 | 2.22 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.82307 | 0.20379 | 447.1441 | 0.074524 | 0.40757 | 0.92548 | FALSE | A
68 | 389 | 71 | 2019-01 | 2025-11 | LOW_ETA_AND_LOW_UTI | 11426.1263 | 61 | 1754.9228 | El Centro Hybrid | CA | IID | Imperial Irrigation District | 30 | 20 | 0.66667 | <1.5h | 2016 | LIB | BL | FALSE |  | 0.77993 | 0.223 | 1631.1625 | 0.27186 | 0.74332 | 0.72814 | FALSE | A
69 | 66006 | 8 | 2024-06 | 2025-09 | THERMAL_AUX | 1699.3775 | 4 | 1699.3775 | House Mountain | TX | ERCO | House Mountain | 73.2 | 120 | 1.6393 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.79801 | -0.64542 | 612.05 | 0.10201 | -0.88172 | 0.89799 | FALSE | A
70 | 67855 | 3 | 2024-10 | 2024-12 | ELEVATED_P_AUX | 1679.9977 | 3 | 1679.9977 | Westwing | AZ | AZPS | AES Clean Energy | 200 | 808.4 | 4.042 | 2.5-4.5h | 2024.59 | LIB | CS | FALSE |  | 0.94033 | 1.3779 | 268.8466 | 0.044808 | 0.68894 | 0.95519 | FALSE | A
71 | 66617 | 2 | 2025-03 | 2025-04 | PARTIAL_AVAILABILITY | 1630 | 2 | 1630 | Cald BESS | CA | CISO | Cald BESS LLC | 100 | 400 | 4 | 2.5-4.5h | 2024 | LIB | CT | FALSE |  | 0.92358 | 0.84213 | 458.2975 | 0.076383 | 0.84213 | 0.92362 | FALSE | B
72 | 64612 | 8 | 2025-04 | 2025-12 | FULL_OUTAGE | 1628 | 4 | 1628 | Kearny North Energy Storage | CA | CISO | San Diego Gas & Electric Co | 10 | 40 | 4 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.86576 | 0.052993 | 527.6875 | 0.087948 | 0.52993 | 0.91205 | FALSE | A
73 | 8063 | 5 | 2024-12 | 2025-08 | PARTIAL_AVAILABILITY | 1617.5 | 3 | 1617.5 | DeCordova Steam Electric Station | TX | ERCO | Luminant Generation Company LLC | 269.1 | 263 | 0.97733 | <1.5h | 2022 | LIB | CS | FALSE |  | 2.1061 | 4.1019 | 551.2738 | 0.091879 | 1.5243 | 0.90812 | FALSE | A
74 | 60231 | 26 | 2023-08 | 2025-12 | LOW_ETA_AND_LOW_UTI | 1712 | 24 | 1530 | Genentech-Oceanside Hybrid | CA | CISO | Tesla Inc. | 2 | 2 | 1 | <1.5h | 2016 | LIB | CS | TRUE | pv_same_plant | 0.80088 | 0.0028783 | 4822.5 | 0.80375 | 0.14391 | 0.19625 | FALSE | C
75 | 66773 | 2 | 2024-10 | 2024-11 | PARTIAL_AVAILABILITY | 1494 | 2 | 1494 | Raceway Solar & Storage | CA | CISO | AES Clean Energy | 80 | 320 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.89259 | -0.058378 | 437.8406 | 0.072973 | -0.072973 | 0.92703 | FALSE | C
76 | 67237 | 8 | 2024-06 | 2025-09 | THERMAL_AUX | 1493.55 | 4 | 1493.55 | Ebony Energy Storage | TX | ERCO | Ebony Energy Storage, LLC | 207.9 | 400 | 1.924 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.7669 | -0.68163 | 449.145 | 0.074857 | -0.32787 | 0.92514 | FALSE | A
77 | 66461 | 2 | 2025-08 | 2025-09 | PARTIAL_AVAILABILITY | 1471 | 2 | 1471 | Beaumont BESS | CA | CISO | Terra-Gen Operating Co-BESS 2 | 116.6 | 400 | 3.4305 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.94544 | 1.0173 | 412.82 | 0.068803 | 0.87244 | 0.9312 | FALSE | B
78 | 56984 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 2056.8873 | 36 | 1452.2313 | Inadale Wind Farm LLC Hybrid | TX | ERCO | RWE Clean Energy | 9.9 | 9.9 | 1 | <1.5h | 2018 | LIB | CS | FALSE |  | 0.77548 | 0.070319 | 2006.0606 | 0.33434 | 0.71029 | 0.66566 | FALSE | A
79 | 62444 | 2 | 2025-08 | 2025-09 | PARTIAL_AVAILABILITY | 1232.5 | 2 | 1232.5 | Meyersdale Battery | PA | PJM | GlidePath Power Operations LLC | 18 | 12.1 | 0.67222 | <1.5h | 2015 | LIB | CT | TRUE | rte_gt_1 | 0.86145 | 0.050541 | 20044.9656 | 3.3408 | 0.28079 | 0 | FALSE | C
80 | 63900 | 2 | 2025-10 | 2025-11 | PARTIAL_AVAILABILITY | 1206 | 2 | 1206 | AES Waikoloa Solar Hybrid | HI | HECO | AES Distributed Energy | 30 | 120 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 1.2168 | 0.84342 | 591.0917 | 0.098515 | 2.8114 | 0.90148 | FALSE | C
81 | 67303 | 19 | 2024-06 | 2025-12 | ELEVATED_P_AUX | 1200.106 | 19 | 1200.106 | Mead Battery Storage | CO | WACM | Mead Energy Storage LLC | 7.8 | 31.3 | 4.0128 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.95589 | 0.084987 | 392.5559 | 0.065426 | 1.0896 | 0.93457 | FALSE | A
82 | 61204 | 8 | 2021-06 | 2025-09 | PARTIAL_AVAILABILITY | 16131.9581 | 3 | 1157.6312 | AES ES Alamitos, LLC | CA | CISO | AES ES Alamitos, LLC | 100 | 400 | 4 | 2.5-4.5h | 2021 | LIB | BL | FALSE |  | 0.94552 | 0.99627 | 1338.95 | 0.22316 | 0.99627 | 0.77684 | FALSE | A
83 | 66716 | 2 | 2025-06 | 2025-07 | THERMAL_AUX | 1145.8634 | 2 | 1145.8634 | Saint Energy Storage II LLC | AZ | SRP | Saint Energy Storage II LLC | 100 | 400 | 4 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.91542 | 0.98823 | 479.7425 | 0.079957 | 0.98823 | 0.92004 | FALSE | B
84 | 64256 | 2 | 2025-04 | 2025-05 | PARTIAL_AVAILABILITY | 1129 | 2 | 1129 | AES Maui Kuihelani Solar Hybrid | HI | HECO | AES Distributed Energy | 60 | 240 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 1.0479 | 0.56966 | 411.4083 | 0.068568 | 0.94944 | 0.93143 | FALSE | C
85 | 60094 | 2 | 2025-04 | 2025-05 | PARTIAL_AVAILABILITY | 1104 | 2 | 1104 | Blythe Solar III, LLC Hybrid | CA | CISO | Blythe Solar III, LLC | 115 | 538.6 | 4.6835 | >4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.9293 | 0.71105 | 835.6387 | 0.13927 | 0.61831 | 0.86073 | FALSE | C
86 | 67083 | 7 | 2024-09 | 2025-03 | LOW_ETA_AND_LOW_UTI | 1094.3987 | 7 | 1094.3987 | Longbow BESS, LLC | TX | ERCO | Longbow BESS, LLC | 174 | 407.4 | 2.3414 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.85775 | 0.45886 | 238.3235 | 0.039721 | 0.26371 | 0.96028 | FALSE | A
87 | 60570 | 10 | 2022-12 | 2025-03 | FULL_OUTAGE | 3525 | 6 | 1045.5 | Escondido Energy Storage | CA | CISO | San Diego Gas & Electric Co | 30 | 120 | 4 | 2.5-4.5h | 2017 | LIB | CS | FALSE |  | 0.90928 | 0.10812 | 1904.7097 | 0.31745 | 0.36039 | 0.68255 | FALSE | A
88 | 66008 | 4 | 2023-11 | 2025-09 | PARTIAL_AVAILABILITY | 1393 | 2 | 1016 | Swoose II | TX | ERCO | Swoose II | 101 | 200 | 1.9802 | 1.5-2.5h | 2022 | LIB | CS | FALSE |  | 0.9039 | 0.41214 | 908.9833 | 0.1515 | 0.40806 | 0.8485 | FALSE | B
89 | 63891 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 1006.5 | 2 | 1006.5 | Saticoy | CA | CISO | Ventura Energy Storage, LLC | 100 | 400 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | rte_gt_1 | 0.89344 | 0.45391 | 1348.8675 | 0.22481 | 0.45391 | 0.77519 | FALSE | C
90 | 64928 | 6 | 2023-10 | 2025-12 | PARTIAL_AVAILABILITY | 1582 | 4 | 986 | Edwards Sanborn S3 | CA | CISO | Terra-Gen Operating Co-Hybrid | 33 | 70 | 2.1212 | 1.5-2.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 1.1125 | 0.77312 | 1059.8143 | 0.17664 | 2.3428 | 0.82336 | FALSE | C
91 | 63913 | 6 | 2022-08 | 2025-05 | PARTIAL_AVAILABILITY | 3274 | 2 | 974 | Dodge Flat | NV | NEVP | Dodge Flat Solar, LLC | 50 | 200 | 4 | 2.5-4.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.9346 | 0.16344 | 1065.06 | 0.17751 | 0.32688 | 0.82249 | FALSE | C
92 | 64743 | 36 | 2023-01 | 2025-12 | THERMAL_AUX | 1490.0099 | 36 | 964.5475 | Tierra Buena Energy Storage | CA | CISO | VESI 10 LLC | 5 | 5 | 1 | <1.5h | 2022 | LIB | CS | FALSE |  | 0.93867 | 0.070261 | 3386.8 | 0.56447 | 1.4052 | 0.43553 | FALSE | A
93 | 67091 | 2 | 2025-08 | 2025-09 | PARTIAL_AVAILABILITY | 945 | 2 | 945 | Yellow Pine II | NV | NEVP | Yellow Pine Solar II, LLC | 85 | 340 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.89506 | 0.14709 | 537.3118 | 0.089552 | 0.17304 | 0.91045 | FALSE | C
94 | 61552 | 15 | 2024-03 | 2025-06 | LOW_ETA_AND_LOW_UTI | 896 | 13 | 896 | Fort Detrick Solar PV | MD | PJM | Montevue Lane Solar, LLC | 6 | 6 | 1 | <1.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.85035 | 0.00078915 | 1471.1667 | 0.24519 | 0.013153 | 0.75481 | FALSE | C
95 | 62908 | 61 | 2019-06 | 2025-12 | LOW_ETA_AND_LOW_UTI | 2098.4235 | 50 | 893.3635 | Anoka BESS | MN | MISO | Gopher Energy Storage, LLC | 6 | 12 | 2 | 1.5-2.5h | 2018 | LIB | CS | FALSE |  | 0.53603 | 0.010459 | 140.6458 | 0.023441 | 0.17431 | 0.97656 | FALSE | A
96 | 64545 | 2 | 2025-09 | 2025-10 | PARTIAL_AVAILABILITY | 799 | 2 | 799 | Ranchland Wind Storage | TX | ERCO | Ranchland Wind Storage, LLC | 73 | 108.6 | 1.4877 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.97981 | 0.69123 | 325.7366 | 0.054289 | 0.9469 | 0.94571 | FALSE | B
97 | 67304 | 16 | 2024-09 | 2025-12 | ELEVATED_P_AUX | 782.2709 | 16 | 782.2709 | Davis Battery Storage | CO | WACM | Davis UP Energy Storage LLC | 11.8 | 47 | 3.9831 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.98656 | 0.18298 | 363.5957 | 0.060599 | 1.5506 | 0.9394 | FALSE | A
98 | 60546 | 8 | 2023-02 | 2025-12 | PARTIAL_AVAILABILITY | 1352.4885 | 3 | 778 | KIUC Kapaia PV and BA Storage Project Hy | HI |  | Tesla Inc. | 13 | 52 | 4 | 2.5-4.5h | 2017 | LIB | CS | TRUE | pv_same_plant | 0.90671 | 0.041256 | 1379.6923 | 0.22995 | 0.31736 | 0.77005 | FALSE | C
99 | 66285 | 18 | 2024-07 | 2025-12 | ELEVATED_P_AUX | 713.866 | 18 | 713.866 | Condor Energy Storage LLC | CA | CISO | Condor Energy Storage LLC | 200 | 800 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.97814 | 2.7563 | 457.155 | 0.076192 | 1.3781 | 0.92381 | FALSE | A
100 | 68683 | 2 | 2025-08 | 2025-09 | FULL_OUTAGE | 711 | 2 | 711 | Crockett BESS | TX | ERCO | Prologis Logistics Services Incorporated BESS | 10 | 24.8 | 2.48 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  |  |  | 133.75 | 0.022292 |  | 0.97771 | FALSE | B
101 | 65271 | 2 | 2024-11 | 2024-12 | PARTIAL_AVAILABILITY | 681 | 2 | 681 | Noble Solar | TX | ERCO | Geronimo Power | 125 | 125 | 1 | <1.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.88097 | 0.18293 | 258.648 | 0.043108 | 0.14635 | 0.95689 | FALSE | C
102 | 64929 | 19 | 2023-04 | 2025-12 | LOW_ETA_AND_LOW_UTI | 1091 | 9 | 661.5 | Edwards Sanborn S1 | CA | CISO | Terra-Gen Operating Co-Hybrid | 40 | 83.5 | 2.0875 | 1.5-2.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.83076 | -0.038845 | 829.2695 | 0.13821 | -0.097112 | 0.86179 | FALSE | C
103 | 67019 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 658 | 2 | 658 | Copperhead Solar, LLC | TX | ERCO | Geronimo Power | 100 | 100 | 1 | <1.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 1.1024 | 0.74848 | 311.69 | 0.051948 | 0.74848 | 0.94805 | FALSE | C
104 | 66330 | 2 | 2025-10 | 2025-11 | FULL_OUTAGE | 641.5 | 2 | 641.5 | Weiser BESS | ID | IPCO | Idaho Power Co | 3 | 12 | 4 | 2.5-4.5h | 2025 | FLB | CS | FALSE |  | 0.89154 | -0.0091887 | 220.1667 | 0.036694 | -0.30629 | 0.96331 | FALSE | B
105 | 60297 | 36 | 2023-01 | 2025-12 | THERMAL_AUX | 806.6772 | 36 | 621.8706 | Clinton Battery | OH | PJM | Clinton Battery Utility, LLC | 10 | 4.1 | 0.41 | <1.5h | 2016 | LIB | CS | FALSE |  | 0.82437 | 0.033484 | 10445 | 1.7408 | 0.33484 | 0 | FALSE | A
106 | 60123 | 28 | 2021-10 | 2025-12 | LOW_ETA_AND_LOW_UTI | 786.5 | 17 | 610.5 | Castle Gap Solar Hybrid | TX | ERCO | Upton County Solar 2 LLC | 9.9 | 42 | 4.2424 | 2.5-4.5h | 2019 | LIB | CS | TRUE | pv_same_plant | 0.57006 | -0.068495 | 1010.1429 | 0.16836 | -0.69187 | 0.83164 | FALSE | C
107 | 66949 | 2 | 2025-08 | 2025-09 | PARTIAL_AVAILABILITY | 609 | 2 | 609 | Sagebrush Solar 2 ESS 40 | CA | CISO | Terra-Gen Operating Co-BESS 2 | 40 | 160 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.80962 | -0.081248 | 377.725 | 0.062954 | -0.20312 | 0.93705 | FALSE | B
108 | 66329 | 7 | 2025-06 | 2025-12 | FULL_OUTAGE | 606.5 | 7 | 606.5 | Melba BESS | ID | IPCO | Idaho Power Co | 2 | 8 | 4 | 2.5-4.5h | 2025 | FLB | CS | FALSE |  |  |  | 117.5 | 0.019583 |  | 0.98042 | FALSE | B
109 | 66266 | 2 | 2024-09 | 2024-10 | PARTIAL_AVAILABILITY | 571 | 2 | 571 | Clairemont Energy Storage | CA | CISO | San Diego Gas & Electric Co | 10 | 10 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.90596 | 0.065575 | 1323 | 0.2205 | 0.65575 | 0.7795 | FALSE | B
110 | 63611 | 3 | 2024-01 | 2024-03 | PARTIAL_AVAILABILITY | 534.9235 | 3 | 534.9235 | CSU Long Beach | CA | CISO | Hybrid-Electric Building Technologies West Los Angeles 1, LLC | 2.5 | 15 | 6 | >4.5h | 2017 | LIB | CS | FALSE |  | 0.8125 | -0.0060754 | 925.5889 | 0.15426 | -0.24302 | 0.84574 | FALSE | A
111 | 65247 | 20 | 2024-04 | 2025-12 | LOW_ETA_AND_LOW_UTI | 523.4516 | 11 | 523.4516 | Zion Hill BESS | NC | CPLE | North Carolina El Member Corp | 5 | 10 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.84647 | 0.037825 | 134.6 | 0.022433 | 0.75651 | 0.97757 | FALSE | A
112 | 64295 | 4 | 2024-09 | 2025-02 | PARTIAL_AVAILABILITY | 504.5 | 2 | 504.5 | Angleton | TX | ERCO | Engie North America | 9.9 | 9.9 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.93027 | 0.010999 | 1212.9293 | 0.20215 | 0.1111 | 0.79785 | FALSE | B
113 | 58383 | 24 | 2024-01 | 2025-12 | ELEVATED_P_AUX | 487.5 | 24 | 487.5 | Hyder II Hybrid | AZ | AZPS | Arizona Public Service Co | 14 | 42 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.997 | 0.26853 | 554.5476 | 0.092425 | 1.9181 | 0.90758 | FALSE | C
114 | 62889 | 24 | 2024-01 | 2025-12 | ELEVATED_P_AUX | 477.7154 | 24 | 477.7154 | Hecate Energy Johanna Facility | CA | CISO | Hecate Energy Johanna Facility LLC | 20 | 80 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.95564 | 0.28125 | 1073.5687 | 0.17893 | 1.4063 | 0.82107 | FALSE | A
115 | 62862 | 7 | 2024-01 | 2025-05 | FULL_OUTAGE | 470.1523 | 5 | 470.1523 | Nabb Battery Energy Storage System | IN | MISO | Duke Energy Indiana, LLC | 5 | 5 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.86897 | -0.00093027 | 261.2 | 0.043533 | -0.018605 | 0.95647 | FALSE | A
116 | 69803 | 3 | 2025-10 | 2025-12 | FULL_OUTAGE | 454.5 | 3 | 454.5 | 55 Drive BESS | NY | NYIS | 55 Drive BESS, LLC | 4.6 | 4.6 | 1 | <1.5h | 2025 | LIB | CT | FALSE |  |  |  | 230.4348 | 0.038406 |  | 0.96159 | FALSE | B
117 | 66265 | 2 | 2024-08 | 2024-09 | PARTIAL_AVAILABILITY | 451 | 2 | 451 | Paradise Energy Storage | CA | CISO | San Diego Gas & Electric Co | 10 | 10 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.91835 | 0.088346 | 1702.1 | 0.28368 | 0.88346 | 0.71632 | FALSE | B
118 | 65241 | 18 | 2024-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 449.8121 | 11 | 449.8121 | McKinney BESS | NC | CPLE | North Carolina El Member Corp | 5 | 10 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.75647 | 0.02975 | 120.3 | 0.02005 | 0.595 | 0.97995 | FALSE | A
119 | 1482 | 33 | 2023-04 | 2025-12 | THERMAL_AUX | 614.3405 | 33 | 446.4045 | Bonny Eagle | ME | ISNE | Brookfield White Pine Hydro LLC | 8 | 16 | 2 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.77888 | -0.0057817 | 1193.875 | 0.19898 | -0.072271 | 0.80102 | FALSE | A
120 | 63616 | 3 | 2025-01 | 2025-03 | PARTIAL_AVAILABILITY | 446 | 3 | 446 | OCSD | CA | CISO | Hybrid-Electric Building Technologies West Los Angeles 1, LLC | 4.9 | 32.6 | 6.6531 | >4.5h | 2019 | LIB | CS | FALSE |  | 0.88272 | 0.0012045 | 376.112 | 0.062685 | 0.024582 | 0.93731 | FALSE | A
121 | 141 | 6 | 2023-10 | 2024-05 | PARTIAL_AVAILABILITY | 1543 | 3 | 444.5 | Agua Fria | AZ | SRP | Salt River Project | 25 | 100 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.88371 | 0.1818 | 875.65 | 0.14594 | 0.7272 | 0.85406 | FALSE | C
122 | 62964 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 441 | 2 | 441 | El Sol BESS | AZ | AZPS | Invenergy Services LLC | 50 | 50 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.89498 | 0.10307 | 2450.465 | 0.40841 | 0.20615 | 0.59159 | FALSE | B
123 | 64811 | 6 | 2024-04 | 2024-11 | LOW_ETA_AND_LOW_UTI | 433.0232 | 4 | 433.0232 | Upton County BESS | TX | ERCO | VESI Upton County BESS, LLC | 24.8 | 25 | 1.0081 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.83197 | 0.058708 | 403.62 | 0.06727 | 0.23673 | 0.93273 | FALSE | A
124 | 65249 | 18 | 2024-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 428.1503 | 11 | 428.1503 | Docs Road BESS | NC | CPLE | North Carolina El Member Corp | 5 | 10 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.73752 | 0.023906 | 119.1 | 0.01985 | 0.47812 | 0.98015 | FALSE | A
125 | 67284 | 6 | 2024-03 | 2025-08 | LOW_ETA_AND_LOW_UTI | 427.5 | 2 | 427.5 | Ganado Solar | TX | ERCO | Enel Green Power NA, Inc. | 70.5 | 115 | 1.6312 | 1.5-2.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.83054 | 0.17767 | 473.2261 | 0.078871 | 0.25202 | 0.92113 | FALSE | C
126 | 66946 | 2 | 2025-04 | 2025-05 | PARTIAL_AVAILABILITY | 415.5 | 2 | 415.5 | Lockhart ESS, LLC | CA | CISO | Terra-Gen Operating Co-Solar | 45 | 180 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.90952 | 0.32703 | 534.0056 | 0.089001 | 0.72673 | 0.911 | FALSE | B
127 | 64546 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 415.1626 | 24 | 415.1626 | Wynwood Energy Storage | FL | FPL | Florida Power & Light Co | 10 | 40 | 4 | 2.5-4.5h | 2019 | LIB | BL | FALSE |  | 0.83396 | 0.044218 | 508.5875 | 0.084765 | 0.44218 | 0.91524 | FALSE | A
128 | 65246 | 18 | 2024-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 411.6313 | 11 | 411.6313 | Walkers Crossroads BESS | NC | CPLE | North Carolina El Member Corp | 5 | 10 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.76413 | 0.027513 | 138.8 | 0.023133 | 0.55027 | 0.97687 | FALSE | A
129 | 65240 | 19 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 411.3195 | 12 | 411.3195 | Maysville BESS | NC | CPLE | North Carolina El Member Corp | 5 | 10 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.76641 | 0.02573 | 144.5 | 0.024083 | 0.5146 | 0.97592 | FALSE | A
130 | 59949 | 15 | 2019-11 | 2024-10 | LOW_ETA_AND_LOW_UTI | 590.5148 | 8 | 378.517 | AES Warrior Run Energy Storage Project | MD | PJM | AES Tait LLC | 11 | 5 | 0.45455 | <1.5h | 2015 | LIB | BL | FALSE |  | 0.83581 | 0.042279 | 14649.0167 | 2.4415 | 0.38435 | 0 | FALSE | A
131 | 1507 | 19 | 2020-03 | 2025-12 | LOW_ETA_AND_LOW_UTI | 554.7132 | 6 | 364.2865 | William F Wyman Hybrid | ME | ISNE | FPL Energy Wyman LLC | 16.7 | 10.9 | 0.65269 | <1.5h | 2016 | LIB | CS | FALSE |  | 0.83322 | 0.023179 | 8314.526 | 1.3858 | 0.1388 | 0 | FALSE | A
132 | 66180 | 19 | 2023-11 | 2025-12 | FULL_OUTAGE | 356 | 13 | 356 | Huxley Solar | MA | ISNE | Agilitas Energy, Inc. | 5 | 3.5 | 0.7 | <1.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_tight | 0.78454 | 0.00050802 | 346.5714 | 0.057762 | 0.01016 | 0.94224 | FALSE | C
133 | 61678 | 14 | 2019-11 | 2025-09 | PARTIAL_AVAILABILITY | 1155.5 | 5 | 351.5 | Pinal Central Energy Center Hybrid | AZ | SRP | Pinal Central Energy Center, LLC | 10 | 40 | 4 | 2.5-4.5h | 2018 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 1.0232 | 0.26109 | 2629.6375 | 0.43827 | 2.6109 | 0.56173 | FALSE | C
134 | 59118 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 346.5 | 24 | 346.5 | Cameron Wind 1 LLC | TX | ERCO | Cameron Wind 1 LLC | 16.4 | 32.8 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.76003 | 0.0089563 | 384.4817 | 0.06408 | 0.054612 | 0.93592 | FALSE | A
135 | 64656 | 3 | 2025-06 | 2025-08 | PARTIAL_AVAILABILITY | 330 | 3 | 330 | AES West Oahu Solar Hybrid | HI | HECO | AES Distributed Energy | 12.5 | 50 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 1.0887 | 0.16767 | 454.08 | 0.07568 | 1.3414 | 0.92432 | FALSE | C
136 | 65243 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 322.5731 | 24 | 322.5731 | New Rosewood BESS | NC | CPLE | North Carolina El Member Corp | 2.5 | 10 | 4 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.80712 | 0.015574 | 64.8 | 0.0108 | 0.62295 | 0.9892 | FALSE | A
137 | 65245 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 318.5144 | 24 | 318.5144 | Rocky Point BESS | NC | CPLE | North Carolina El Member Corp | 5 | 5 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.77489 | 0.01398 | 130.8 | 0.0218 | 0.27959 | 0.9782 | FALSE | A
138 | 63238 | 9 | 2025-03 | 2025-11 | FULL_OUTAGE | 316.5 | 9 | 316.5 | Willis Battery Storage | NY | NYIS | New York Power Authority | 20 | 20 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  |  |  | 64.225 | 0.010704 |  | 0.9893 | FALSE | B
139 | 64614 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 314.6782 | 24 | 314.6782 | Kearny South Energy Storage | CA | CISO | San Diego Gas & Electric Co | 10 | 40 | 4 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.85693 | 0.037152 | 667.1292 | 0.11119 | 0.37152 | 0.88881 | FALSE | A
140 | 66181 | 13 | 2024-12 | 2025-12 | FULL_OUTAGE | 314.5 | 13 | 314.5 | Beacon Solar, LLC | MA | ISNE | Agilitas Energy, Inc. | 5 | 7.8 | 1.56 | 1.5-2.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_tight | 0.94614 | 0.0035222 | 185.9402 | 0.03099 | 0.070443 | 0.96901 | FALSE | C
141 | 67886 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 313.4262 | 24 | 313.4262 | Gunther | NY | NYIS | NineDot Holdings, LLC | 3 | 12.4 | 4.1333 | 2.5-4.5h | 2023 | NIB | CS | FALSE |  | 0.78267 | 0.01248 | 76.5054 | 0.012751 | 0.41601 | 0.98725 | FALSE | A
142 | 64916 | 5 | 2025-04 | 2025-09 | PARTIAL_AVAILABILITY | 313 | 3 | 313 | Swoose I | TX | ERCO | Swoose | 9.9 | 19.8 | 2 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.93017 | 0.037949 | 1390.2778 | 0.23171 | 0.38332 | 0.76829 | FALSE | A
143 | 63612 | 6 | 2024-01 | 2025-03 | PARTIAL_AVAILABILITY | 304.817 | 3 | 304.817 | DATS | CA | CISO | Hybrid-Electric Building Technologies West Los Angeles 1, LLC | 1 | 6 | 6 | >4.5h | 2017 | LIB | CS | FALSE |  | 0.86012 | 0.0020414 | 783 | 0.1305 | 0.20414 | 0.8695 | FALSE | A
144 | 64319 | 3 | 2025-08 | 2025-10 | PARTIAL_AVAILABILITY | 290.5 | 3 | 290.5 | Ranchtown | TX | ERCO | Engie North America | 9.9 | 9.9 | 1 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.93547 | 0.018885 | 2560.7828 | 0.4268 | 0.19076 | 0.5732 | FALSE | A
145 | 65951 | 3 | 2024-07 | 2024-09 | PARTIAL_AVAILABILITY | 290 | 3 | 290 | Bowling Green Energy Storage Project | OH | PJM | VESI 21 LLC | 12 | 12 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.90494 | -0.012802 | 5467.6944 | 0.91128 | -0.10668 | 0.088718 | FALSE | A
146 | 63022 | 36 | 2023-01 | 2025-12 | THERMAL_AUX | 298.4837 | 36 | 286.0011 | Fort Carson Battery Energy Storage Syste | CO | WACM | Department of the Army, Fort Carson | 4.2 | 8.5 | 2.0238 | 1.5-2.5h | 2018 | LIB | CS | FALSE |  | 0.50472 | -0.0070776 | 902.6569 | 0.15044 | -0.16851 | 0.84956 | FALSE | A
147 | 67861 | 2 | 2024-08 | 2024-09 | LOW_ETA_AND_LOW_UTI | 280.3096 | 2 | 280.3096 | Connolly BESS | TX | ERCO | BT Connolly Storage, LLC | 125 | 250 | 2 | 1.5-2.5h | 2024 | OTH | CS | FALSE |  | 0.83155 | -0.059416 | 412.584 | 0.068764 | -0.047533 | 0.93124 | FALSE | B
148 | 59444 | 24 | 2024-01 | 2025-12 | ELEVATED_P_AUX | 264 | 24 | 264 | Desert Star Hybrid | AZ | AZPS | Arizona Public Service Co | 10 | 30 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.931 | 0.14655 | 634.8 | 0.1058 | 1.4655 | 0.8942 | FALSE | C
149 | 64374 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 298.5 | 36 | 241.5 | Norwich Solar and Energy Storage CSG | NY | NYIS | DG New York CS, LLC | 5 | 15 | 3 | 2.5-4.5h | 2021 | LIB | CS | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_tight | 0.83305 | 7.854e-05 | 189.9333 | 0.031656 | 0.0015708 | 0.96834 | FALSE | C
150 | 62875 | 31 | 2023-05 | 2025-12 | THERMAL_AUX | 399.7372 | 29 | 237.982 | Wildcat I Energy Storage LLC | CA | CISO | Wildcat I Energy Storage LLC | 3 | 12 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.99712 | 0.019731 | 699.75 | 0.11663 | 0.6577 | 0.88338 | FALSE | A
151 | 65244 | 18 | 2024-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 225.5295 | 11 | 225.5295 | Queens Creek BESS | NC | CPLE | North Carolina El Member Corp | 2.5 | 5 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.74284 | 0.013073 | 130.4 | 0.021733 | 0.52291 | 0.97827 | FALSE | A
152 | 63522 | 6 | 2023-08 | 2025-10 | PARTIAL_AVAILABILITY | 491.5 | 4 | 225 | Hickory Park Solar Hybrid | GA | SOCO | RWE Clean Energy | 40 | 80 | 2 | 1.5-2.5h | 2022 | LIB | OT | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | 0.94086 | 0.24958 | 842.4875 | 0.14041 | 0.62394 | 0.85959 | FALSE | C
153 | 64617 | 4 | 2023-12 | 2025-11 | PARTIAL_AVAILABILITY | 319.5 | 2 | 222.5 | Kearsarge William Way | MA | ISNE | Kearsarge William Way LLC | 2.6 | 9.5 | 3.6538 | 2.5-4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.9249 | 0.0096706 | 916.6316 | 0.15277 | 0.37195 | 0.84723 | FALSE | C
154 | 57206 | 8 | 2024-04 | 2025-09 | PARTIAL_AVAILABILITY | 220 | 3 | 220 | Soldotna | AK |  | Homer Electric Assn Inc | 46.5 | 93 | 2 | 1.5-2.5h | 2022 | LIB | CS | FALSE |  | 1.1293 | 0.15811 | 101.0108 | 0.016835 | 0.34002 | 0.98316 | FALSE | A
155 | 60467 | 2 | 2025-08 | 2025-09 | PARTIAL_AVAILABILITY | 219.5 | 2 | 219.5 | Red Rock | AZ | AZPS | Arizona Public Service Co | 41 | 164 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.91854 | 0.14349 | 241.9858 | 0.040331 | 0.34998 | 0.95967 | FALSE | C
156 | 62874 | 7 | 2023-12 | 2024-11 | PARTIAL_AVAILABILITY | 250 | 5 | 215 | Acorn I Energy Storage LLC | CA | CISO | Acorn I Energy Storage LLC | 2 | 6 | 3 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.89439 | -0.00037965 | 1205.7917 | 0.20097 | -0.018982 | 0.79903 | FALSE | A
157 | 66228 | 15 | 2023-06 | 2025-12 | FULL_OUTAGE | 347.192 | 7 | 212.5 | Salt Point Solar (Hybrid) | NY | NYIS | Generate Capital | 2 | 2 | 1 | <1.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.93738 | 0.0011547 | 604.0455 | 0.10067 | 0.057736 | 0.89933 | FALSE | C
158 | 63610 | 4 | 2024-01 | 2024-04 | PARTIAL_AVAILABILITY | 211.96 | 4 | 211.96 | Baker | CA | CISO | Hybrid-Electric Building Technologies West Los Angeles 1, LLC | 1.2 | 6.3 | 5.25 | >4.5h | 2019 | LIB | CS | FALSE |  | 0.819 | -0.0017171 | 500.2778 | 0.08338 | -0.14309 | 0.91662 | FALSE | A
159 | 64207 | 12 | 2024-09 | 2025-11 | THERMAL_AUX | 210.5 | 6 | 210.5 | Crane Battery Energy Storage System | IN | MISO | Duke Energy Indiana, LLC | 5 | 5 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.91335 | 0.0050732 | 485.4 | 0.0809 | 0.10146 | 0.9191 | FALSE | A
160 | 65248 | 18 | 2024-04 | 2025-12 | LOW_ETA_AND_LOW_UTI | 209.7404 | 9 | 209.7404 | Collier BESS | NC | CPLE | North Carolina El Member Corp | 2.5 | 5 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.78737 | 0.014631 | 139.8 | 0.0233 | 0.58524 | 0.9767 | FALSE | A
161 | 63995 | 23 | 2024-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 206.0711 | 23 | 206.0711 | Trenton | FL | FPC | Duke Energy Florida, LLC | 11 | 10.1 | 0.91818 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.67784 | 0.0040787 | 64.1997 | 0.0107 | 0.037079 | 0.9893 | FALSE | A
162 | 69300 | 4 | 2025-09 | 2025-12 | FULL_OUTAGE | 206 | 4 | 206 | Regis Continental | TX | ERCO | Regis Continental LLC | 9.9 | 9.9 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  |  |  | 86.5152 | 0.014419 |  | 0.98558 | FALSE | B
163 | 64293 | 2 | 2025-01 | 2025-02 | PARTIAL_AVAILABILITY | 202 | 2 | 202 | Alvin | TX | ERCO | Engie North America | 9.9 | 9.9 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.94288 | 0.015546 | 1273.0303 | 0.21217 | 0.15703 | 0.78783 | FALSE | B
164 | 68148 | 13 | 2024-12 | 2025-12 | LOW_ETA_AND_LOW_UTI | 200.0115 | 13 | 200.0115 | Baldwin Solar BESS | IL | MISO | Vistra Corp | 2 | 8 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.57822 | -0.012652 | 64.625 | 0.010771 | -0.63262 | 0.98923 | FALSE | C
165 | 67185 | 2 | 2025-08 | 2025-09 | PARTIAL_AVAILABILITY | 200 | 2 | 200 | Groton BESS 1 | MA | ISNE | Groton BESS 1 LLC | 2 | 8.9 | 4.45 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.86999 | 0.0082207 | 276.4045 | 0.046067 | 0.41104 | 0.95393 | FALSE | B
166 | 67041 | 9 | 2025-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 193.978 | 5 | 193.978 | McLauchin | NC | CPLE | North Carolina El Member Corp | 15 | 30 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.78017 | 0.015015 | 60.9333 | 0.010156 | 0.1001 | 0.98984 | FALSE | A
167 | 63722 | 14 | 2023-01 | 2025-07 | FULL_OUTAGE | 195.013 | 9 | 192 | Rawhide Prairie Solar Hybrid | CO | PSCO | Greenbacker Renewable Energy Corporation | 1 | 2 | 2 | 1.5-2.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.82907 | 3.6514e-05 | 1104.5 | 0.18408 | 0.0036514 | 0.81592 | FALSE | C
168 | 64917 | 4 | 2025-08 | 2025-12 | PARTIAL_AVAILABILITY | 188 | 2 | 188 | Triple Butte I | TX | ERCO | Triple Butte | 7.5 | 15 | 2 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.91182 | 0.018965 | 1464.4667 | 0.24408 | 0.25286 | 0.75592 | FALSE | B
169 | 63614 | 3 | 2024-01 | 2024-03 | PARTIAL_AVAILABILITY | 183.3865 | 3 | 183.3865 | LAWRP | CA | CISO | Hybrid-Electric Building Technologies West Los Angeles 1, LLC | 1 | 5 | 5 | >4.5h | 2019 | LIB | CS | FALSE |  | 0.84181 | -0.00050064 | 541.2 | 0.0902 | -0.050064 | 0.9098 | FALSE | A
170 | 60661 | 15 | 2024-05 | 2025-12 | THERMAL_AUX | 177.8477 | 6 | 177.8477 | Mira Loma Energy Storage Facility | CA | CISO | Southern California Edison Co | 20 | 80 | 4 | 2.5-4.5h | 2016 | LIB | CS | FALSE |  | 0.88062 | 0.057217 | 309.6375 | 0.051606 | 0.28609 | 0.94839 | FALSE | A
171 | 63337 | 4 | 2025-02 | 2025-10 | PARTIAL_AVAILABILITY | 168 | 2 | 168 | Lansing Renewables, LLC | NY | NYIS | Lansing Renewables, LLC | 3 | 3 | 1 | <1.5h | 2022 | LIB | CT | TRUE | pv_same_plant,dc_coupled | 0.91175 | 0.0010695 | 874.3333 | 0.14572 | 0.035651 | 0.85428 | FALSE | C
172 | 66794 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 167.5913 | 24 | 167.5913 | Diboll BESS | TX | ERCO | HEN Infrastructure, L.L.C. | 9.9 | 9.9 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.82266 | 0.0065412 | 202.4242 | 0.033737 | 0.066072 | 0.96626 | FALSE | A
173 | 66488 | 12 | 2024-01 | 2025-12 | FULL_OUTAGE | 162.5 | 5 | 162.5 | Davis Solar | NY | NYIS | Generate Capital | 2 | 4 | 2 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.9022 | 0.0029007 | 177.75 | 0.029625 | 0.14504 | 0.97037 | FALSE | C
174 | 65945 | 4 | 2025-08 | 2025-11 | FULL_OUTAGE | 162 | 4 | 162 | Brookville Smart Bus Depot Microgrid | MD | PJM | AlphaStruxure Service Co LP | 1.5 | 4.3 | 2.8667 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.92614 | 0.00083745 | 305.1163 | 0.050853 | 0.05583 | 0.94915 | FALSE | C
175 | 54639 | 6 | 2024-09 | 2025-07 | PARTIAL_AVAILABILITY | 152 | 3 | 152 | Berlin Gorham | NH | ISNE | Great Lakes Hydro America LLC | 14 | 14 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.90483 | 0.072447 | 1289.9286 | 0.21499 | 0.51748 | 0.78501 | FALSE | A
176 | 61891 | 9 | 2020-02 | 2024-04 | PARTIAL_AVAILABILITY | 4142.5 | 3 | 148 | Stryker 22, L.L.C. | NJ | PJM | Stryker 22, L.L.C. | 19.8 | 19.8 | 1 | <1.5h | 2018 | LIB | CS | FALSE |  | 0.88438 | 0.087767 | 13575.7989 | 2.2626 | 0.44327 | 0 | FALSE | A
177 | 63998 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 145.3104 | 24 | 145.3104 | Jennings Energy Storage Facility | FL | FPC | Duke Energy Florida, LLC | 5.5 | 5.5 | 1 | <1.5h | 2022 | LIB | CS | FALSE |  | 0.59505 | -0.00030688 | 141.6364 | 0.023606 | -0.0055796 | 0.97639 | FALSE | A
178 | 65242 | 20 | 2023-07 | 2025-12 | FULL_OUTAGE | 154.5 | 13 | 144 | Charlemont A | MA | ISNE | Agilitas Energy, Inc. | 2.5 | 3.8 | 1.52 | 1.5-2.5h | 2021 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.92833 | 0.00096191 | 97.1053 | 0.016184 | 0.038476 | 0.98382 | FALSE | C
179 | 65953 | 2 | 2024-10 | 2024-11 | PARTIAL_AVAILABILITY | 143 | 2 | 143 | Howell Energy Storage Project | NJ | PJM | VESI 24 LLC | 7 | 7 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.89693 | -0.0030635 | 5686.7143 | 0.94779 | -0.043764 | 0.052214 | FALSE | B
180 | 66420 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 141 | 2 | 141 | Five Wells Solar Center - Hybrid | TX | ERCO | Five Wells Solar Center, LLC | 262.5 | 250 | 0.95238 | <1.5h | 2024 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.92487 | 1.1464 | 354.492 | 0.059082 | 0.43673 | 0.94092 | FALSE | C
181 | 66772 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 140.5 | 2 | 140.5 | Estrella Solar & Storage | CA | CISO | AES Clean Energy | 28 | 112 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.89305 | 0.010826 | 536.9196 | 0.089487 | 0.038665 | 0.91051 | FALSE | C
182 | 62835 | 21 | 2023-12 | 2025-12 | FULL_OUTAGE | 180.5422 | 17 | 121.5422 | Acushnet Ball Plant 2 | MA | ISNE | Acushnet | 1.5 | 3 | 2 | 1.5-2.5h | 2019 | LIB | CS | FALSE |  | 0.75316 | -0.0012365 | 1747.6667 | 0.29128 | -0.082435 | 0.70872 | FALSE | A
183 | 67042 | 7 | 2025-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 119.0747 | 5 | 119.0747 | Butler | NC | CPLE | North Carolina El Member Corp | 10 | 20 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.83723 | 0.027067 | 63.85 | 0.010642 | 0.27067 | 0.98936 | FALSE | A
184 | 63255 | 2 | 2024-10 | 2024-11 | PARTIAL_AVAILABILITY | 117 | 2 | 117 | 2W Permian Solar Project Hybrid | TX | ERCO | 2W Permian Solar, LLC | 40 | 40 | 1 | <1.5h | 2021 | LIB | BL | TRUE | pv_same_plant | 0.45877 | -0.003097 | 251.225 | 0.041871 | -0.0077424 | 0.95813 | FALSE | C
185 | 65950 | 2 | 2024-12 | 2025-01 | PARTIAL_AVAILABILITY | 117 | 2 | 117 | Kearsarge 100 Sohier Rd | MA | ISNE | Kearsarge Beverly LLC | 1.8 | 6.4 | 3.5556 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.94223 | 0.0087754 | 425.1562 | 0.070859 | 0.48752 | 0.92914 | FALSE | C
186 | 66807 | 2 | 2025-01 | 2025-02 | PARTIAL_AVAILABILITY | 116 | 2 | 116 | SEPV Cuyama Hybrid | CA | CISO | SEPV Cuyama, LLC | 3 | 12 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.95478 | 0.0055936 | 635.4167 | 0.1059 | 0.18645 | 0.8941 | FALSE | C
187 | 66499 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 115.5 | 24 | 115.5 | Federalsburg Energy Storage 1 LLC | MD | PJM | Convergent Energy and Power LP | 1.2 | 2.4 | 2 | 1.5-2.5h | 2021 | LIB | CT | TRUE | pv_same_plant,dc_coupled | 0.84362 | 0.00045144 | 578.75 | 0.096458 | 0.03762 | 0.90354 | FALSE | C
188 | 69411 | 2 | 2025-06 | 2025-07 | PARTIAL_AVAILABILITY | 114.5 | 2 | 114.5 | Snyder BESS | TX | ERCO | Snyder ESS Assets, LLC | 10 | 20 | 2 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.89207 | 0.021575 | 763.75 | 0.12729 | 0.21575 | 0.87271 | FALSE | B
189 | 63011 | 2 | 2024-03 | 2024-04 | FULL_OUTAGE | 114 | 2 | 114 | Cronin Road Solar 1, LLC CSG Hybrid | MA | ISNE | AES Distributed Energy | 1.5 | 7.7 | 5.1333 | >4.5h | 2020 | LIB | CT | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.98201 | 0.0014219 | 460.9091 | 0.076818 | 0.094792 | 0.92318 | FALSE | C
190 | 66218 | 19 | 2023-09 | 2025-12 | FULL_OUTAGE | 278.5 | 7 | 113 | Dubois Solar (Hybrid) | NY | NYIS | Generate Capital | 2 | 4 | 2 | 1.5-2.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.99165 | 0.0044273 | 521.1856 | 0.086864 | 0.22136 | 0.91314 | FALSE | C
191 | 54134 | 2 | 2024-02 | 2024-03 | PARTIAL_AVAILABILITY | 113 | 2 | 113 | Great Lakes Hydro America - ME | ME | ISNE | Great Lakes Hydro America LLC | 20 | 20 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.88399 | 0.10614 | 2637.25 | 0.43954 | 0.53069 | 0.56046 | FALSE | B
192 | 59020 | 3 | 2025-05 | 2025-07 | PARTIAL_AVAILABILITY | 112 | 3 | 112 | Gila Bend Hybrid | AZ | AZPS | Arizona Public Service Co | 32 | 96 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.84217 | 0.072494 | 528.6562 | 0.088109 | 0.22654 | 0.91189 | FALSE | C
193 | 63609 | 3 | 2025-01 | 2025-03 | PARTIAL_AVAILABILITY | 111.5 | 3 | 111.5 | Allergan | CA | CISO | Hybrid-Electric Building Technologies West Los Angeles 1, LLC | 1.5 | 9 | 6 | >4.5h | 2019 | LIB | CS | FALSE |  | 0.8658 | 0.00016476 | 370.4444 | 0.061741 | 0.010984 | 0.93826 | FALSE | A
194 | 64765 | 13 | 2024-01 | 2025-02 | LOW_ETA_AND_LOW_UTI | 111.4575 | 7 | 111.4575 | Madison ESS | ME | ISNE | Agilitas Energy, Inc. | 4.9 | 10 | 2.0408 | 1.5-2.5h | 2019 | LIB | CS | FALSE |  | 0.58379 | -0.004273 | 178.3583 | 0.029726 | -0.087204 | 0.97027 | FALSE | A
195 | 60760 | 24 | 2023-01 | 2024-12 | LOW_ETA_AND_LOW_UTI | 205.0762 | 24 | 111.1559 | PPA Grand | CA | CISO | esVolta LP | 2 | 8 | 4 | 2.5-4.5h | 2016 | LIB | BL | FALSE |  | 0.78976 | 0.011445 | 1484.0312 | 0.24734 | 0.57223 | 0.75266 | FALSE | A
196 | 61334 | 9 | 2024-12 | 2025-12 | FULL_OUTAGE | 102.5 | 6 | 102.5 | Volkman Road Solar Array Hybrid | IN | MISO | Southern Indiana Gas & Elec Co | 1 | 4.6 | 4.6 | >4.5h | 2019 | LIB | CT | TRUE | pv_same_plant | 0.90287 | -0.00016941 | 411.5217 | 0.068587 | -0.016941 | 0.93141 | FALSE | C
197 | 65217 | 35 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 102 | 28 | 102 | South Goshen Community Solar | NY | NYIS | AES Distributed Energy | 4.5 | 17 | 3.7778 | 2.5-4.5h | 2021 | LIB | OT | TRUE | pv_same_plant,dc_tight | 0.84243 | 0.0026557 | 139.1765 | 0.023196 | 0.059015 | 0.9768 | FALSE | C
198 | 66791 | 3 | 2024-10 | 2024-12 | PARTIAL_AVAILABILITY | 102 | 3 | 102 | Garden City East BESS | TX | ERCO | HEN Infrastructure, L.L.C. | 9.9 | 9.9 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.92632 | 0.010839 | 357.3737 | 0.059562 | 0.10948 | 0.94044 | FALSE | A
199 | 67578 | 2 | 2025-09 | 2025-10 | PARTIAL_AVAILABILITY | 102 | 2 | 102 | Sandwich | MA | ISNE | LSE Ophiuchus LLC | 2 | 4.6 | 2.3 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.99441 | -0.00050183 | 1912.6087 | 0.31877 | -0.025092 | 0.68123 | FALSE | C
200 | 67162 | 7 | 2024-06 | 2025-05 | LOW_ETA_AND_LOW_UTI | 101.0451 | 4 | 101.0451 | Groton BESS 2 | MA | ISNE | Groton BESS 2 LLC | 2 | 8.9 | 4.45 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.84758 | 0.014706 | 209.6629 | 0.034944 | 0.7353 | 0.96506 | FALSE | A
201 | 65531 | 9 | 2024-02 | 2025-10 | LOW_ETA_AND_LOW_UTI | 99.4785 | 4 | 99.4785 | Deer Run Battery | IA | MISO | Interstate Power and Light Co | 5 | 10 | 2 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.77427 | 0.0085555 | 430 | 0.071667 | 0.17111 | 0.92833 | FALSE | A
202 | 66182 | 23 | 2023-04 | 2025-12 | FULL_OUTAGE | 97.5 | 14 | 97.5 | Town of Amherst Solar | MA | ISNE | Agilitas Energy, Inc. | 2.5 | 2 | 0.8 | <1.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_tight | 0.69192 | -0.00098809 | 381 | 0.0635 | -0.039523 | 0.9365 | FALSE | C
203 | 10493 | 2 | 2025-01 | 2025-02 | PARTIAL_AVAILABILITY | 97.5 | 2 | 97.5 | Rumford Falls Hydro Facility | ME | ISNE | Brookfield Power New England | 8 | 16 | 2 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.8457 | 0.063707 | 909.875 | 0.15165 | 0.79634 | 0.84835 | FALSE | B
204 | 68773 | 2 | 2025-04 | 2025-05 | FULL_OUTAGE | 97.5 | 2 | 97.5 | Apollo | MA | ISNE | Sunrise on Wing Ln. LLC | 1.3 | 2.8 | 2.1538 | 1.5-2.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled | 0.9261 | 0.0009087 | 1607.381 | 0.2679 | 0.0699 | 0.7321 | FALSE | C
205 | 65692 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 94.5 | 2 | 94.5 | NY6 Battery | NY | NYIS | Key Capture Energy | 20 | 42 | 2.1 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.90135 | 0.16228 | 1841.9524 | 0.30699 | 0.81142 | 0.69301 | FALSE | B
206 | 63996 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 91.2418 | 24 | 91.2418 | Cape San Blas | FL | FPC | Duke Energy Florida, LLC | 5.5 | 14.3 | 2.6 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.82172 | 4.4219e-05 | 138.4266 | 0.023071 | 0.00080398 | 0.97693 | FALSE | A
207 | 62147 | 5 | 2023-01 | 2024-07 | PARTIAL_AVAILABILITY | 2854.4495 | 3 | 89 | KCE NY 1 | NY | NYIS | KCE NY 1, LLC | 20 | 8.4 | 0.42 | <1.5h | 2019 | LIB | CS | FALSE |  | 0.87338 | -0.025964 | 14062.8571 | 2.3438 | -0.12982 | 0 | FALSE | A
208 | 64296 | 2 | 2024-06 | 2024-07 | PARTIAL_AVAILABILITY | 87 | 2 | 87 | Brazoria | TX | ERCO | Engie North America | 9.9 | 9.9 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.9418 | 0.013996 | 1226.1616 | 0.20436 | 0.14137 | 0.79564 | FALSE | B
209 | 64314 | 2 | 2025-02 | 2025-03 | PARTIAL_AVAILABILITY | 85 | 2 | 85 | Dickinson | TX | ERCO | Engie North America | 9.9 | 9.9 | 1 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.9263 | 0.0023861 | 2741.9024 | 0.45698 | 0.024102 | 0.54302 | FALSE | B
210 | 67043 | 9 | 2025-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 83.6679 | 5 | 83.6679 | Double Creek | NC | CPLE | North Carolina El Member Corp | 5 | 10 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.85318 | 0.016769 | 71.4 | 0.0119 | 0.33538 | 0.9881 | FALSE | A
211 | 63214 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 83.5 | 12 | 83.5 | Middleton Solar Park | MA | ISNE | Novis Renewables, LLC | 3 | 6.6 | 2.2 | 1.5-2.5h | 2019 | LIB | CS | TRUE | pv_same_plant | 0.96937 | 0.014724 | 285.9848 | 0.047664 | 0.49081 | 0.95234 | FALSE | C
212 | 63774 | 2 | 2025-11 | 2025-12 | FULL_OUTAGE | 83 | 2 | 83 | Mount Kisco Landfill Solar & Storage CSG | NY | NYIS | BQ Energy LLC | 0.7 | 2.1 | 3 | 2.5-4.5h | 2020 | LIB | CS | TRUE | colocated_firming,pv_same_plant |  |  | 151.9048 | 0.025317 |  | 0.97468 | FALSE | C
213 | 62714 | 32 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 135.0856 | 29 | 81.2918 | Eyak Service Center BESS | AK |  | Cordova Electric Coop, Inc | 1 | 0.9 | 0.9 | <1.5h | 2019 | LIB | CS | FALSE |  | 0.58822 | 0.0010686 | 481.1111 | 0.080185 | 0.10686 | 0.91981 | FALSE | A
214 | 68069 | 4 | 2024-10 | 2025-01 | FULL_OUTAGE | 81 | 4 | 81 | Old Frontier Solar III | MA | ISNE | Old Frontier Solar III PV, LLC | 2 | 2.2 | 1.1 | <1.5h | 2022 | LIB | CT | TRUE | pv_same_plant,dc_coupled | 0.9135 | -0.00049603 | 400.4545 | 0.066742 | -0.024802 | 0.93326 | FALSE | C
215 | 67899 | 12 | 2024-05 | 2025-07 | THERMAL_AUX | 78.9561 | 4 | 78.9561 | PNY BESS LLC | PA | PJM | Citizens Enterprises Corporation | 6.2 | 6.2 | 1 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.94369 | 0.020433 | 6119.3145 | 1.0199 | 0.32956 | 0 | FALSE | A
216 | 64092 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 77 | 12 | 77 | Great Lakes Seaway Community Solar | NY | NYIS | OYA Great Lakes Seaway LLC | 5 | 15 | 3 | 2.5-4.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_tight |  |  | 30.0667 | 0.0050111 |  | 0.99499 | FALSE | C
217 | 57996 | 5 | 2023-01 | 2024-11 | PARTIAL_AVAILABILITY | 183.3375 | 3 | 77 | Auwahi Wind Energy Hybrid | HI |  | Auwahi Wind Energy LLC | 11 | 4.4 | 0.4 | <1.5h | 2012 | LIB | CS | FALSE |  | 1.1137 | 0.025302 | 3143.3144 | 0.52389 | 0.23002 | 0.47611 | FALSE | A
218 | 64395 | 22 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 75.5 | 12 | 75.5 | ZPD-PT Solar Project 2017-006 LLC Hybrid | MA | ISNE | AES Distributed Energy | 2.5 | 5 | 2 | 1.5-2.5h | 2021 | LIB | CT | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.78096 | -0.00047134 | 388.2 | 0.0647 | -0.018853 | 0.9353 | FALSE | C
219 | 64696 | 2 | 2023-12 | 2024-01 | PARTIAL_AVAILABILITY | 135 | 2 | 73 | Dunstable Solar 1, LLC | MA | ISNE | AES Distributed Energy | 4.5 | 20.2 | 4.4889 | 2.5-4.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 1.006 | 0.0045351 | 496.1386 | 0.08269 | 0.10078 | 0.91731 | FALSE | C
220 | 62970 | 7 | 2024-01 | 2024-07 | LOW_ETA_AND_LOW_UTI | 71.5335 | 7 | 71.5335 | Syncarpha Puddon II Hybrid CSG | MA | ISNE | Syncarpha Puddon II, LLC | 4 | 8 | 2 | 1.5-2.5h | 2021 | LIB | CT | TRUE | pv_same_plant | 0.79998 | 0.0011774 | 318.375 | 0.053062 | 0.029436 | 0.94694 | FALSE | C
221 | 67170 | 16 | 2024-03 | 2025-12 | LOW_ETA_AND_LOW_UTI | 71 | 9 | 71 | Amazon SAN3 Solar Project | CA | CISO | Solar Star Prime 4 LLC | 2.4 | 8.9 | 3.7083 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.8399 | -0.0049746 | 208.5393 | 0.034757 | -0.20728 | 0.96524 | FALSE | C
222 | 57561 | 2 | 2025-06 | 2025-07 | PARTIAL_AVAILABILITY | 71 | 2 | 71 | Cotton Center Solar Hybrid | AZ | AZPS | Arizona Public Service Co | 17 | 51 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.86715 | 0.08643 | 571.5686 | 0.095261 | 0.50841 | 0.90474 | FALSE | C
223 | 64318 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 71 | 2 | 71 | Pueblo BA | TX | ERCO | Engie North America | 19.8 | 19.8 | 1 | <1.5h | 2022 | LIB | CS | FALSE |  | 0.92569 | 0.060505 | 1782.2727 | 0.29705 | 0.30558 | 0.70295 | FALSE | B
224 | 64084 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 66.5 | 12 | 66.5 | Blanchard Road 1 Community Solar | NY | NYIS | OYA Blanchard Road LLC | 5 | 15 | 3 | 2.5-4.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_tight |  |  | 27.7333 | 0.0046222 |  | 0.99538 | FALSE | C
225 | 60959 | 26 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 66.5 | 7 | 66.5 | Chocksett Rd Energy Storage Project | MA | ISNE | Sterling Municipal Light Department - (MA) | 2 | 3.9 | 1.95 | 1.5-2.5h | 2017 | LIB | CS | TRUE | rte_gt_1 | 0.61144 | 0.0053094 | 276.7308 | 0.046122 | 0.26547 | 0.95388 | FALSE | C
226 | 64315 | 2 | 2024-12 | 2025-01 | PARTIAL_AVAILABILITY | 66.5 | 2 | 66.5 | Loop 463 | TX | ERCO | Engie North America | 9.9 | 9.9 | 1 | <1.5h | 2021 | LIB | CS | FALSE |  | 0.94573 | 0.019251 | 2816.3721 | 0.4694 | 0.19446 | 0.5306 | FALSE | B
227 | 64766 | 36 | 2023-01 | 2025-12 | ELEVATED_P_AUX | 66 | 36 | 66 | Redwood Coast Airport Microgrid | CA | CISO | Redwood Coast Energy Authority | 2.2 | 8.8 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled | 0.87677 | 0.034564 | 677.9545 | 0.11299 | 1.5711 | 0.88701 | FALSE | C
228 | 66789 | 9 | 2024-02 | 2024-10 | LOW_ETA_AND_LOW_UTI | 65.1611 | 9 | 65.1611 | Lufkin South BESS | TX | ERCO | HEN Infrastructure, L.L.C. | 9.9 | 9.9 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.82512 | 0.004585 | 233.8384 | 0.038973 | 0.046313 | 0.96103 | FALSE | A
229 | 64695 | 2 | 2024-10 | 2024-11 | PARTIAL_AVAILABILITY | 63 | 2 | 63 | Angel Fire Energy Facility | NM | PNM | Angel Fire Energy Facility, LLC | 3.7 | 15 | 4.0541 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.89142 | 0.02132 | 299.1333 | 0.049856 | 0.57621 | 0.95014 | FALSE | C
230 | 64630 | 2 | 2025-04 | 2025-05 | PARTIAL_AVAILABILITY | 59 | 2 | 59 | Rabbitbrush Solar, LLC | CA | CISO | Leeward Asset Management, LLC | 20 | 50 | 2.5 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.8556 | 0.017078 | 980.92 | 0.16349 | 0.085388 | 0.83651 | FALSE | C
231 | 1615 | 8 | 2024-07 | 2025-12 | FULL_OUTAGE | 58 | 5 | 58 | Nantucket Hybrid | MA | ISNE | Nantucket Electric Co | 6 | 48 | 8 | >4.5h | 2019 | LIB | BL | FALSE |  | 0.87413 | 0.02725 | 26.9583 | 0.0044931 | 0.45416 | 0.99551 | FALSE | A
232 | 62999 | 12 | 2024-02 | 2025-12 | FULL_OUTAGE | 55.5 | 10 | 55.5 | Finchville Solar, LLC Hybrid CSG | NY | NYIS | AES Distributed Energy | 3 | 4.4 | 1.4667 | <1.5h | 2020 | LIB | CT | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.9681 | -7.1018e-06 | 287.7273 | 0.047955 | -0.00023673 | 0.95205 | FALSE | C
233 | 65670 | 9 | 2024-09 | 2025-12 | LOW_ETA_AND_LOW_UTI | 53 | 5 | 53 | Ventura | MA | ISNE | Ventura Drive Dartmouth Solar 1, LLC | 1 | 5 | 5 | >4.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.77168 | 0.00051479 | 249 | 0.0415 | 0.051479 | 0.9585 | FALSE | C
234 | 67845 | 3 | 2025-01 | 2025-03 | LOW_ETA_AND_LOW_UTI | 52.9129 | 3 | 52.9129 | Junction BESS | TX | ERCO | SBESS TX5 LLC | 9.9 | 24.7 | 2.4949 | 1.5-2.5h | 2025 | LIB | CS | FALSE |  | 0.80887 | 0.012724 | 178.3401 | 0.029723 | 0.12853 | 0.97028 | FALSE | A
235 | 61186 | 31 | 2023-05 | 2025-12 | LOW_ETA_AND_LOW_UTI | 58.4569 | 17 | 51.4141 | Boston Medical Center CHP Plant | MA | ISNE | Boston Medical Center | 1 | 1.1 | 1.1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.69749 | 0.0005437 | 160.9091 | 0.026818 | 0.05437 | 0.97318 | FALSE | A
236 | 64752 | 19 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 50 | 10 | 50 | John Hopkins Middle School Microgrid | FL | FPC | Duke Energy Florida, LLC | 2.5 | 18 | 7.2 | >4.5h | 2023 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.81709 | 0.001213 | 72.9444 | 0.012157 | 0.048521 | 0.98784 | FALSE | C
237 | 61925 | 84 | 2019-01 | 2025-12 | THERMAL_AUX | 145.3768 | 84 | 49.6901 | Casa Mesa Wind Energy Center Hybrid | NM | PNM | Casa Mesa Wind, LLC | 1 | 1 | 1 | <1.5h | 2018 | LIB | CS | FALSE |  | 0.69984 | 0.0031447 | 1361.1667 | 0.22686 | 0.31447 | 0.77314 | FALSE | A
238 | 64087 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 49.5 | 12 | 49.5 | Blanchard Road 2 Community Solar | NY | NYIS | OYA Blanchard Road 2 LLC | 5 | 15 | 3 | 2.5-4.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_tight |  |  | 21.3333 | 0.0035556 |  | 0.99644 | FALSE | C
239 | 60565 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 93.748 | 36 | 49 | Borrego Springs Energy Storage | CA | CISO | SDGE Batteries | 1.5 | 4.5 | 3 | 2.5-4.5h | 2013.3333 | LIB | CS | TRUE | rte_gt_1 | 0.60141 | -0.00090114 | 201.7407 | 0.033623 | -0.060076 | 0.96638 | FALSE | C
240 | 63473 | 4 | 2023-12 | 2025-10 | FULL_OUTAGE | 89.5 | 2 | 49 | West A&B Solar Project Hybrid CSG | MA | ISNE | AES Distributed Energy | 1.8 | 3.5 | 1.9444 | 1.5-2.5h | 2020 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.93143 | 0.0011315 | 590.5714 | 0.098429 | 0.062861 | 0.90157 | FALSE | C
241 | 60061 | 4 | 2024-10 | 2025-09 | PARTIAL_AVAILABILITY | 47 | 2 | 47 | Citrus Solar Energy Center Hybrid | FL | FPL | Florida Power & Light Co | 4 | 16 | 4 | 2.5-4.5h | 2018 | LIB | CS | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_tight | 0.8843 | -0.00082767 | 725.7083 | 0.12095 | -0.020692 | 0.87905 | FALSE | C
242 | 63000 | 32 | 2023-01 | 2025-12 | FULL_OUTAGE | 131.4675 | 28 | 46 | RT 52 Walden Solar 1, LLC Hybrid | NY | NYIS | AES Distributed Energy | 4 | 8.8 | 2.2 | 1.5-2.5h | 2020 | LIB | CT | TRUE | rte_gt_1,pv_same_plant | 0.73823 | -2.13e-05 | 303.75 | 0.050625 | -0.00053251 | 0.94937 | FALSE | C
243 | 64601 | 4 | 2024-03 | 2024-06 | FULL_OUTAGE | 45 | 4 | 45 | County of San Diego COC Hybrid | CA | CISO | Solar Star California LXXVIII, LLC | 0.4 | 1 | 2.5 | 2.5-4.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.87494 | -0.0037306 | 688.5 | 0.11475 | -0.93265 | 0.88525 | FALSE | C
244 | 65382 | 4 | 2025-09 | 2025-12 | PARTIAL_AVAILABILITY | 43.5 | 4 | 43.5 | Lincoln WWTF Hybrid | CA | CISO | Lincoln Solar Star, LLC | 1 | 2 | 2 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.79206 | 0.0009945 | 217 | 0.036167 | 0.09945 | 0.96383 | FALSE | C
245 | 645 | 20 | 2023-10 | 2025-12 | FULL_OUTAGE | 168.5 | 15 | 43 | Big Bend | FL | TEC | Tampa Electric Co | 12.6 | 25.2 | 2 | 1.5-2.5h | 2017 | LIB | CS | TRUE | pv_same_plant | 0.90825 | 0.0074176 | 25.9127 | 0.0043188 | 0.05887 | 0.99568 | FALSE | C
246 | 63064 | 2 | 2024-10 | 2024-11 | FULL_OUTAGE | 43 | 2 | 43 | Asheville-Rock Hill Battery | NC | CPLW | Duke Energy Progress - (NC) | 8.8 | 8.8 | 1 | <1.5h | 2020 | LIB | CS | FALSE |  | 0.86318 | 0.018088 | 216.9318 | 0.036155 | 0.20554 | 0.96384 | FALSE | B
247 | 64759 | 4 | 2024-07 | 2025-04 | PARTIAL_AVAILABILITY | 42.5 | 2 | 42.5 | Old Middleboro Road Solar | MA | ISNE | Agilitas Energy, Inc. | 4.5 | 13.4 | 2.9778 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.89665 | -0.002003 | 257.3881 | 0.042898 | -0.044511 | 0.9571 | FALSE | C
248 | 57584 | 60 | 2019-01 | 2025-07 | LOW_ETA_AND_LOW_UTI | 259.365 | 30 | 39.5483 | University of California San Diego Hybri | CA | CISO | University of California San Diego | 2.5 | 5 | 2 | 1.5-2.5h | 2015 | LIB | CS | FALSE |  | 0.84818 | -0.00030282 | 3020.4 | 0.5034 | -0.012113 | 0.4966 | FALSE | A
249 | 63341 | 3 | 2024-04 | 2024-06 | FULL_OUTAGE | 39 | 3 | 39 | Owlville Creek Solar, LLC | NY | NYIS | Owlville Creek Solar, LLC | 3 | 12.8 | 4.2667 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.90149 | -9.1441e-05 | 145.3906 | 0.024232 | -0.003048 | 0.97577 | FALSE | C
250 | 62441 | 2 | 2024-09 | 2024-10 | PARTIAL_AVAILABILITY | 38.5 | 2 | 38.5 | Kearny Mesa Storage LLC | CA | CISO | Kearny Mesa Storage LLC | 1 | 1 | 1 | <1.5h | 2020 | LIB | CS | TRUE | colocated_firming | 0.93928 | 0.0013094 | 1871 | 0.31183 | 0.13094 | 0.68817 | FALSE | C
251 | 61923 | 21 | 2023-01 | 2025-02 | LOW_ETA_AND_LOW_UTI | 144.4117 | 12 | 38.3512 | ACUA | NJ | PJM | Viridity Energy Solutions, Inc. | 1 | 1 | 1 | <1.5h | 2018 | LIB | CS | FALSE |  | 0.79686 | 0.0030477 | 10229.4167 | 1.7049 | 0.30477 | 0 | FALSE | A
252 | 62373 | 84 | 2019-01 | 2025-12 | THERMAL_AUX | 134.1312 | 84 | 38.3457 | I25 Battery Storage | CO | WACM | United Power, Inc | 4 | 16 | 4 | 2.5-4.5h | 2018 | LIB | CS | FALSE |  | 0.84071 | 0.010407 | 2899.7188 | 0.48329 | 0.26018 | 0.51671 | FALSE | A
253 | 65098 | 15 | 2024-10 | 2025-12 | LOW_ETA_AND_LOW_UTI | 38.1524 | 15 | 38.1524 | South Sioux City Energy Storage | NE | SWPP | DG Nebraska Energy Storage, LLC | 1.5 | 3 | 2 | 1.5-2.5h | 2020 | LIB | CS | FALSE |  | 0.78582 | -3.3491e-05 | 533.75 | 0.088958 | -0.0022327 | 0.91104 | FALSE | A
254 | 63510 | 13 | 2023-10 | 2025-12 | FULL_OUTAGE | 74.5 | 6 | 36.5 | Walnut Unified School District Walnut HS | CA | CISO | Tesla Inc. | 0.5 | 0.5 | 1 | <1.5h | 2020 | LIB | CS | TRUE | pv_same_plant | 0.95797 | 0.0011682 | 1130 | 0.18833 | 0.23364 | 0.81167 | FALSE | C
255 | 66222 | 34 | 2023-01 | 2025-12 | FULL_OUTAGE | 156 | 30 | 36 | Landau II Solar (Hybrid) | NY | NYIS | Generate Capital | 4 | 8 | 2 | 1.5-2.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.85568 | -0.0010354 | 114.9015 | 0.01915 | -0.025886 | 0.98085 | FALSE | C
256 | 64090 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 35.5 | 12 | 35.5 | NYS Rte 12 Community Solar | NY | NYIS | OYA NYS Rte 12 LLC | 5 | 15 | 3 | 2.5-4.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_tight |  |  | 13.4667 | 0.0022444 |  | 0.99776 | FALSE | C
257 | 61995 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 35.5 | 36 | 35.5 | UC Merced Solar Hybrid | CA | CISO | MN8 Energy LLC | 0.5 | 0.9 | 1.8 | 1.5-2.5h | 2018 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.8232 | 0.005576 | 774.7222 | 0.12912 | 1.1152 | 0.87088 | FALSE | C
258 | 64170 | 3 | 2024-09 | 2024-11 | PARTIAL_AVAILABILITY | 34.5 | 3 | 34.5 | BWC Muddy Brook, LLC Hybrid | MA | ISNE | AES Distributed Energy | 0.9 | 1.8 | 2 | 1.5-2.5h | 2021 | LIB | CT | TRUE | pv_same_plant,dc_tight | 0.88556 | 9.0235e-05 | 458.8889 | 0.076481 | 0.010026 | 0.92352 | FALSE | C
259 | 64763 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 32.7134 | 24 | 32.7134 | Rumford ESS | ME | ISNE | Agilitas Energy, Inc. | 4.9 | 10 | 2.0408 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.59848 | -0.0055185 | 128.1333 | 0.021356 | -0.11262 | 0.97864 | FALSE | A
260 | 61901 | 25 | 2023-12 | 2025-12 | FULL_OUTAGE | 87.5 | 25 | 32.5 | Redstone Arsenal Hybrid | AL | TVA | MN8 Energy LLC | 1 | 2 | 2 | 1.5-2.5h | 2017 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.8678 | 0.0012579 | 967.375 | 0.16123 | 0.12579 | 0.83877 | FALSE | C
261 | 63728 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 30 | 2 | 30 | Taos Mesa Energy Facility Hybrid | NM | PNM | Taos Mesa Energy Facility, LLC | 12.5 | 25 | 2 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.86069 | 0.01259 | 863.56 | 0.14393 | 0.10072 | 0.85607 | FALSE | C
262 | 64876 | 4 | 2023-08 | 2025-10 | PARTIAL_AVAILABILITY | 33 | 2 | 30 | 0 Hammond St CSG | MA | ISNE | 0HAM WHAM8 Solar, LLC | 5 | 4.9 | 0.98 | <1.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.91732 | 0.0076463 | 1370.2041 | 0.22837 | 0.15293 | 0.77163 | FALSE | C
263 | 67743 | 9 | 2024-11 | 2025-07 | FULL_OUTAGE | 29.5 | 9 | 29.5 | Bishop Ranch BR 1-X | CA | CISO | Bollinger Canyon Road BR 1-X Solar Project 2020 | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.97328 | 0.0034743 | 356.5152 | 0.059419 | 0.69486 | 0.94058 | FALSE | C
264 | 66076 | 2 | 2024-11 | 2024-12 | PARTIAL_AVAILABILITY | 29.5 | 2 | 29.5 | Electric Avenue Lunenburg Solar 1 | MA | ISNE | Electric Avenue Lunenburg Solar 1, LLC | 1 | 1 | 1 | <1.5h | 2022 | LIB | CT | TRUE | pv_same_plant,dc_coupled | 0.9461 | 0.0016839 | 1540 | 0.25667 | 0.16839 | 0.74333 | FALSE | C
265 | 66799 | 14 | 2024-11 | 2025-12 | FULL_OUTAGE | 29 | 14 | 29 | Bishop Ranch - BR 1-Y | CA | CISO | Distributed Solar Development, LLC | 0.7 | 1.3 | 1.8571 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.92678 | 0.0012322 | 68.4615 | 0.01141 | 0.17602 | 0.98859 | FALSE | C
266 | 62683 | 59 | 2019-11 | 2025-12 | LOW_ETA_AND_LOW_UTI | 28.5 | 29 | 28.5 | Westside Wastewater Treatment Plant Hybr | AR | SWPP | Today's Power, Inc. | 6 | 13.1 | 2.1833 | 1.5-2.5h | 2019 | LIB | BL | TRUE | rte_gt_1,pv_same_plant | 0.69519 | 0.0022993 | 158.855 | 0.026476 | 0.038321 | 0.97352 | FALSE | C
267 | 64213 | 4 | 2023-10 | 2024-07 | FULL_OUTAGE | 103.5 | 2 | 28 | Auburn Solar Project | MA | ISNE | Agilitas Energy, Inc. | 3.8 | 9.4 | 2.4737 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.8986 | 0.0025503 | 240.7447 | 0.040124 | 0.067113 | 0.95988 | FALSE | C
268 | 58236 | 27 | 2023-08 | 2025-12 | FULL_OUTAGE | 41.5 | 25 | 28 | Marshalltown Generating Station | IA | MISO | Interstate Power and Light Co | 0.3 | 0.6 | 2 | 1.5-2.5h | 2020 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.89339 | -0.00011521 | 651.6667 | 0.10861 | -0.038402 | 0.89139 | FALSE | C
269 | 63339 | 5 | 2024-12 | 2025-05 | FULL_OUTAGE | 27.5 | 3 | 27.5 | Hales Mills Solar, LLC | NY | NYIS | Hales Mills Solar, LLC | 3 | 12.8 | 4.2667 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.91669 | 0.00067064 | 23.9062 | 0.0039844 | 0.022355 | 0.99602 | FALSE | C
270 | 64425 | 3 | 2025-08 | 2025-10 | FULL_OUTAGE | 27.5 | 3 | 27.5 | TX2 Port Lavaca | TX | ERCO | Key Capture Energy | 9.9 | 11.9 | 1.202 | <1.5h | 2020 | LIB | CS | FALSE |  |  |  | 65.5882 | 0.010931 |  | 0.98907 | FALSE | B
271 | 63186 | 24 | 2023-01 | 2025-12 | FULL_OUTAGE | 229.912 | 12 | 25 | Imeson Solar | FL | JEA | Imeson Solar Farm LLC | 5 | 3.8 | 0.76 | <1.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.98801 | 0.0013046 | 522.8947 | 0.087149 | 0.026091 | 0.91285 | FALSE | C
272 | 64731 | 6 | 2024-03 | 2024-12 | FULL_OUTAGE | 24 | 4 | 24 | Maple(CSG) | MA | ISNE | Maple Street Solar 1, LLC | 2.3 | 4.8 | 2.087 | 1.5-2.5h | 2021 | OTH | CS | TRUE | pv_same_plant | 0.44174 | -0.0013654 | 42.9167 | 0.0071528 | -0.059366 | 0.99285 | FALSE | C
273 | 64432 | 24 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 23.2325 | 8 | 23 | Breckenridge Solar | MA | ISNE | Breckenridge Street Solar 1, LLC | 2.2 | 4.7 | 2.1364 | 1.5-2.5h | 2020 | LIB | CS | TRUE | pv_same_plant | 0.85091 | 0.0040385 | 283.4043 | 0.047234 | 0.18357 | 0.95277 | FALSE | C
274 | 65469 | 2 | 2024-04 | 2024-05 | PARTIAL_AVAILABILITY | 20.5 | 2 | 20.5 | Sealed Air Madera Solar Project | CA | CISO | Sealed Air Corporation | 0.8 | 3.1 | 3.875 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 1.1201 | 0.015675 | 589.0323 | 0.098172 | 1.9594 | 0.90183 | FALSE | C
275 | 64877 | 5 | 2022-10 | 2025-07 | PARTIAL_AVAILABILITY | 94.5 | 3 | 20.5 | Edwards Sanborn E3 | CA | CISO | Terra-Gen Operating Co-Hybrid | 11 | 31.5 | 2.8636 | 2.5-4.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.88596 | 0.068176 | 976.5714 | 0.16276 | 0.61978 | 0.83724 | FALSE | C
276 | 64508 | 35 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 17.5 | 27 | 17.5 | Hall Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 2.5 | 5 | 2 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.76372 | 0.0060685 | 163 | 0.027167 | 0.24274 | 0.97283 | FALSE | C
277 | 60609 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 24.68 | 36 | 14.5 | CMEEC - Norwich Stott St Solar Hybrid | CT | ISNE | Tesla Inc. | 0.8 | 3 | 3.75 | 2.5-4.5h | 2016 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.7044 | -0.00036458 | 94 | 0.015667 | -0.045572 | 0.98433 | FALSE | C
278 | 67187 | 3 | 2025-10 | 2025-12 | PARTIAL_AVAILABILITY | 14 | 3 | 14 | Paxton BESS 1 | MA | ISNE | Paxton BESS 1 LLC | 3 | 8.9 | 2.9667 | 2.5-4.5h | 2024 | LIB | CS | FALSE |  | 0.90261 | 0.016254 | 295.9551 | 0.049326 | 0.5418 | 0.95067 | FALSE | A
279 | 62978 | 10 | 2023-01 | 2024-07 | LOW_ETA_AND_LOW_UTI | 78 | 4 | 13.5 | Syncarpha Northbridge II Hybrid CSG | MA | ISNE | Syncarpha Northbridge II, LLC | 3 | 6 | 2 | 1.5-2.5h | 2021 | LIB | CT | TRUE | pv_same_plant | 0.83908 | 0.00012412 | 471.6667 | 0.078611 | 0.0041375 | 0.92139 | FALSE | C
280 | 60562 | 4 | 2023-08 | 2025-02 | PARTIAL_AVAILABILITY | 55 | 2 | 13 | GMP Solar - Panton Hybrid | VT | ISNE | Green Mountain Power Corp | 1 | 4 | 4 | 2.5-4.5h | 2018 | LIB | OT | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 1.6267 | 0.02326 | 1886.4167 | 0.3144 | 2.326 | 0.6856 | FALSE | C
281 | 68266 | 20 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 12 | 9 | 12 | North Juvenile Detention Center Solar | CA | CISO | SoCore Energy LLC | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2019 | LIB | CS | TRUE | pv_same_plant | 0.79297 | 0.00073143 | 570.3333 | 0.095056 | 0.24381 | 0.90494 | FALSE | C
282 | 62652 | 2 | 2025-06 | 2025-07 | PARTIAL_AVAILABILITY | 11.5 | 2 | 11.5 | Happy Hollow CSG Hybrid | MA | ISNE | REA Investments, LLC | 3.3 | 6.6 | 2 | 1.5-2.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.92772 | 0.015025 | 390.4545 | 0.065076 | 0.45531 | 0.93492 | FALSE | C
283 | 66966 | 24 | 2024-01 | 2025-12 | THERMAL_AUX | 10.5 | 24 | 10.5 | Acton-Boxborough Schools BESS | MA | ISNE | MSS Energy Holdings, LLC (d.b.a. Calibrant Energy) | 2.1 | 4.3 | 2.0476 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  | 0.85079 | 0.0037599 | 527.9845 | 0.087997 | 0.17904 | 0.912 | FALSE | A
284 | 67948 | 19 | 2024-03 | 2025-12 | THERMAL_AUX | 10.2147 | 10 | 10.2147 | Hampton Substation Energy Storage | IA | SWPP | Corn Belt Power Coop | 1.8 | 9.1 | 5.0556 | >4.5h | 2022 | LIB | CS | FALSE |  | 0.91104 | 0.00019053 | 138.7729 | 0.023129 | 0.010585 | 0.97687 | FALSE | A
285 | 66505 | 7 | 2024-10 | 2025-11 | LOW_ETA_AND_LOW_UTI | 8.7006 | 5 | 8.7006 | EnerSmart Chula Vista Sub Station | CA | CISO | EnerSmart Chula Vista Sub Station | 6 | 12 | 2 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.81776 | 0.0031409 | 220.0833 | 0.036681 | 0.052348 | 0.96332 | FALSE | A
286 | 64764 | 3 | 2024-02 | 2024-04 | LOW_ETA_AND_LOW_UTI | 8.3163 | 3 | 8.3163 | Madison BTM | ME | ISNE | Agilitas Energy, Inc. | 1.5 | 3.1 | 2.0667 | 1.5-2.5h | 2020 | LIB | CS | FALSE |  | 0.6542 | -0.00080733 | 303.871 | 0.050645 | -0.053822 | 0.94935 | FALSE | A
287 | 66232 | 25 | 2023-10 | 2025-12 | FULL_OUTAGE | 194 | 21 | 8 | Svenski Solar (Hybrid) | NY | NYIS | Generate Capital | 2 | 4 | 2 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_tight | 0.91985 | 0.00053422 | 195.2045 | 0.032534 | 0.026711 | 0.96747 | FALSE | C
288 | 65568 | 4 | 2023-10 | 2024-01 | PARTIAL_AVAILABILITY | 27 | 4 | 8 | Google Moffett Park Solar Project | CA | CISO | Google, Inc. | 0.6 | 1.1 | 1.8333 | 1.5-2.5h | 2021 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.89537 | 0.00017763 | 992.7273 | 0.16545 | 0.029605 | 0.83455 | FALSE | C
289 | 64522 | 31 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 7.5 | 17 | 7.5 | Old Cedar Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 1.3 | 2 | 1.5385 | 1.5-2.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.83516 | 0.003318 | 252.5 | 0.042083 | 0.25523 | 0.95792 | FALSE | C
290 | 62976 | 14 | 2023-01 | 2025-09 | FULL_OUTAGE | 175.7185 | 12 | 7 | Syncarpha Northampton Hybrid CSG | MA | ISNE | Syncarpha Northampton, LLC | 2 | 4 | 2 | 1.5-2.5h | 2020 | LIB | CT | TRUE | pv_same_plant | 0.94786 | 0.0073688 | 292.75 | 0.048792 | 0.36844 | 0.95121 | FALSE | C
291 | 6304 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 6 | 36 | 6 | Kotzebue Hybrid | AK |  | Kotzebue Electric Assn Inc | 1.2 | 1 | 0.83333 | <1.5h | 2015 | LIB | CT | TRUE | colocated_firming,pv_same_plant | 0.72944 | -0.00049887 | 480.5833 | 0.080097 | -0.041573 | 0.9199 | FALSE | C
292 | 63422 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 6 | 36 | 6 | Fresno Sunnyside High School Hybrid | CA | CISO | Forefront Power, LLC | 0.3 | 0.3 | 1 | <1.5h | 2020 | LIB | CS | TRUE | pv_same_plant | 0.7655 | -0.0011916 | 596.6667 | 0.099444 | -0.39721 | 0.90056 | FALSE | C
293 | 69128 | 2 | 2025-06 | 2025-07 | PARTIAL_AVAILABILITY | 6 | 2 | 6 | Chesapeake Beach BESS | MD | PJM | Chesapeake Beach BESS LLC | 1.1 | 2.3 | 2.0909 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.86819 | 0.0057582 | 773.4783 | 0.12891 | 0.52348 | 0.87109 | FALSE | B
294 | 63421 | 2 | 2024-01 | 2024-02 | FULL_OUTAGE | 6 | 2 | 6 | Fresno Hoover High School Hybrid | CA | CISO | Forefront Power, LLC | 0.2 | 0.2 | 1 | <1.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 1.2561 | 0.00051157 | 940 | 0.15667 | 0.25578 | 0.84333 | FALSE | C
295 | 60906 | 12 | 2023-01 | 2024-02 | LOW_ETA_AND_LOW_UTI | 5.5 | 8 | 5.5 | Mt. Tom Solar Project Hybrid | MA | ISNE | Mt. Tom Solar, LLC | 3.1 | 6.1 | 1.9677 | 1.5-2.5h | 2019 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.85148 | 0.01608 | 334.5902 | 0.055765 | 0.5187 | 0.94423 | FALSE | C
296 | 66648 | 7 | 2025-03 | 2025-09 | LOW_ETA_AND_LOW_UTI | 5.0909 | 7 | 5.0909 | Blackwell?s Corner Storage Facility | CA | CISO | Blackwell Test Facility, LLC | 2 | 9 | 4.5 | >4.5h | 2025 | LIB | CS | FALSE |  | 0.78002 | -0.00035205 | 59.4444 | 0.0099074 | -0.017603 | 0.99009 | FALSE | A
297 | 67296 | 29 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 4.5 | 13 | 4.5 | CVEC Round 4 Brewster Captn Golf Course | MA | ISNE | Freemans Way Solar Project 2019, LLC | 0.4 | 0.9 | 2.25 | 1.5-2.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.85246 | 0.00016045 | 160 | 0.026667 | 0.040113 | 0.97333 | FALSE | C
298 | 65029 | 18 | 2024-01 | 2025-12 | FULL_OUTAGE | 4.5 | 8 | 4.5 | Bissell Solar and Battery Generator | MI | MISO | Consumers Energy Co - (MI) | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2021 | LIB | BL | TRUE | rte_gt_1,colocated_firming,pv_same_plant | 0.8708 | 0.0012043 | 234 | 0.039 | 0.40144 | 0.961 | FALSE | C
299 | 64514 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 4.5 | 36 | 4.5 | Ludie Brown Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 2.5 | 2.5 | 1 | <1.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.77384 | 0.0070566 | 1656.8 | 0.27613 | 0.28226 | 0.72387 | FALSE | C
300 | 67282 | 7 | 2025-01 | 2025-07 | FULL_OUTAGE | 4 | 7 | 4 | FFP - NY Varano | NY | NYIS | FFP NY Goshen Project2, LLC | 5 | 10.5 | 2.1 | 1.5-2.5h | 2024 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled |  |  | 24.6667 | 0.0041111 |  | 0.99589 | FALSE | C
301 | 69344 | 2 | 2025-09 | 2025-10 | FULL_OUTAGE | 4 | 2 | 4 | Regis Hearn | TX | ERCO | Regis Hearn LLC | 9.9 | 9.9 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  |  |  | 31.1953 | 0.0051992 |  | 0.9948 | FALSE | B
302 | 66075 | 2 | 2025-06 | 2025-07 | PARTIAL_AVAILABILITY | 4 | 2 | 4 | Blacksmith Road Solar 1 | MA | ISNE | Blacksmith Road Solar 1, LLC | 2 | 3.3 | 1.65 | 1.5-2.5h | 2021 | LIB | CT | TRUE | colocated_firming,pv_same_plant | 0.91492 | 0.0010539 | 1004.2424 | 0.16737 | 0.052694 | 0.83263 | FALSE | C
303 | 65650 | 2 | 2025-09 | 2025-10 | PARTIAL_AVAILABILITY | 3.5 | 2 | 3.5 | Brockelman Road Solar 2 | MA | ISNE | Brockelman Road Solar 2, LLC | 2 | 1.7 | 0.85 | <1.5h | 2021 | LIB | CT | TRUE | colocated_firming,pv_same_plant,dc_coupled | 0.92922 | 0.0010771 | 457.6471 | 0.076275 | 0.053857 | 0.92373 | FALSE | C
304 | 65409 | 4 | 2023-01 | 2025-02 | LOW_ETA_AND_LOW_UTI | 3.5 | 2 | 3.5 | Gilead Foster City Solar Project | CA | CISO | Gilead Sciences Inc. Foster City | 0.5 | 0.9 | 1.8 | 1.5-2.5h | 2021 | LIB | CT | TRUE | rte_gt_1,pv_same_plant | 0.81278 | -0.0025527 | 866.6667 | 0.14444 | -0.51053 | 0.85556 | FALSE | C
305 | 69210 | 2 | 2025-10 | 2025-11 | PARTIAL_AVAILABILITY | 3 | 2 | 3 | Salem Henningsen | OR | PGE | Lineage Logistics Solar PV - Salem OR | 1 | 2 | 2 | 1.5-2.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 1 | 4.9103e-18 | 63.3333 | 0.010556 | 4.9103e-16 | 0.98944 | FALSE | C
306 | 64513 | 32 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 3 | 27 | 3 | Wake RJ3 Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 0.6 | 1.1 | 1.8333 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.69068 | 0.00020504 | 96.3636 | 0.016061 | 0.034174 | 0.98394 | FALSE | C
307 | 58585 | 33 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 9.5645 | 27 | 3 | Sierra Nevada Brewing Co Hybrid | CA | CISO | Sierra Nevada Brewing Co | 0.5 | 1 | 2 | 1.5-2.5h | 2017 | LIB | CS | TRUE | pv_same_plant | 0.80218 | 0.00035967 | 919.6667 | 0.15328 | 0.071934 | 0.84672 | FALSE | C
308 | 67275 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 5.5 | 36 | 2.5 | White Plains_RFP-Gedney Way Landfill | NY | NYIS | Distributed Solar Development, LLC | 1.3 | 5.1 | 3.9231 | 2.5-4.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.76887 | -0.0002753 | 66.5196 | 0.011087 | -0.021177 | 0.98891 | FALSE | C
309 | 60567 | 26 | 2023-03 | 2025-12 | FULL_OUTAGE | 6.897 | 24 | 2 | Ortega Highway Energy Storage | CA | CISO | SDGE Batteries | 2 | 6 | 3 | 2.5-4.5h | 2015 | LIB | CS | TRUE | rte_gt_1 |  |  | 17.1111 | 0.0028519 |  | 0.99715 | FALSE | C
310 | 65015 | 2 | 2024-08 | 2024-09 | PARTIAL_AVAILABILITY | 2 | 2 | 2 | ASD Wallum MA Solar LLC(CSG) | MA | ISNE | ASD Wallum MA Solar LLC | 3.8 | 12.8 | 3.3684 | 2.5-4.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled | 1.0065 | 0.0083307 | 330.5469 | 0.055091 | 0.21923 | 0.94491 | FALSE | C
311 | 60568 | 25 | 2023-04 | 2025-12 | FULL_OUTAGE | 9.6465 | 19 | 2 | Canyon Crest Academy | CA | CISO | SDGE Batteries | 1 | 3 | 3 | 2.5-4.5h | 2014 | LIB | CS | TRUE | rte_gt_1 |  |  | 464.8333 | 0.077472 |  | 0.92253 | FALSE | C
312 | 67122 | 14 | 2024-02 | 2025-04 | LOW_ETA_AND_LOW_UTI | 1.5769 | 11 | 1.5769 | BRIGHT Battery | NE | SWPP | Omaha Public Power District | 1 | 2.4 | 2.4 | 1.5-2.5h | 2023 | LIB | CS | FALSE |  | 0.81408 | -0.0024064 | 433.3333 | 0.072222 | -0.24064 | 0.92778 | FALSE | A
313 | 67281 | 4 | 2025-02 | 2025-05 | FULL_OUTAGE | 1.5 | 4 | 1.5 | FFP - NY Urbanski | NY | NYIS | FFP NY Goshen Project1, LLC | 4 | 10.5 | 2.625 | 2.5-4.5h | 2024 | LIB | CS | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled |  |  | 7.4286 | 0.0012381 |  | 0.99876 | FALSE | C
314 | 61730 | 3 | 2025-09 | 2025-11 | PARTIAL_AVAILABILITY | 0.5 | 3 | 0.5 | MA Solar Storage 1 Hybrid | MA | ISNE | Origis Energy USA, Inc | 1 | 2 | 2 | 1.5-2.5h | 2018 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.93197 | -0.00018915 | 1055.125 | 0.17585 | -0.018915 | 0.82415 | FALSE | C
315 | 61722 | 12 | 2024-01 | 2024-12 | LOW_ETA_AND_LOW_UTI | 0.25424 | 12 | 0.25424 | HEBT Irvine 1 | CA | CISO | Electrodes | 5.5 | 33.5 | 6.0909 | >4.5h | 2018 | LIB | CS | FALSE |  | 0.856 | -0.0014965 | 1266.8856 | 0.21115 | -0.027209 | 0.78885 | FALSE | A
316 | 66023 | 9 | 2025-04 | 2025-12 | FULL_OUTAGE | 0 | 9 | 0 | Grossmont-Cuyamaca-Cuyamaca Col. Solar & | CA | CISO | Forefront Power, LLC | 1 | 1 | 1 | <1.5h | 2024 | LIB | CS | TRUE | colocated_firming,pv_same_plant |  |  | 0 | 0 |  | 1 | FALSE | C
317 | 66717 | 21 | 2024-04 | 2025-12 | FULL_OUTAGE | 0 | 21 | 0 | Eastover Solar | SC | CPLE | Eastover Solar, LLC | 18 | 72 | 4 | 2.5-4.5h | 2023 | OTH | CS | TRUE | pv_same_plant,dc_coupled |  |  | 0 | 0 |  | 1 | FALSE | C
318 | 68523 | 5 | 2025-08 | 2025-12 | FULL_OUTAGE | 0 | 5 | 0 | Bishop Ranch - BR 8-Q | CA | CISO | Executive Parkway BR8-Q Solar Project 2020 LLC | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 | LIB | CS | TRUE | pv_same_plant |  |  | 0 | 0 |  | 1 | FALSE | C
319 | 68525 | 5 | 2025-08 | 2025-12 | FULL_OUTAGE | 0 | 5 | 0 | Bishop Ranch - BR 15-CC | CA | CISO | Alcosta Boulevard BR 15-CC Solar Project 2020, LLC | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 | LIB | CS | TRUE | pv_same_plant |  |  | 0 | 0 |  | 1 | FALSE | C
320 | 64453 | 32 | 2023-05 | 2025-12 | FULL_OUTAGE | 0 | 32 | 0 | Volney II | NY | NYIS | DG New York CS, LLC | 3 | 12 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_tight |  |  | 0.33333 | 5.5556e-05 |  | 0.99994 | FALSE | C
321 | 61739 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 0 | 36 | 0 | Lockheed Martin RMS Syracuse | NY | NYIS | Lockheed Martin RMS Syracuse | 1 | 1.3 | 1.3 | <1.5h | 2017 | LIB | CS | FALSE |  |  |  | 0.76923 | 0.00012821 |  | 0.99987 | FALSE | B
322 | 68522 | 2 | 2025-09 | 2025-10 | FULL_OUTAGE | 0 | 2 | 0 | Bishop Ranch - BR 8-O | CA | CISO | Executive Parkway BR8-O Solar Project 2020 LLC | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2025 | LIB | CS | TRUE | pv_same_plant |  |  | 0.90909 | 0.00015152 |  | 0.99985 | FALSE | C
323 | 66474 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 31.8825 | 36 | 0 | MA Blackstone | MA | ISNE | Catalyze Blackstone 83 Federal Street Microgrid, LLC | 3 | 6.4 | 2.1333 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled |  |  | 8.5938 | 0.0014323 |  | 0.99857 | FALSE | C
324 | 63775 | 34 | 2023-02 | 2025-12 | FULL_OUTAGE | 0 | 23 | 0 | Tech Square Microgrid | GA | SOCO | Georgia Power Co | 0.2 | 0.4 | 2 | 1.5-2.5h | 2020 | LIB | BL | FALSE |  |  |  | 10 | 0.0016667 |  | 0.99833 | FALSE | B
325 | 64050 | 2 | 2025-06 | 2025-07 | FULL_OUTAGE | 0 | 2 | 0 | Fort Bragg - Camp Mackall PV BESS System | NC | CPLE | Ameresco Federal Solutions | 2 | 2 | 1 | <1.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_coupled |  |  | 13.5 | 0.00225 |  | 0.99775 | FALSE | C
326 | 60249 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 0 | 36 | 0 | Silicon Valley Clean Water | CA | CISO | Silicon Valley Clean Water | 1 | 2 | 2 | 1.5-2.5h | 2020 | LIB | CS | FALSE |  |  |  | 16.5 | 0.00275 |  | 0.99725 | FALSE | B
327 | 65815 | 2 | 2024-06 | 2024-07 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | NY - Mines Press | NY | NYIS | NY - Mines Press | 1 | 2.1 | 2.1 | 1.5-2.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled |  |  | 29.0476 | 0.0048413 |  | 0.99516 | FALSE | C
328 | 67745 | 2 | 2025-06 | 2025-07 | FULL_OUTAGE | 0 | 2 | 0 | White Plains RFP Shapham Place | NY | NYIS | Shapham Place Solar Project 2020 LLC | 5 | 2 | 0.4 | <1.5h | 2022 | LIB | CS | TRUE | colocated_firming,pv_same_plant |  |  | 40.5 | 0.00675 |  | 0.99325 | FALSE | C
329 | 61795 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 24 | 0 | Pacific Union College BESS | CA | CISO | ENGIE Storage Services NA LLC | 1 | 2 | 2 | 1.5-2.5h | 2020 | LIB | CS | TRUE | rte_gt_1 | 0.5901 | 0.001929 | 55.5 | 0.00925 | 0.1929 | 0.99075 | FALSE | C
330 | 65154 | 9 | 2025-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 4 | 0 | UMass PV Lot 22 | MA | ISNE | RWE Clean Energy | 2 | 4.3 | 2.15 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.77745 | 0.0058351 | 55.5814 | 0.0092636 | 0.29175 | 0.99074 | FALSE | C
331 | 61990 | 14 | 2024-01 | 2025-09 | FULL_OUTAGE | 0 | 12 | 0 | TAC-Distributed Energy Resource Hybrid | IL | MISO | Ameren Illinois | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2017 | LIB | CT | TRUE | pv_same_plant |  |  | 74.6667 | 0.012444 |  | 0.98756 | FALSE | C
332 | 60491 | 54 | 2021-07 | 2025-12 | FULL_OUTAGE | 13.5 | 54 | 0 | Springbok 3 Solar Farm Hybrid | CA | LDWP | 64KT 8me LLC | 1.5 | 1.5 | 1 | <1.5h | 2019 | LIB | CT | TRUE | pv_same_plant,dc_coupled | 0.8607 | -0.00015117 | 78 | 0.013 | -0.010078 | 0.987 | FALSE | C
333 | 68147 | 13 | 2024-12 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 13 | 0 | Coffeen Solar BESS | IL | MISO | Vistra Corp | 2 | 8 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.67817 | 6.9958e-05 | 82.125 | 0.013688 | 0.0034979 | 0.98631 | FALSE | C
334 | 65441 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 4 | 36 | 0 | USS Itasca Clean Energy Solar LLC | MN | MISO | United States Solar Corporation | 1 | 3 | 3 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.7807 | 0.0020507 | 86.3333 | 0.014389 | 0.20507 | 0.98561 | FALSE | C
335 | 63415 | 32 | 2023-05 | 2025-12 | FULL_OUTAGE | 141 | 32 | 0 | Middletown Solar 1, LLC Hybrid CSG | NY | NYIS | AES Distributed Energy | 1.6 | 6.6 | 4.125 | 2.5-4.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight |  |  | 90 | 0.015 |  | 0.985 | FALSE | C
336 | 66764 | 22 | 2024-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 15 | 0 | SCH - (2A) 156 Barhydt Rd Glenville | NY | NYIS | Distributed Solar Development, LLC | 2.5 | 10 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled | 0.7374 | -0.00097707 | 92.4 | 0.0154 | -0.039083 | 0.9846 | FALSE | C
337 | 68816 | 20 | 2024-05 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 20 | 0 | Google Bayhill Solar PV and Microgrid | CA | CISO | Google, Inc. | 2.6 | 5.3 | 2.0385 | 1.5-2.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.67247 | 0.00017174 | 93.2075 | 0.015535 | 0.0066054 | 0.98447 | FALSE | C
338 | 62839 | 25 | 2023-05 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 12 | 0 | 98th Street Battery Storage Station | NY | NYIS | Consolidated Edison Co-NY Inc | 2 | 10 | 5 | >4.5h | 2021 | LIB | CS | TRUE | rte_gt_1 | 0.78195 | 0.0095459 | 93.5667 | 0.015594 | 0.4773 | 0.98441 | FALSE | C
339 | 59256 | 31 | 2019-01 | 2021-07 | LOW_ETA_AND_LOW_UTI | 1746.1275 | 31 | 0 | Vaca Dixon Battery Storage System | CA | CISO | Pacific Gas & Electric Co. | 2 | 14 | 7 | >4.5h | 2013 | NAB | CS | FALSE |  | 0.77365 | 0.067801 | 94.6429 | 0.015774 | 3.39 | 0.98423 | FALSE | A
340 | 62754 | 12 | 2024-07 | 2025-07 | FULL_OUTAGE | 0 | 7 | 0 | San Diego International Airport BESS | CA | CISO | Critical Loop, Inc. | 2 | 4 | 2 | 1.5-2.5h | 2021 | LIB | CS | FALSE |  |  |  | 97.7292 | 0.016288 |  | 0.98371 | FALSE | B
341 | 64509 | 33 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 2 | 24 | 0 | South River H4 Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 0.6 | 1.1 | 1.8333 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.73349 | -2.0245e-05 | 107.2727 | 0.017879 | -0.0033741 | 0.98212 | FALSE | C
342 | 62937 | 61 | 2019-06 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 50 | 0 | Athens BESS | MN | MISO | Gopher Energy Storage, LLC | 6 | 12 | 2 | 1.5-2.5h | 2018 | LIB | CS | TRUE | colocated_firming | 0.50827 | 0.0039861 | 111.7986 | 0.018633 | 0.066435 | 0.98137 | FALSE | C
343 | 64512 | 34 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 24 | 0 | Hamlet Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 0.5 | 1.1 | 2.2 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.786 | 0.00075965 | 119.0909 | 0.019848 | 0.15193 | 0.98015 | FALSE | C
344 | 60607 | 35 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 21 | 0 | CMEEC - Polaris Park Solar Hybrid | CT | ISNE | Tesla Inc. | 0.8 | 3.3 | 4.125 | 2.5-4.5h | 2017 | LIB | CS | TRUE | pv_same_plant | 0.81112 | 0.0016292 | 120.303 | 0.020051 | 0.20366 | 0.97995 | FALSE | C
345 | 63090 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Athens - Coopers Corner BESS | MN | MISO | Gopher Energy Storage, LLC | 3 | 6 | 2 | 1.5-2.5h | 2018 | LIB | CS | TRUE | colocated_firming |  |  | 141.3611 | 0.02356 |  | 0.97644 | FALSE | C
346 | 60316 | 24 | 2024-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 24 | 0 | Scott Solar Farm | VA | PJM | Dominion Energy Inc. | 40 | 48 | 1.2 | <1.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.81884 | 0.017842 | 147.1458 | 0.024524 | 0.044606 | 0.97548 | FALSE | C
347 | 60698 | 5 | 2021-12 | 2023-09 | PARTIAL_AVAILABILITY | 59 | 3 | 0 | Stanton Energy Reliability Center Hybrid | CA | CISO | Wellhead Services, Inc | 20 | 9 | 0.45 | <1.5h | 2020 | LIB | CS | TRUE | rte_gt_1 | 0.43863 | -0.00040987 | 150.5556 | 0.025093 | -0.0020493 | 0.97491 | FALSE | C
348 | 62682 | 59 | 2019-11 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 29 | 0 | Noland Wastewater Treatment Plant Hybrid | AR | SWPP | Today's Power, Inc. | 6 | 13.1 | 2.1833 | 1.5-2.5h | 2019 | LIB | BL | TRUE | rte_gt_1,pv_same_plant | 0.64232 | 0.0012491 | 151.2977 | 0.025216 | 0.020818 | 0.97478 | FALSE | C
349 | 64511 | 31 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 24 | 0 | Rose Acre Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 2.5 | 5 | 2 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.85206 | 0.012372 | 157.6 | 0.026267 | 0.49489 | 0.97373 | FALSE | C
350 | 62753 | 6 | 2021-01 | 2023-11 | FULL_OUTAGE | 88 | 4 | 0 | Prospect Storage | TX | ERCO | GlidePath Power Operations LLC | 9.9 | 10 | 1.0101 | <1.5h | 2020 | LIB | CS | TRUE | rte_gt_1 | 1.294 | 0.038063 | 161.1 | 0.02685 | 0.38447 | 0.97315 | FALSE | C
351 | 68548 | 5 | 2025-01 | 2025-05 | FULL_OUTAGE | 0 | 5 | 0 | Tipton 2 - (CA) | CA | CISO | CleanCapital Holdings | 0.7 | 2.9 | 4.1429 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant |  |  | 166.2069 | 0.027701 |  | 0.9723 | FALSE | C
352 | 64719 | 2 | 2023-01 | 2023-02 | FULL_OUTAGE | 38 | 2 | 0 | Glenmere Lake | NY | ISNE | AES Distributed Energy | 2 | 7.5 | 3.75 | 2.5-4.5h | 2021 | LIB | CT | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.91193 | 2.5886e-05 | 167.4667 | 0.027911 | 0.0012943 | 0.97209 | FALSE | C
353 | 64875 | 25 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 8 | 0 | 276 Federal Rd(CSG) | MA | ISNE | 276FED WHAM8 Solar, LLC | 3.3 | 6.9 | 2.0909 | 1.5-2.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.73674 | 0.0050719 | 168.6957 | 0.028116 | 0.1537 | 0.97188 | FALSE | C
354 | 66905 | 2 | 2025-09 | 2025-10 | LOW_ETA_AND_LOW_UTI | 0 | 2 | 0 | Ables Springs Solar & Storage | TX | ERCO | Ables Springs Solar, LLC | 100 | 157.7 | 1.577 | 1.5-2.5h | 2025 | LIB | CS | TRUE | pv_same_plant | 0.76825 | -0.049502 | 173.9759 | 0.028996 | -0.049502 | 0.971 | FALSE | C
355 | 64516 | 35 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 24 | 0 | Lowe Solar Energy Storage | NC | CPLE | North Carolina El Member Corp | 2.5 | 5 | 2 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.80414 | 0.0076733 | 180 | 0.03 | 0.30693 | 0.97 | FALSE | C
356 | 68684 | 2 | 2025-01 | 2025-02 | LOW_ETA_AND_LOW_UTI | 0 | 2 | 0 | Century BESS | TX | ERCO | Prologis Logistics Services Incorporated BESS | 10 | 24.8 | 2.48 | 1.5-2.5h | 2024 | LIB | CS | FALSE |  | 0.82852 | -0.0055303 | 181.9355 | 0.030323 | -0.055303 | 0.96968 | FALSE | B
357 | 66598 | 9 | 2024-10 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 4 | 0 | Baldy Mesa Solar & Storage | CA | CISO | AES Clean Energy | 75 | 300 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.85963 | -0.27831 | 190.2633 | 0.031711 | -0.37107 | 0.96829 | FALSE | C
358 | 65114 | 11 | 2023-05 | 2024-12 | LOW_ETA_AND_LOW_UTI | 0 | 6 | 0 | 196 Tremont St(CSG) | MA | ISNE | 196TRE WHAM8 Solar, LLC | 1.5 | 8 | 5.3333 | >4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.7903 | -9.6719e-05 | 192.375 | 0.032063 | -0.006448 | 0.96794 | FALSE | C
359 | 60014 | 48 | 2022-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 3009.5 | 48 | 0 | Manatee Solar Energy Center | FL | FPL | Florida Power & Light Co | 409 | 900 | 2.2005 | 1.5-2.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.81905 | 1.6858 | 192.9989 | 0.032166 | 0.41217 | 0.96783 | FALSE | C
360 | 67545 | 14 | 2024-11 | 2025-12 | ELEVATED_P_AUX | 0 | 14 | 0 | Marshall Solar Plus LLC | MN | MISO | Western Minnesota Mun Pwr Agny | 5 | 30.6 | 6.12 | >4.5h | 2024 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.97272 | 0.1409 | 196.732 | 0.032789 | 2.8179 | 0.96721 | FALSE | C
361 | 64844 | 4 | 2025-01 | 2025-04 | FULL_OUTAGE | 0 | 4 | 0 | Three Rivers Solar LLC | MA | ISNE | ASD Three Rivers Road MA Solar LLC | 1.4 | 2.8 | 2 | 1.5-2.5h | 2024 | PBB | CS | TRUE | pv_same_plant,dc_coupled |  |  | 201.0714 | 0.033512 |  | 0.96649 | FALSE | C
362 | 63805 | 18 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 7 | 0 | Williamsville Hybrid CSG | MA | ISNE | 147 Williamsville Solar 1, LLC | 3.3 | 6.7 | 2.0303 | 1.5-2.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.83948 | 0.0020053 | 202.9851 | 0.033831 | 0.060767 | 0.96617 | FALSE | C
363 | 65291 | 19 | 2024-06 | 2025-12 | ELEVATED_P_AUX | 0 | 19 | 0 | Golden Triangle II | MS | TVA | Origis Energy USA, Inc | 50 | 200 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.99357 | 0.65242 | 208.23 | 0.034705 | 1.3048 | 0.9653 | FALSE | C
364 | 60974 | 18 | 2023-02 | 2025-12 | FULL_OUTAGE | 30.615 | 4 | 0 | Glendale Battery Energy Storage System | CA | LDWP | City of Glendale - (CA) | 2 | 1 | 0.5 | <1.5h | 2017 | LIB | CS | TRUE | rte_gt_1 |  |  | 216.5 | 0.036083 |  | 0.96392 | FALSE | C
365 | 64446 | 33 | 2023-01 | 2025-09 | LOW_ETA_AND_LOW_UTI | 0 | 33 | 0 | Arlington Microgrid | WA | BPAT | PUD No 1 of Snohomish County - (WA) | 1 | 1.4 | 1.4 | <1.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.73878 | 0.00028455 | 232.8571 | 0.03881 | 0.028455 | 0.96119 | FALSE | C
366 | 60815 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 2.709 | 36 | 0 | Hampshire College Hybrid | MA | ISNE | Tesla Inc. | 1 | 1 | 1 | <1.5h | 2017 | LIB | CS | TRUE | pv_same_plant | 0.68184 | 0.0014605 | 238 | 0.039667 | 0.14605 | 0.96033 | FALSE | C
367 | 67321 | 10 | 2025-03 | 2025-12 | ELEVATED_P_AUX | 0 | 10 | 0 | Yuma Solar + Storage | AZ | AZPS | Invenergy Services LLC | 70 | 268 | 3.8286 | 2.5-4.5h | 2025 | LIB | CS | TRUE | pv_same_plant | 0.97884 | 0.79839 | 251.8619 | 0.041977 | 1.1406 | 0.95802 | FALSE | C
368 | 65057 | 22 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 8 | 0 | 299 Farm to Market Rd Hybrid(CSG) | MA | ISNE | 299F2M WHAM8 Solar, LLC | 2.3 | 4.9 | 2.1304 | 1.5-2.5h | 2021 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.84668 | -0.0049457 | 258.5714 | 0.043095 | -0.21503 | 0.9569 | FALSE | C
369 | 65669 | 25 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 16 | 0 | Faunce Corner Community Solar | MA | ISNE | Faunce Corner Road Dartmouth Solar 1, LLC | 1 | 3.9 | 3.9 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.76918 | 0.0029527 | 266.9231 | 0.044487 | 0.29527 | 0.95551 | FALSE | C
370 | 69190 | 10 | 2025-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 7 | 0 | GreenStruxure BBU004, LLC | CA | CISO | ClearGen LLC | 0.2 | 0.4 | 2 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.79007 | -0.00026526 | 270.8333 | 0.045139 | -0.13263 | 0.95486 | FALSE | C
371 | 61741 | 9 | 2023-04 | 2023-12 | FULL_OUTAGE | 29.931 | 9 | 0 | Kingsberry Energy Storage System | TX | ERCO | Austin Energy | 1.5 | 3 | 2 | 1.5-2.5h | 2018 | LIB | CS | TRUE | colocated_firming |  |  | 275.5556 | 0.045926 |  | 0.95407 | FALSE | C
372 | 67496 | 4 | 2025-01 | 2025-04 | PARTIAL_AVAILABILITY | 0 | 4 | 0 | Sandlake | TX | ERCO | HEN Infrastructure, L.L.C. | 9.9 | 9.9 | 1 | <1.5h | 2024 | LIB | CS | FALSE |  | 0.90067 | 0.0025951 | 275.5556 | 0.045926 | 0.026213 | 0.95407 | FALSE | A
373 | 64980 | 33 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 18 | 0 | UMass Boston | MA | ISNE | MSS Energy Holdings, LLC (d.b.a. Calibrant Energy) | 0.5 | 2.1 | 4.2 | 2.5-4.5h | 2021 | LIB | BL | TRUE | pv_same_plant | 0.77373 | 0.0026009 | 283.3333 | 0.047222 | 0.52018 | 0.95278 | FALSE | C
374 | 64640 | 35 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 38.6255 | 19 | 0 | Hot Springs Energy Storage & Microgrid | NC | CPLW | Duke Energy Progress - (NC) | 4.4 | 4.4 | 1 | <1.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.8571 | 0.0061293 | 285.9091 | 0.047652 | 0.1393 | 0.95235 | FALSE | C
375 | 61197 | 9 | 2019-12 | 2024-03 | FULL_OUTAGE | 11 | 7 | 0 | Pima Energy Storage System | AZ | TEPC | Pima Energy Storage System | 10 | 10 | 1 | <1.5h | 2017 | LIB | CS | TRUE | rte_gt_1 |  |  | 303.7 | 0.050617 |  | 0.94938 | FALSE | C
376 | 62497 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 0 | 12 | 0 | Orange County Energy Storage 2 | CA | CISO | Convergent Energy and Power LP | 9 | 36 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  |  |  | 312.1806 | 0.05203 |  | 0.94797 | FALSE | B
377 | 63763 | 2 | 2025-09 | 2025-10 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | CES Agawam Tuckahoe Solar Hybrid | MA | ISNE | CES Agawam Tuckahoe Solar LLC | 2.6 | 5.2 | 2 | 1.5-2.5h | 2021 | LIB | CS | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | 1 | -3.1915e-18 | 317.1154 | 0.052853 | -1.2275e-16 | 0.94715 | FALSE | C
378 | 64000 | 2 | 2023-07 | 2023-08 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Amaterasu LLC | MA | ISNE | AES Distributed Energy | 3.2 | 6 | 1.875 | 1.5-2.5h | 2021 | LIB | CT | TRUE | pv_same_plant,dc_tight | 0.86535 | 0.00020485 | 324 | 0.054 | 0.0064016 | 0.946 | FALSE | C
379 | 66620 | 29 | 2023-08 | 2025-12 | ELEVATED_P_AUX | 0 | 29 | 0 | Resurgence Solar II | CA | CISO | Resurgence Solar II | 40 | 300 | 7.5 | >4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.95123 | 0.40281 | 328.32 | 0.05472 | 1.007 | 0.94528 | FALSE | C
380 | 67762 | 2 | 2025-09 | 2025-10 | LOW_ETA_AND_LOW_UTI | 0 | 2 | 0 | Stampede Solar Hybrid | TX | ERCO | Stampede Solar Project LLC | 72.2 | 115 | 1.5928 | 1.5-2.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.81474 | -0.084502 | 340.313 | 0.056719 | -0.11704 | 0.94328 | FALSE | C
381 | 63804 | 17 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 6 | 0 | Partridgeville Hybrid CSG | MA | ISNE | Partridgeville Road Solar 1, LLC | 2 | 3.9 | 1.95 | 1.5-2.5h | 2020 | LIB | CS | TRUE | pv_same_plant | 0.85026 | 0.00084537 | 343.0769 | 0.057179 | 0.042268 | 0.94282 | FALSE | C
382 | 54296 | 46 | 2021-11 | 2025-12 | LOW_ETA_AND_LOW_UTI | 1 | 29 | 0 | Biola University Hybrid | CA | CISO | Biola University | 0.3 | 0.5 | 1.6667 | 1.5-2.5h | 2018 | LIB | CS | TRUE | rte_gt_1 | 0.85003 | 0.00025954 | 356.5 | 0.059417 | 0.086512 | 0.94058 | FALSE | C
383 | 65028 | 17 | 2023-07 | 2024-12 | LOW_ETA_AND_LOW_UTI | 0 | 14 | 0 | Roseland Solar Project, LLC | TX | ERCO | Enel Green Power Roseland Solar, LLC | 51.8 | 84.5 | 1.6313 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.79994 | 0.38853 | 381.7278 | 0.063621 | 0.75006 | 0.93638 | FALSE | C
384 | 64672 | 17 | 2023-06 | 2024-12 | LOW_ETA_AND_LOW_UTI | 0 | 10 | 0 | Blue Jay Solar I, LLC | TX | ERCO | Blue Jay Solar I, LLC | 51.6 | 84.5 | 1.6376 | 1.5-2.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.75549 | 0.1624 | 383.9882 | 0.063998 | 0.31472 | 0.936 | FALSE | C
385 | 65695 | 25 | 2022-10 | 2025-07 | LOW_ETA_AND_LOW_UTI | 0 | 19 | 0 | TX12 Silicon Hill Storage | TX | ERCO | Key Capture Energy | 100 | 100 | 1 | <1.5h | 2022 | LIB | CS | TRUE | rte_gt_1 | 0.58996 | 0.075363 | 418.52 | 0.069753 | 0.075363 | 0.93025 | FALSE | C
386 | 57583 | 4 | 2020-01 | 2023-05 | PARTIAL_AVAILABILITY | 11 | 2 | 0 | Battery Energy Storage System | AK |  | Golden Valley Elec Assn Inc | 40 | 11 | 0.275 | <1.5h | 2003 | NIB | BL | FALSE |  |  |  | 437.9015 | 0.072984 |  | 0.92702 | FALSE | B
387 | 62968 | 3 | 2023-10 | 2023-12 | FULL_OUTAGE | 123.5 | 3 | 0 | Syncarpha Tewksbury Hybrid CSG | MA | ISNE | Syncarpha Tewksbury, LLC | 2 | 4 | 2 | 1.5-2.5h | 2022 | LIB | CT | TRUE | pv_same_plant | 0.87589 | 0.0024944 | 458.5 | 0.076417 | 0.12472 | 0.92358 | FALSE | C
388 | 65614 | 19 | 2023-01 | 2024-08 | LOW_ETA_AND_LOW_UTI | 38 | 13 | 0 | Orange Coast College PH2 Solar Project | CA | CISO | Solar Star Coastal Pirate, LLC | 2.1 | 4 | 1.9048 | 1.5-2.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 0.51731 | -0.082572 | 505 | 0.084167 | -3.932 | 0.91583 | FALSE | C
389 | 57997 | 24 | 2024-01 | 2025-12 | ELEVATED_P_AUX | 0 | 24 | 0 | Foothills Solar Plant Hybrid | AZ | AZPS | Arizona Public Service Co | 35 | 105 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.93541 | 0.4883 | 509.9333 | 0.084989 | 1.3951 | 0.91501 | FALSE | C
390 | 66263 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Eleven Mile Solar Center | AZ | SRP | Eleven Mile Solar Center, LLC | 300 | 1200 | 4 | 2.5-4.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.92159 | 0.96564 | 509.9908 | 0.084998 | 0.32188 | 0.915 | FALSE | C
391 | 60441 | 2 | 2023-10 | 2023-11 | PARTIAL_AVAILABILITY | 2.5 | 2 | 0 | Salem Smart Power Center | OR | PGE | Portland General Electric Co | 5 | 5 | 1 | <1.5h | 2013 | LIB | BL | TRUE | colocated_firming,dc_coupled |  |  | 527.4744 | 0.087912 |  | 0.91209 | FALSE | C
392 | 57563 | 24 | 2024-01 | 2025-12 | ELEVATED_P_AUX | 0 | 24 | 0 | Hyder Solar Hybrid | AZ | AZPS | Arizona Public Service Co | 16 | 48 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.97373 | 0.25363 | 547.4583 | 0.091243 | 1.5852 | 0.90876 | FALSE | C
393 | 63472 | 9 | 2023-01 | 2024-05 | LOW_ETA_AND_LOW_UTI | 0 | 5 | 0 | Cycz Solar Project CSG Hybrid | MA | ISNE | AES Distributed Energy | 1.3 | 2.5 | 1.9231 | 1.5-2.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.7645 | -0.00033773 | 550.8 | 0.0918 | -0.025979 | 0.9082 | FALSE | C
394 | 59257 | 31 | 2019-01 | 2021-07 | LOW_ETA_AND_LOW_UTI | 5673.0361 | 31 | 0 | Yerba Buena | CA | CISO | Pacific Gas & Electric Co. | 4 | 28 | 7 | >4.5h | 2013 | NAB | CS | FALSE |  | 0.65786 | 0.17232 | 564.494 | 0.094082 | 4.3079 | 0.90592 | FALSE | A
395 | 62499 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 0 | 12 | 0 | Orange County Energy Storage 3 | CA | CISO | Convergent Energy and Power LP | 6 | 24 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  |  |  | 568.5486 | 0.094758 |  | 0.90524 | FALSE | B
396 | 64489 | 4 | 2024-05 | 2025-04 | LOW_ETA_AND_LOW_UTI | 0 | 2 | 0 | Resurgence Solar | CA | CISO | Resurgence Solar | 75 | 300 | 4 | 2.5-4.5h | 2023 | OTH | CS | TRUE | pv_same_plant | 0.84459 | -0.095791 | 575.1967 | 0.095866 | -0.12772 | 0.90413 | FALSE | C
397 | 57562 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Paloma Solar Hybrid | AZ | AZPS | Arizona Public Service Co | 17 | 51 | 3 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.85475 | 0.059303 | 588.0784 | 0.098013 | 0.34884 | 0.90199 | FALSE | C
398 | 64618 | 7 | 2024-08 | 2025-02 | LOW_ETA_AND_LOW_UTI | 0 | 7 | 0 | Kearsarge Haverhill | MA | ISNE | Kearsarge Haverhill LLC | 2 | 9 | 4.5 | >4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.85219 | 0.0053492 | 627 | 0.1045 | 0.26746 | 0.8955 | FALSE | C
399 | 65675 | 2 | 2024-04 | 2024-05 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Edwards Sanborn E4 | CA | CISO | Terra-Gen Operating Co-Hybrid | 100 | 100 | 1 | <1.5h | 2023 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 1.0514 | 0.85621 | 635.08 | 0.10585 | 0.85621 | 0.89415 | FALSE | C
400 | 66163 | 4 | 2024-10 | 2025-05 | LOW_ETA_AND_LOW_UTI | 0 | 2 | 0 | Jicarilla Solar 1 LLC | NM | PNM | Repsol Renewables NA | 20 | 80 | 4 | 2.5-4.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.84002 | -0.040051 | 641.3125 | 0.10689 | -0.20026 | 0.89311 | FALSE | C
401 | 61721 | 4 | 2020-08 | 2022-09 | PARTIAL_AVAILABILITY | 120 | 2 | 0 | Baldwin (CA) | CA | CISO | Electrodes | 1 | 6.9 | 6.9 | >4.5h | 2019 | LIB | CS | TRUE | rte_gt_1 | 0.87837 | -0.00021785 | 679.8551 | 0.11331 | -0.021785 | 0.88669 | FALSE | C
402 | 64103 | 58 | 2021-03 | 2025-12 | ELEVATED_P_AUX | 0 | 58 | 0 | Desert Harvest II LLC | CA | CISO | Desert Harvest II LLC | 35 | 140 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.94985 | 0.36413 | 714.8714 | 0.11915 | 1.0404 | 0.88085 | FALSE | C
403 | 66423 | 2 | 2024-04 | 2024-05 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Stanton Battery Energy Storage | CA | CISO | Wellhead Services, Inc | 68.8 | 275.2 | 4 | 2.5-4.5h | 2023 | LIB | CS | FALSE |  | 0.91993 | 0.27653 | 724.2078 | 0.1207 | 0.40193 | 0.8793 | FALSE | B
404 | 64620 | 36 | 2023-01 | 2025-12 | ELEVATED_P_AUX | 0 | 36 | 0 | Kearsarge Montague BD(CSG) | MA | ISNE | Kearsarge Montague BD LLC | 1.3 | 5.1 | 3.9231 | 2.5-4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.9263 | 0.013159 | 742.1569 | 0.12369 | 1.0122 | 0.87631 | FALSE | C
405 | 64564 | 9 | 2022-08 | 2023-11 | LOW_ETA_AND_LOW_UTI | 3632.5 | 7 | 0 | Arlington Energy Center III | CA | CISO | Arlington Energy Center III | 110 | 440 | 4 | 2.5-4.5h | 2022 | LIB | CT | TRUE | pv_same_plant | 0.83188 | 0.12898 | 743.3909 | 0.1239 | 0.11726 | 0.8761 | FALSE | C
406 | 59993 | 49 | 2019-02 | 2025-12 | LOW_ETA_AND_LOW_UTI | 1310 | 23 | 0 | Babcock Solar Energy Center Hybrid | FL | FPL | Florida Power & Light Co | 10 | 40 | 4 | 2.5-4.5h | 2018 | LIB | CS | TRUE | rte_gt_1,colocated_firming,pv_same_plant | 0.73129 | 0.029433 | 745.1 | 0.12418 | 0.29433 | 0.87582 | FALSE | C
407 | 62745 | 14 | 2022-11 | 2025-12 | LOW_ETA_AND_LOW_UTI | 1175 | 5 | 0 | Wheatridge Hybrid | OR | BPAT | Wheatridge Wind Holdings, LLC | 30 | 120 | 4 | 2.5-4.5h | 2022 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.74406 | 0.024342 | 773.3083 | 0.12888 | 0.081141 | 0.87112 | FALSE | C
408 | 64105 | 2 | 2023-06 | 2023-07 | PARTIAL_AVAILABILITY | 1420 | 2 | 0 | Maverick Solar 6, LLC | CA | CISO | Maverick Solar 6, LLC | 50 | 200 | 4 | 2.5-4.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.86791 | -0.074377 | 777.205 | 0.12953 | -0.14875 | 0.87047 | FALSE | C
409 | 63468 | 34 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 18 | 0 | Hurteau Solar Project Hybrid | MA | ISNE | AES Distributed Energy | 1.3 | 1.5 | 1.1538 | <1.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.71176 | 0.0055396 | 800.6667 | 0.13344 | 0.42612 | 0.86656 | FALSE | C
410 | 63486 | 2 | 2023-11 | 2023-12 | PARTIAL_AVAILABILITY | 1.5 | 2 | 0 | D'Arrigo Brothers - Phase 4 | CA | CISO | CalCom Energy | 0.5 | 0.8 | 1.6 | 1.5-2.5h | 2019 | LIB | CS | TRUE | pv_same_plant | 1.2724 | 0.0099631 | 810 | 0.135 | 1.9926 | 0.865 | FALSE | C
411 | 62382 | 2 | 2021-09 | 2021-10 | PARTIAL_AVAILABILITY | 22 | 2 | 0 | GMP Solar/Storage-Ferrisburgh Hybrid | VT | ISNE | Green Mountain Power Corp | 2 | 8 | 4 | 2.5-4.5h | 2019 | LIB | OT | TRUE | rte_gt_1,pv_same_plant | 2.158 | -0.012747 | 843.875 | 0.14065 | -0.63736 | 0.85935 | FALSE | C
412 | 62733 | 9 | 2023-06 | 2024-05 | FULL_OUTAGE | 0 | 5 | 0 | East Hampton Energy Storage Center | NY | NYIS | East Hampton Energy Storage Center, LLC | 5 | 40 | 8 | >4.5h | 2018 | LIB | BL | FALSE |  | 0.94622 | 0.016416 | 848.9354 | 0.14149 | 0.32832 | 0.85851 | FALSE | A
413 | 64450 | 36 | 2023-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 36 | 0 | Grissom Solar, LLC | NC | PJM | SunStrong Management | 10 | 10 | 1 | <1.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.85338 | 0.0018346 | 872.7 | 0.14545 | 0.018346 | 0.85455 | FALSE | C
414 | 64481 | 7 | 2022-08 | 2023-10 | LOW_ETA_AND_LOW_UTI | 2888 | 3 | 0 | Arlington Energy Center II | CA | CISO | Arlington Energy Center II | 132 | 528 | 4 | 2.5-4.5h | 2022 | LIB | CT | TRUE | pv_same_plant | 0.84763 | 0.048473 | 878.8864 | 0.14648 | 0.036722 | 0.85352 | FALSE | C
415 | 59939 | 4 | 2023-01 | 2023-07 | PARTIAL_AVAILABILITY | 3060.4675 | 2 | 0 | RE Tranquillity | CA | CISO | Southern Power Co | 72 | 288 | 4 | 2.5-4.5h | 2021.4861 | LIB | CS | TRUE | pv_same_plant,dc_coupled | 0.93866 | 0.64574 | 884.4358 | 0.14741 | 0.89687 | 0.85259 | FALSE | C
416 | 61366 | 2 | 2023-06 | 2023-07 | PARTIAL_AVAILABILITY | 535 | 2 | 0 | Top Gun Energy Storage | CA | CISO | San Diego Gas & Electric Co | 30 | 120 | 4 | 2.5-4.5h | 2021 | LIB | CS | FALSE |  | 0.90905 | 0.28396 | 886.8417 | 0.14781 | 0.94654 | 0.85219 | FALSE | B
417 | 60092 | 2 | 2022-08 | 2022-09 | PARTIAL_AVAILABILITY | 2557 | 2 | 0 | Blythe Solar II, LLC | CA | CISO | Blythe Solar II, LLC | 115 | 538.6 | 4.6835 | >4.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.94801 | 0.80332 | 915.8522 | 0.15264 | 0.69854 | 0.84736 | FALSE | C
418 | 63420 | 3 | 2023-09 | 2023-11 | FULL_OUTAGE | 29 | 3 | 0 | Fresno Bullard High School Hybrid | CA | CISO | Forefront Power, LLC | 0.4 | 0.4 | 1 | <1.5h | 2020 | LIB | CS | TRUE | rte_gt_1,pv_same_plant | 1.0297 | 0.0013745 | 917.5 | 0.15292 | 0.34362 | 0.84708 | FALSE | C
419 | 61439 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 0 | 36 | 0 | Panasonic Carport Solar Hybrid | CO | PSCO | Public Service Co of Colorado | 1 | 2.2 | 2.2 | 1.5-2.5h | 2017 | LIB | CS | TRUE | rte_gt_1,pv_same_plant |  |  | 924.2424 | 0.15404 |  | 0.84596 | FALSE | C
420 | 61068 | 5 | 2020-10 | 2022-07 | PARTIAL_AVAILABILITY | 2810.5 | 3 | 0 | AES Lawai Solar Hybrid | HI |  | AES Distributed Energy | 20 | 100 | 5 | >4.5h | 2018 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.99442 | 0.020298 | 935.69 | 0.15595 | 0.10149 | 0.84405 | FALSE | C
421 | 59871 | 13 | 2024-12 | 2025-12 | ELEVATED_P_AUX | 0 | 13 | 0 | Desert Quartzite | CA | CISO | Desert Quartzite LLC | 150 | 150 | 1 | <1.5h | 2024 | LIB | CS | TRUE | pv_same_plant | 0.98194 | 2.0627 | 993.4467 | 0.16557 | 1.3751 | 0.83443 | FALSE | C
422 | 64879 | 5 | 2022-10 | 2023-11 | PARTIAL_AVAILABILITY | 2817 | 3 | 0 | Edwards Sanborn E2 | CA | CISO | Terra-Gen Operating Co-Hybrid | 120 | 250 | 2.0833 | 1.5-2.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.88516 | 0.78251 | 1004.256 | 0.16738 | 0.65209 | 0.83262 | FALSE | C
423 | 61861 | 44 | 2022-05 | 2025-12 | FULL_OUTAGE | 3203.5 | 44 | 0 | AES ES GILBERT | AZ | SRP | AES ES GILBERT, LLC | 10 | 40 | 4 | 2.5-4.5h | 2019 | LIB | BL | TRUE | rte_gt_1 | 0.87258 | 0.017088 | 1008.75 | 0.16812 | 0.17088 | 0.83188 | FALSE | C
424 | 64148 | 4 | 2023-03 | 2023-08 | PARTIAL_AVAILABILITY | 1944 | 2 | 0 | Fish Springs | NV | NEVP | Fish Springs Ranch Solar, LLC | 25 | 100 | 4 | 2.5-4.5h | 2022 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_tight | 0.88043 | -0.023365 | 1011.16 | 0.16853 | -0.093461 | 0.83147 | FALSE | C
425 | 63324 | 9 | 2023-01 | 2023-10 | FULL_OUTAGE | 285.1195 | 7 | 0 | Camp Atterbury Microgrid Hybrid | IN | MISO | Duke Energy Indiana, LLC | 5 | 5 | 1 | <1.5h | 2019 | LIB | BL | TRUE | rte_gt_1,pv_same_plant | 0.89809 | 0.0037108 | 1011.8 | 0.16863 | 0.074217 | 0.83137 | FALSE | C
426 | 65140 | 2 | 2023-03 | 2023-04 | PARTIAL_AVAILABILITY | 3703 | 2 | 0 | Crimson | CA | CISO | RE Crimson LLC | 350 | 1400 | 4 | 2.5-4.5h | 2022 | LIB | CS | FALSE |  | 0.87457 | -0.48569 | 1052.2657 | 0.17538 | -0.13877 | 0.82462 | FALSE | B
427 | 63930 | 2 | 2022-10 | 2022-11 | PARTIAL_AVAILABILITY | 2346 | 2 | 0 | Cal Flats BESS | CA | CISO | Arevon Energy, Inc. | 60 | 242 | 4.0333 | 2.5-4.5h | 2021 | LIB | CS | TRUE | rte_gt_1,colocated_firming | 0.89865 | 0.23822 | 1053.7686 | 0.17563 | 0.39703 | 0.82437 | FALSE | C
428 | 62609 | 4 | 2019-10 | 2020-07 | FULL_OUTAGE | 46 | 2 | 0 | Commerce ESS | TX | ERCO | City of San Antonio - (TX) | 10 | 10 | 1 | <1.5h | 2019 | LIB | CS | FALSE |  | 0.96341 | 0.094758 | 1076.1 | 0.17935 | 0.94758 | 0.82065 | FALSE | B
429 | 60016 | 60 | 2019-09 | 2024-10 | FULL_OUTAGE | 12.5 | 34 | 0 | MESA 1 | WA | BPAT | PUD No 1 of Snohomish County - (WA) | 2 | 1 | 0.5 | <1.5h | 2015.5 | LIB | CS | FALSE |  |  |  | 1081 | 0.18017 |  | 0.81983 | FALSE | B
430 | 60654 | 2 | 2022-09 | 2022-10 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Townsite Solar Project Hybrid | NV | WALC | Townsite Solar, LLC | 90 | 360 | 4 | 2.5-4.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant | 0.84491 | -0.24226 | 1101.8194 | 0.18364 | -0.26917 | 0.81636 | FALSE | C
431 | 64701 | 2 | 2025-07 | 2025-08 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | LeConte Energy Storage | CA | CISO | LeConte Energy Storage, LLC | 125 | 250 | 2 | 1.5-2.5h | 2022 | LIB | CS | FALSE |  | 0.86386 | 0.58065 | 1136.22 | 0.18937 | 0.46452 | 0.81063 | FALSE | B
432 | 60444 | 12 | 2025-01 | 2025-12 | FULL_OUTAGE | 0 | 12 | 0 | Glacier Battery Storage | WA | PSEI | Puget Sound Energy Inc | 2 | 4.4 | 2.2 | 1.5-2.5h | 2016 | LIB | CT | FALSE |  |  |  | 1154.6212 | 0.19244 |  | 0.80756 | FALSE | B
433 | 64426 | 2 | 2023-08 | 2023-09 | PARTIAL_AVAILABILITY | 276 | 2 | 0 | Wilmot Energy Center LLC | AZ | TEPC | Wilmot Energy Center LLC | 30 | 60 | 2 | 1.5-2.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.95268 | 0.22939 | 1260.1833 | 0.21003 | 0.76463 | 0.78997 | FALSE | C
434 | 60569 | 2 | 2021-10 | 2021-11 | PARTIAL_AVAILABILITY | 246 | 2 | 0 | El Cajon Energy Storage | CA | CISO | San Diego Gas & Electric Co | 7.5 | 30 | 4 | 2.5-4.5h | 2017 | LIB | CS | FALSE |  | 0.91281 | 0.032769 | 1356.0833 | 0.22601 | 0.43692 | 0.77399 | FALSE | B
435 | 64400 | 24 | 2023-01 | 2024-12 | FULL_OUTAGE | 435.693 | 24 | 0 | BYU - Hawaii | HI | HECO | SkyHigh 2 Solar | 1.9 | 1.9 | 1 | <1.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.89749 | 0.0076518 | 1460.5263 | 0.24342 | 0.40272 | 0.75658 | FALSE | C
436 | 64664 | 2 | 2023-11 | 2023-12 | PARTIAL_AVAILABILITY | 29.5 | 2 | 0 | Clark Road Solar 1, LLC | MA | ISNE | Clark Road Solar 1, LLC | 3.3 | 3 | 0.90909 | <1.5h | 2021 | LIB | CS | TRUE | colocated_firming,pv_same_plant,dc_coupled | 1.0072 | 0.015664 | 1561.6667 | 0.26028 | 0.47465 | 0.73972 | FALSE | C
437 | 60390 | 2 | 2020-12 | 2021-01 | PARTIAL_AVAILABILITY | 143 | 2 | 0 | Beech Ridge Energy Storage | WV | PJM | Invenergy Services LLC | 31.5 | 12.5 | 0.39683 | <1.5h | 2015 | LIB | CT | TRUE | dc_coupled | 0.43691 | -0.012277 | 1602.78 | 0.26713 | -0.038976 | 0.73287 | FALSE | C
438 | 65674 | 2 | 2025-05 | 2025-06 | PARTIAL_AVAILABILITY | 0 | 2 | 0 | Edwards Sanborn E1B | CA | CISO | Terra-Gen Operating Co-Hybrid | 136 | 136 | 1 | <1.5h | 2023 | LIB | CS | TRUE | pv_same_plant | 0.94939 | 1.3348 | 1617.0441 | 0.26951 | 0.98147 | 0.73049 | FALSE | C
439 | 63757 | 6 | 2023-06 | 2023-11 | THERMAL_AUX | 1283.3045 | 6 | 0 | Madero Grid | TX | ERCO | Madero Grid, LLC | 100 | 100 | 1 | <1.5h | 2023 | LIB | CS | FALSE |  | 0.87641 | 0.36863 | 1637.38 | 0.2729 | 0.36863 | 0.7271 | FALSE | A
440 | 60518 | 50 | 2021-11 | 2025-12 | FULL_OUTAGE | 0 | 50 | 0 | Stafford Hill Solar Hybrid | VT | ISNE | Green Mountain Power Corp | 2 | 3.4 | 1.7 | 1.5-2.5h | 2015 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 1.1512 | -0.0019823 | 1643.5294 | 0.27392 | -0.099117 | 0.72608 | FALSE | C
441 | 61107 | 36 | 2023-01 | 2025-12 | ELEVATED_P_AUX | 0 | 36 | 0 | Vanadium Redox Flow Battery Plant | CA | CISO | SDGE Batteries | 2 | 8 | 4 | 2.5-4.5h | 2017 | FLB | CS | TRUE | colocated_firming | 0.68766 | 0.12073 | 1662.6146 | 0.2771 | 6.0364 | 0.7229 | FALSE | C
442 | 1016 | 28 | 2022-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 0 | 18 | 0 | Butler-Warner Generation Plant | NC | CPLE | Fayetteville Public Works Commission | 0.5 | 0.5 | 1 | <1.5h | 2019 | LIB | CS | TRUE | pv_same_plant | 0.81993 | 0.0038186 | 1770 | 0.295 | 0.76371 | 0.705 | FALSE | C
443 | 60996 | 24 | 2023-01 | 2024-12 | FULL_OUTAGE | 419.995 | 24 | 0 | Iron Horse Battery Storage Hybrid | AZ | TEPC | RWE Clean Energy | 10 | 2.5 | 0.25 | <1.5h | 2017 | LIB | CS | TRUE | pv_same_plant | 0.82869 | 0.066954 | 1773.8 | 0.29563 | 0.66954 | 0.70437 | FALSE | C
444 | 62027 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 0 | 36 | 0 | Caldwell Wastewater Treatment Plant Hybr | NJ | PJM | Caldwell Wastewater Treatment Plant | 1 | 2 | 2 | 1.5-2.5h | 2016 | OTH | CS | TRUE | colocated_firming,pv_same_plant |  |  | 1797.625 | 0.2996 |  | 0.7004 | FALSE | C
445 | 61956 | 29 | 2023-03 | 2025-12 | LOW_ETA_AND_LOW_UTI | 5.728 | 9 | 0 | MCRD Parris Island PV Hybrid | SC | SCEG | Ameresco Federal Solutions | 4 | 8 | 2 | 1.5-2.5h | 2018 | LIB | CS | TRUE | rte_gt_1,pv_same_plant,dc_coupled | 0.77141 | 0.0050236 | 1846.1042 | 0.30768 | 0.12559 | 0.69232 | FALSE | C
446 | 61431 | 65 | 2019-01 | 2025-06 | LOW_ETA_AND_LOW_UTI | 319 | 55 | 0 | Beacon BESS 1 | CA | LDWP | Los Angeles Department of Water & Power | 20 | 10 | 0.5 | <1.5h | 2018 | LIB | CS | TRUE | colocated_firming | 0.74977 | 0.063687 | 1919.825 | 0.31997 | 0.31843 | 0.68003 | FALSE | C
447 | 62856 | 67 | 2019-04 | 2025-11 | LOW_ETA_AND_LOW_UTI | 0 | 44 | 0 | Marengo Battery Storage LLC | IL | PJM | Marengo Battery Storage LLC | 20 | 20 | 1 | <1.5h | 2018 | LIB | CS | TRUE | rte_gt_1 | 0.83514 | -0.071729 | 2173.7458 | 0.36229 | -0.35864 | 0.63771 | FALSE | C
448 | 60095 | 2 | 2025-06 | 2025-07 | LOW_ETA_AND_LOW_UTI | 0 | 2 | 0 | Blythe Solar IV, LLC | CA | CISO | Blythe Solar IV, LLC | 47 | 47 | 1 | <1.5h | 2022 | LIB | CS | TRUE | pv_same_plant | 0.83788 | 0.026572 | 2644.2181 | 0.4407 | 0.056537 | 0.5593 | FALSE | C
449 | 56981 | 84 | 2019-01 | 2025-12 | ELEVATED_P_AUX | 15.5 | 84 | 0 | Pyron Wind Farm LLC Hybrid | TX | ERCO | RWE Clean Energy | 9.9 | 9.9 | 1 | <1.5h | 2018 | LIB | CS | TRUE | rte_gt_1 | 0.97322 | 0.16196 | 3067.5758 | 0.51126 | 1.6359 | 0.48874 | FALSE | C
450 | 61473 | 36 | 2023-01 | 2025-12 | FULL_OUTAGE | 0 | 36 | 0 | Hopewell Valley High School Hybrid | NJ | PJM | Hopewell Valley High School | 1 | 1 | 1 | <1.5h | 2015 | LIB | BL | TRUE | colocated_firming,pv_same_plant |  |  | 3266.6667 | 0.54444 |  | 0.45556 | FALSE | C
451 | 59960 | 30 | 2019-01 | 2021-06 | THERMAL_AUX | 731.3852 | 30 | 0 | Jake Energy Storage Center | IL | PJM | Joliet Battery Storage LLC | 19.8 | 7.9 | 0.39899 | <1.5h | 2015 | LIB | CS | FALSE |  | 0.82503 | 0.074112 | 3658.9451 | 0.60982 | 0.3743 | 0.39018 | FALSE | A
452 | 61661 | 3 | 2019-06 | 2019-08 | PARTIAL_AVAILABILITY | 2175 | 3 | 0 | Vista Energy Storage System | CA | CISO | Vista Energy Storage, LLC | 40 | 38 | 0.95 | <1.5h | 2018 | LIB | BL | FALSE |  | 0.94202 | 0.27938 | 4442.1547 | 0.74036 | 0.69845 | 0.25964 | FALSE | A
453 | 59150 | 2 | 2023-01 | 2023-02 | PARTIAL_AVAILABILITY | 5801.8815 | 2 | 0 | RE Mustang LLC | CA | CISO | MN8 Energy LLC | 75 | 75 | 1 | <1.5h | 2021 | LIB | CS | TRUE | pv_same_plant | 0.85916 | 0.017245 | 4669.44 | 0.77824 | 0.022994 | 0.22176 | FALSE | C
454 | 60656 | 12 | 2023-12 | 2024-11 | FULL_OUTAGE | 0 | 12 | 0 | McHenry Battery Storage | IL | PJM | McHenry Battery Storage | 20 | 7.8 | 0.39 | <1.5h | 2016 | LIB | CS | FALSE |  | 0.89847 | 0.059361 | 4681.6239 | 0.78027 | 0.29681 | 0.21973 | FALSE | A
455 | 2830 | 76 | 2019-01 | 2025-12 | LOW_ETA_AND_LOW_UTI | 164 | 27 | 0 | Walter C Beckjord | OH | PJM | Duke Energy Ohio Inc | 4 | 1.8 | 0.45 | <1.5h | 2015 | LIB | CS | TRUE | rte_gt_1 | 0.71279 | 0.017874 | 7086.6667 | 1.1811 | 0.44685 | 0 | FALSE | C
456 | 50300 | 48 | 2019-01 | 2022-12 | ELEVATED_P_AUX | 15256.7175 | 48 | 0 | VESI Pomona | CA | CISO | VESI Pomona Energy Storage, Inc. | 40 | 40 | 1 | <1.5h | 2019.5 | LIB | BL | FALSE |  | 0.9922 | 0.38754 | 8653.7917 | 1.4423 | 0.96886 | 0 | FALSE | A
457 | 56961 | 2 | 2023-11 | 2023-12 | PARTIAL_AVAILABILITY | 269 | 2 | 0 | Notrees Windpower Hybrid | TX | ERCO | Deriva Energy | 36 | 13.6 | 0.37778 | <1.5h | 2012 | LIB | BL | FALSE |  | 1.1042 | 0.3549 | 7154.5956 | 1.1924 | 0.98583 | 0 | FALSE | B
458 | 57325 | 2 | 2022-12 | 2023-01 | PARTIAL_AVAILABILITY | 347 | 2 | 0 | FPL Energy Illinois Wind LLC Hybrid | IL | PJM | FPL Energy Illinois Wind LLC | 20 | 8.3 | 0.415 | <1.5h | 2014 | LIB | CS | TRUE | rte_gt_1 | 0.89811 | 0.0058536 | 24216.6064 | 4.0361 | 0.029268 | 0 | FALSE | C
459 | 59959 | 24 | 2019-07 | 2021-10 | LOW_ETA_AND_LOW_UTI | 1291.1651 | 22 | 0 | Elwood Energy Storage Center | IL | PJM | West Chicago Battery Storage LLC | 19.8 | 7.9 | 0.39899 | <1.5h | 2015 | LIB | CS | FALSE |  | 0.80433 | 0.075531 | 7017.8165 | 1.1696 | 0.38147 | 0 | FALSE | A
460 | 60299 | 24 | 2023-01 | 2024-12 | FULL_OUTAGE | 0 | 24 | 0 | HMV Minster Energy Storage System | OH | PJM | Summit Ridge Energy | 7 | 7 | 1 | <1.5h | 2016 | LIB | CS | TRUE | rte_gt_1 |  |  | 13222.2619 | 2.2037 |  | 0 | FALSE | C
461 | 60566 | 12 | 2025-01 | 2025-12 | ELEVATED_P_AUX | 0 | 12 | 0 | Pala Energy Storage Yard | CA | CISO | SDGE Batteries | 1 | 2 | 2 | 1.5-2.5h | 2015 | LIB | CS | TRUE | rte_gt_1 | 0.92925 | 0.084451 | 6635.119 | 1.1059 | 8.4451 | 0 | FALSE | C
462 | 60690 | 6 | 2021-06 | 2023-12 | PARTIAL_AVAILABILITY | 1440 | 2 | 0 | Blue Summit Storage, LLC | TX | ERCO | Blue Summit Storage, LLC | 30 | 12.6 | 0.42 | <1.5h | 2017 | LIB | CS | FALSE |  | 0.87195 | 0.1476 | 8189.1204 | 1.3649 | 0.49201 | 0 | FALSE | B
463 | 61892 | 2 | 2021-08 | 2021-09 | PARTIAL_AVAILABILITY | 1575 | 2 | 0 | Plumsted 537 LLC | NJ | PJM | Plumsted 537 LLC | 19.8 | 19.8 | 1 | <1.5h | 2019 | LIB | CS | FALSE |  | 0.87781 | 0.0098683 | 12567.5253 | 2.0946 | 0.04984 | 0 | FALSE | B
464 | 64611 | 2 | 2023-08 | 2023-09 | PARTIAL_AVAILABILITY | 44.5 | 2 | 0 | SEPV Sierra | CA | CISO | SEPV Sierra, LLC | 8.3 | 3.4 | 0.40964 | <1.5h | 2020 | LIB | CS | TRUE | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled | 1.4631 | 0.046024 | 8997.3529 | 1.4996 | 0.55451 | 0 | FALSE | C

## gates
check | expected | got | status | note
Fleet median apparent RTE 2025, standalone (site annual D/C) | 0.851 ±0.02 | 0.84 | PASS | median of monthly RTE 0.842; throughput-weighted 0.855
Decomposed eta_true, fleet median | 0.889 ±0.02 | 0.889 | PASS | p10 0.778, p90 0.954; standalone only 0.888
Naive RTE on the same fitted sites (site mean of monthly RTE) | 0.844 ±0.02 | 0.84 | PASS | throughput-weighted per site 0.854
Gap eta_true - naive (points) | ~4.5 ±1.5 | 4.87 | PASS | with throughput-weighted naive: 3.42
eta_true above naive RTE (regression not inverted) | True | TRUE | PASS
P_aux % of nameplate, median | 0.21 (p90 < ~1%) | 0.221 | PASS | p10 -0.07%, p90 0.84%
Sites with a usable aux decomposition | ~600 of ~960 | 623 of 988 | PASS
Total BESS discharge 2025 (MWh) | 26,500,000 ±1,000,000 | 26,706,620 | PASS
Total BESS discharge 2019 (MWh) | 430,000 ±30,000 | 456,006 | PASS
BESS nameplate 2025 (GW, EIA-860 3_4 BA) | ~40-43 | 44 | WARN | year-end operable incl. units commissioned late 2025
Median duration 2025 (h) | 2.0 | 2 | PASS
Capacity join rate to EIA-860 (plant-months) | >=0.98 | 0.9942 | PASS | same-vintage 0.9837
Fleet RTE vs EIA published anchor (standalone 2025, throughput-weighted) | ~0.82-0.85 (and <0.95) | 0.855 | PASS | above 0.95 would mean hybrids included or Quantity/Grossgen swapped
Variance/mean of fault counts, FULL_OUTAGE | >1 (overdispersion -> NB) | 1.1 | WARN | NB alpha=0.000; used: poisson (alpha~0)
Variance/mean of fault counts, PARTIAL_AVAILABILITY | >1 (overdispersion -> NB) | 0.93 | WARN | NB alpha=0.000; used: poisson (alpha~0)
Variance/mean of fault counts, THERMAL_AUX | >1 (overdispersion -> NB) | 1.18 | WARN | NB alpha=1.041; used: negative binomial
Variance/mean of fault counts, UNATTRIBUTED | >1 (overdispersion -> NB) | 1.26 | WARN | NB alpha=0.000; used: poisson (alpha~0)
Backtest FULL_OUTAGE (fit<=Y, predict Y+1, 2023-2025) | AUC>0.65, slope~1, chi2/df~1, beats mean | AUC 0.63, slope 0.65, chi2/df 3.9 | WARN | 40% of test plant-years are sites with no prior history; beats mean: True
Backtest PARTIAL_AVAILABILITY (fit<=Y, predict Y+1, 2023-2025) | AUC>0.65, slope~1, chi2/df~1, beats mean | AUC 0.61, slope 0.48, chi2/df 11.3 | WARN | 40% of test plant-years are sites with no prior history; beats mean: False
Backtest THERMAL_AUX (fit<=Y, predict Y+1, 2023-2025) | AUC>0.65, slope~1, chi2/df~1, beats mean | AUC 0.74, slope 0.83, chi2/df 3.9 | WARN | 40% of test plant-years are sites with no prior history; beats mean: True
Backtest UNATTRIBUTED (fit<=Y, predict Y+1, 2023-2025) | AUC>0.65, slope~1, chi2/df~1, beats mean | AUC 0.61, slope 0.41, chi2/df 6.2 | WARN | 40% of test plant-years are sites with no prior history; beats mean: False

## efficiency_decomposition
plant_id | plant_name | hybrid | dur_band | enclosure | nameplate_mw | usable_months | n | fit_ok | eta_true | P_aux_mw | P_aux_pct_nameplate | P_aux_summer_mw | P_aux_shoulder_mw | P_aux_winter_mw | hvac_excess_mw | hvac_excess_pct_nameplate | naive_rte | naive_rte_mean_month | naive_rte_median_month | r2 | se_a | se_b | eta_trend_pts_per_yr | paux_trend_pct_per_yr | trend_status
141 | Agua Fria | TRUE | 2.5-4.5h | CS | 25 | 49 | 49 | TRUE | 0.88371 | 0.1818 | 0.7272 | 0.045654 | 0.18339 | 0.17859 | -0.13773 | -0.55094 | 0.82369 | 0.80533 | 0.84633 | 0.36749 | 0.033415 | 0.03479 | -2.4722 | -25.753 | ok
260 | Dynegy Moss Landing Power Plant Hybrid | TRUE | 2.5-4.5h | BL | 750 | 43 | 43 | TRUE | 0.79721 | -1.1221 | -0.14961 | -1.7254 | -1.4549 | 0.62429 | -0.27054 | -0.036072 | 0.83591 | 0.82314 | 0.83816 | 0.34076 | 0.025466 | 0.24374 | 5.1133 | 92.1275 | ok
389 | El Centro Hybrid | FALSE | <1.5h | BL | 30 | 74 | 74 | TRUE | 0.77993 | 0.223 | 0.74332 | 0.21301 | 0.20107 | 0.26045 | 0.01194 | 0.039801 | 0.56876 | 0.51966 | 0.54739 | 0.44721 | 0.077946 | 0.029218 | 0.086568 | 0.88962 | ok
645 | Big Bend | TRUE | 1.5-2.5h | CS | 12.6 | 12 | 12 | TRUE | 0.90825 | 0.0074176 | 0.05887 | 0.0068253 | 0.0075837 | 0.0077095 | -0.00075834 | -0.0060186 | 0.85772 | 0.70328 | 0.76188 | 0.90474 | 0.056224 | 0.00076114 |  |  | ok
1016 | Butler-Warner Generation Plant | TRUE | <1.5h | CS | 0.5 | 44 | 44 | TRUE | 0.81993 | 0.0038186 | 0.76371 | 0.004813 | 0.0035283 | 0.0030625 | 0.0012847 | 0.25694 | 0.7308 | 0.67997 | 0.69097 | 0.618 | 0.0449 | 0.00046325 | -1.8892 | 34.178 | ok
1482 | Bonny Eagle | FALSE | 1.5-2.5h | CS | 8 | 32 | 32 | TRUE | 0.77888 | -0.0057817 | -0.072271 | 0.011075 | -0.01437 | 0.0065744 | 0.025445 | 0.31806 | 0.78661 | 0.79017 | 0.8053 | 0.0021744 | 0.038781 | 0.022613 | 9.7409 | 135.5103 | ok
1507 | William F Wyman Hybrid | FALSE | <1.5h | CS | 16.7 | 83 | 83 | TRUE | 0.83322 | 0.023179 | 0.1388 | 0.030172 | 0.020217 | 0.033955 | 0.0099548 | 0.05961 | 0.83276 | 0.80771 | 0.81476 | 0.44162 | 0.0083018 | 0.002896 | -2.4443 | -28.5301 | ok
1615 | Nantucket Hybrid | FALSE | >4.5h | BL | 6 | 16 | 16 | TRUE | 0.87413 | 0.02725 | 0.45416 | 0.025644 | 0.034659 | 0.029109 | -0.0090157 | -0.15026 | 0.61007 | 0.41166 | 0.54953 | 0.55213 | 0.1872 | 0.0065592 |  |  | ok
1682 | Cleary Flood Hybrid | FALSE | 1.5-2.5h | CS | 3 | 36 | 36 | TRUE | 0.94286 | 0.013795 | 0.45982 | 0.013773 | 0.013794 | 0.015149 | -2.0868e-05 | -0.00069561 | 0.74915 | 0.70992 | 0.73329 | 0.91539 | 0.026054 | 0.00071926 | -0.27738 | -9.7166 | ok
2324 | Reid Gardner | FALSE | <1.5h | CS | 220 | 23 | 23 | TRUE | 0.81626 | -0.83654 | -0.38025 | 0.74638 | 0.31562 | 0.10268 | 0.43077 | 0.1958 | 0.84797 | 0.84831 | 0.8538 | 0.032091 | 0.055291 | 1.0025 |  |  | insufficient_history
2830 | Walter C Beckjord | TRUE | <1.5h | CS | 4 | 82 | 82 | TRUE | 0.71279 | 0.017874 | 0.44685 | 0.016292 | 0.04516 | 0.055261 | -0.028869 | -0.72171 | 0.68197 | 0.67016 | 0.73205 | 0.076628 | 0.069843 | 0.0069369 | 2.0041 | 22.4372 | ok
6304 | Kotzebue Hybrid | TRUE | <1.5h | CT | 1.2 | 33 | 33 | TRUE | 0.72944 | -0.00049887 | -0.041573 | -0.00048967 | -0.00050489 | -0.00050432 | 1.5223e-05 | 0.0012686 | 0.8481 | 0.92778 | 1 | 0.68875 | 0.036676 | 6.0233e-05 | -7.2631 | -23.9474 | ok
6377 | Ocracoke Hybrid | TRUE | <1.5h | CS | 1 | 16 | 16 | TRUE | 0.8846 | 0.0014522 | 0.14522 | 0.0031824 | 0.0028164 | 0.0012431 | 0.00036604 | 0.036604 | 0.81098 | 0.52479 | 0.81818 | 0.17808 | 0.12474 | 0.00083383 |  |  | ok
8063 | DeCordova Steam Electric Station | FALSE | <1.5h | CS | 269.1 | 36 | 36 | FALSE | 2.1061 | 4.1019 | 1.5243 | 4.6006 | 3.4431 | 2.624 | 1.1575 | 0.43014 | 0.64955 | 0.66292 | 0.65858 | 0.3792 | 0.24481 | 0.9001 | 21.5781 | 123.6667 | ok
10156 | Fresno Cogen Partners | FALSE | <1.5h | CS | 16 | 15 | 15 | FALSE | 0.36808 | -0.0045298 | -0.028311 | -0.0020478 | -0.0034359 |  | 0.0013881 | 0.0086755 | 0.38469 | 0.29026 | 0.39286 | 0.13964 | 0.11803 | 0.0031185 |  |  | ok
10444 | Lockhart Solar PV, LLC | TRUE | <1.5h | CS | 69 | 3 |  | FALSE | [9 empty] | 0.66057 | [6 empty] | insufficient_history
10493 | Rumford Falls Hydro Facility | FALSE | 1.5-2.5h | CS | 8 | 24 | 24 | TRUE | 0.8457 | 0.063707 | 0.79634 | 0.077688 | 0.034499 | -0.01242 | 0.043189 | 0.53987 | 0.79413 | 0.79438 | 0.78813 | 0.10566 | 0.052294 | 0.039517 | -12.3101 | -118.4463 | ok
50064 | University of California Santa Cruz | TRUE | <1.5h | CS | 1 | 22 | 22 | TRUE | 0.9279 | 0.00086671 | 0.086671 | 0.0011608 | 0.0012267 | -0.00015206 | -6.5954e-05 | -0.0065954 | 0.88761 | 0.87969 | 0.90238 | 0.3116 | 0.033474 | 0.00028806 |  |  | ok
50300 | VESI Pomona | FALSE | <1.5h | BL | 40 | 84 | 84 | TRUE | 0.9922 | 0.38754 | 0.96886 | 0.37841 | 0.3804 | 0.40519 | -0.0019866 | -0.0049666 | 0.85988 | 0.85019 | 0.87012 | 0.6703 | 0.01472 | 0.030015 | -1.1975 | 10.0174 | ok
54134 | Great Lakes Hydro America - ME | FALSE | <1.5h | CS | 20 | 36 | 36 | TRUE | 0.88399 | 0.10614 | 0.53069 | 0.060658 | 0.082141 | 0.11624 | -0.021483 | -0.10742 | 0.80608 | 0.80198 | 0.80857 | 0.36365 | 0.027819 | 0.024079 | -0.94561 | -6.9196 | ok
54296 | Biola University Hybrid | TRUE | 1.5-2.5h | CS | 0.3 | 65 | 65 | TRUE | 0.85003 | 0.00025954 | 0.086512 | 0.00036146 | 0.00025847 | 0.00025761 | 0.00010298 | 0.034328 | 0.80193 | 0.79077 | 0.85714 | 0.028644 | 0.098763 | 0.00019042 | -3.4933 | 26.1669 | ok
54639 | Berlin Gorham | FALSE | <1.5h | CS | 14 | 24 | 24 | TRUE | 0.90483 | 0.072447 | 0.51748 | 0.076748 | 0.066961 | 0.073281 | 0.0097865 | 0.069903 | 0.85068 | 0.8499 | 0.84867 | 0.39217 | 0.01918 | 0.019229 | 2.8996 | 28.1787 | ok
55370 | Green Mountain Storage, LLC | FALSE | <1.5h | CT | 10.4 | 17 | 17 | TRUE | 0.88713 | 0.076314 | 0.73379 | 0.068857 | 0.076113 | 0.072597 | -0.0072561 | -0.06977 | 0.83924 | 0.75598 | 0.844 | 0.9797 | 0.010332 | 0.0028366 |  |  | insufficient_history
56961 | Notrees Windpower Hybrid | FALSE | <1.5h | BL | 36 | 77 | 77 | FALSE | 1.1042 | 0.3549 | 0.98583 | 0.36822 | 0.38927 | 0.27497 | -0.021055 | -0.058487 | 0.74991 | 0.68079 | 0.76326 | 0.59672 | 0.055561 | 0.033689 | -1.3547 | -5.3582 | ok
56981 | Pyron Wind Farm LLC Hybrid | TRUE | <1.5h | CS | 9.9 | 71 | 71 | TRUE | 0.97322 | 0.16196 | 1.6359 | 0.17347 | 0.13898 | 0.16972 | 0.034491 | 0.34839 | 0.73911 | 0.64322 | 0.78827 | 0.37685 | 0.074614 | 0.025072 | -1.4886 | 30.1354 | ok
56984 | Inadale Wind Farm LLC Hybrid | FALSE | <1.5h | CS | 9.9 | 32 | 32 | TRUE | 0.77548 | 0.070319 | 0.71029 | 0.068983 | 0.070811 | 0.069418 | -0.001828 | -0.018465 | 0.54181 | 0.50406 | 0.52642 | 0.72761 | 0.082795 | 0.0078553 | 7.0112 | 10.5973 | ok
57206 | Soldotna | FALSE | 1.5-2.5h | CS | 46.5 | 36 | 36 | FALSE | 1.1293 | 0.15811 | 0.34002 | 0.14293 | 0.12949 | 0.13677 | 0.013436 | 0.028894 | 0.75278 | 0.74966 | 0.74258 | 0.68769 | 0.052941 | 0.018273 |  |  | ok
57242 | Mililani South Solar Farm | TRUE | 2.5-4.5h | CS | 39 | 30 | 30 | TRUE | 0.92127 | 0.067978 | 0.1743 | 0.068511 | 0.058132 | 0.13793 | 0.010379 | 0.026614 | 0.91168 | 0.91288 | 0.97299 | 0.033695 | 0.026499 | 0.068796 | -8.8823 | 107.7069 | ok
57325 | FPL Energy Illinois Wind LLC Hybrid | TRUE | <1.5h | CS | 20 | 83 | 83 | TRUE | 0.89811 | 0.0058536 | 0.029268 | 0.11347 | 0.081981 | 0.0017647 | 0.031486 | 0.15743 | 0.93624 | 0.90938 | 0.87361 | 0.030211 | 0.01958 | 0.003685 | -0.73845 | 31.6001 | ok
57447 | Laurel Mountain Hybrid | FALSE | <1.5h | CS | 16 | 77 | 77 | TRUE | 0.80524 | 0.21454 | 1.3409 | 0.24158 | 0.17992 | 0.17057 | 0.061662 | 0.38539 | 0.70183 | 0.69513 | 0.70235 | 0.37989 | 0.028546 | 0.031651 | -3.8966 | -28.4876 | ok
57560 | Chino Valley Solar | TRUE | 2.5-4.5h | CS | 19 | 23 | 23 | TRUE | 0.91859 | 0.18413 | 0.96913 | 0.31868 | 0.24826 | 0.18855 | 0.070426 | 0.37066 | 0.84998 | 0.79353 | 0.85344 | 0.98778 | 0.0086241 | 0.0044697 | -3.4265 | -57.0148 | ok
57561 | Cotton Center Solar Hybrid | TRUE | 2.5-4.5h | CS | 17 | 24 | 24 | TRUE | 0.86715 | 0.08643 | 0.50841 | 0.13586 | 0.073402 | 0.056232 | 0.062456 | 0.36739 | 0.82954 | 0.82986 | 0.83371 | 0.030485 | 0.06324 | 0.10392 | -0.83474 | -29.6936 | ok
57562 | Paloma Solar Hybrid | TRUE | 2.5-4.5h | CS | 17 | 24 | 24 | TRUE | 0.85475 | 0.059303 | 0.34884 | 0.12949 | 0.067748 | 0.0629 | 0.061737 | 0.36316 | 0.82998 | 0.83029 | 0.83177 | 0.017992 | 0.055321 | 0.093407 | -7.3065 | -153.1079 | ok
57563 | Hyder Solar Hybrid | TRUE | 2.5-4.5h | CS | 16 | 24 | 24 | TRUE | 0.97373 | 0.25363 | 1.5852 | 0.23062 | 0.18095 | 0.18323 | 0.049674 | 0.31046 | 0.83587 | 0.83464 | 0.83554 | 0.43118 | 0.042456 | 0.062107 |  |  | ok
57583 | Battery Energy Storage System | FALSE | <1.5h | BL | 40 | 2 |  | FALSE | [9 empty] | 0.092839 | [6 empty] | insufficient_history
57584 | University of California San Diego Hybri | FALSE | 1.5-2.5h | CS | 2.5 | 76 | 76 | TRUE | 0.84818 | -0.00030282 | -0.012113 | -0.00035254 | 0.0026188 | 0.0026418 | -0.0029713 | -0.11885 | 0.86149 | 0.85566 | 0.86254 | 0.07749 | 0.0075713 | 0.00012146 | -1.1209 | -18.0885 | ok
57996 | Auwahi Wind Energy Hybrid | FALSE | <1.5h | CS | 11 | 36 | 36 | FALSE | 1.1137 | 0.025302 | 0.23002 | 0.033952 | 0.032133 | 0.026788 | 0.0018186 | 0.016533 | 0.91321 | 0.90603 | 0.93578 | 0.3073 | 0.058405 | 0.0065148 |  |  | ok
57997 | Foothills Solar Plant Hybrid | TRUE | 2.5-4.5h | CS | 35 | 24 | 24 | TRUE | 0.93541 | 0.4883 | 1.3951 | 0.57468 | 0.43106 | 0.36186 | 0.14362 | 0.41034 | 0.81324 | 0.81269 | 0.8148 | 0.33619 | 0.049399 | 0.14629 |  |  | ok
58236 | Marshalltown Generating Station | TRUE | 1.5-2.5h | CS | 0.3 | 36 | 36 | TRUE | 0.89339 | -0.00011521 | -0.038402 | -0.0001534 | -0.00041295 | 8.6439e-05 | 0.00025954 | 0.086515 | 0.90092 | 0.90779 | 0.91667 | 0.037764 | 0.017052 | 9.9733e-05 | -7.5456 | -169.8884 | ok
58256 | Los Alamos PV Site | TRUE | >4.5h | CS | 1.8 | 2 |  | FALSE | [9 empty] | 0.32094 | [6 empty] | insufficient_history
58383 | Hyder II Hybrid | TRUE | 2.5-4.5h | CS | 14 | 24 | 24 | TRUE | 0.997 | 0.26853 | 1.9181 | 0.2309 | 0.19728 | 0.19904 | 0.033621 | 0.24015 | 0.8296 | 0.82856 | 0.82834 | 0.50632 | 0.043383 | 0.056532 | -1.2734 | -8.9529 | ok
58462 | McCoy Solar Energy Project Hybrid | TRUE | 2.5-4.5h | CS | 230 | 33 | 33 | TRUE | 0.92817 | 0.6154 | 0.26756 | 0.63006 | 0.27353 | 0.50469 | 0.35653 | 0.15501 | 0.90768 | 0.85634 | 0.9105 | 0.09387 | 0.016755 | 0.3434 | -2.6035 | -151.5059 | ok
58585 | Sierra Nevada Brewing Co Hybrid | TRUE | 1.5-2.5h | CS | 0.5 | 29 | 29 | TRUE | 0.80218 | 0.00035967 | 0.071934 | 0.00021759 | 0.00016685 | 0.00060344 | 5.0736e-05 | 0.010147 | 0.78238 | 0.68438 | 0.75 | 0.050417 | 0.094765 | 0.0003004 | 1.8298 | -7.1028 | ok
58639 | KRS I Anahola Solar Hybrid | TRUE | <1.5h | CS | 6 | 3 |  | FALSE | [9 empty] | 0.10738 | [6 empty] | insufficient_history
59020 | Gila Bend Hybrid | TRUE | 2.5-4.5h | CS | 32 | 24 | 24 | TRUE | 0.84217 | 0.072494 | 0.22654 | 0.20345 | 0.12593 | 0.076953 | 0.077527 | 0.24227 | 0.82534 | 0.81792 | 0.82701 | 0.90464 | 0.0054776 | 0.005018 | -9.445 | -101.7834 | ok
59118 | Cameron Wind 1 LLC | FALSE | 1.5-2.5h | CS | 16.4 | 23 | 23 | TRUE | 0.76003 | 0.0089563 | 0.054612 | -0.07158 | 0.00711 | 0.0051494 | -0.07869 | -0.47982 | 0.76615 | 0.74328 | 0.77035 | 0.031708 | 0.053305 | 0.0108 | 1.1641 | 93.8256 | ok
59150 | RE Mustang LLC | TRUE | <1.5h | CS | 75 | 36 | 36 | TRUE | 0.85916 | 0.017245 | 0.022994 | 0.15512 | 0.082581 | 0.019687 | 0.072541 | 0.096722 | 0.85927 | 0.85774 | 0.85843 | 0.01008 | 0.0056528 | 0.029309 | -1.3948 | -110.47 | ok
59256 | Vaca Dixon Battery Storage System | FALSE | >4.5h | CS | 2 | 10 | 10 | TRUE | 0.77365 | 0.067801 | 3.39 |  | 0.054838 | 0.032938 |  |  | 0.47364 | 0.29941 | 0.47758 | 0.47985 | 0.33876 | 0.024958 |  |  | ok
59257 | Yerba Buena | FALSE | >4.5h | CS | 4 | 15 | 15 | TRUE | 0.65786 | 0.17232 | 4.3079 | 0.15984 | 0.18526 |  | -0.02542 | -0.6355 | 0.46577 | 0.35477 | 0.41727 | 0.51999 | 0.22074 | 0.045918 |  |  | insufficient_history
59444 | Desert Star Hybrid | TRUE | 2.5-4.5h | CS | 10 | 24 | 24 | TRUE | 0.931 | 0.14655 | 1.4655 | 0.13457 | 0.10159 | 0.094021 | 0.032981 | 0.32981 | 0.82692 | 0.82667 | 0.82691 | 0.27725 | 0.046999 | 0.050447 | -7.3092 | -72.0418 | ok
59871 | Desert Quartzite | TRUE | <1.5h | CS | 150 | 13 | 13 | TRUE | 0.98194 | 2.0627 | 1.3751 | 1.8307 | 1.2239 | 1.3152 | 0.60681 | 0.40454 | 0.87088 | 0.86352 | 0.8539 | 0.44509 | 0.051303 | 0.69441 |  |  | insufficient_history
59939 | RE Tranquillity | TRUE | 2.5-4.5h | CS | 72 | 36 | 36 | TRUE | 0.93866 | 0.64574 | 0.89687 | 0.63703 | 0.62954 | 0.65895 | 0.0074883 | 0.0104 | 0.86625 | 0.86019 | 0.86897 | 0.74565 | 0.010756 | 0.064679 | -0.36223 | -9.4639 | ok
59949 | AES Warrior Run Energy Storage Project | FALSE | <1.5h | BL | 11 | 64 | 64 | TRUE | 0.83581 | 0.042279 | 0.38435 | 0.083748 | 0.041333 | 0.050541 | 0.042415 | 0.38559 | 0.80945 | 0.80291 | 0.80968 | 0.54889 | 0.0076136 | 0.0048677 | 0.72608 | 16.9949 | ok
59957 | Grand Ridge Battery Projects | TRUE | <1.5h | CT | 36 | 18 | 18 | FALSE | 0.42024 | -0.14299 | -0.3972 | -0.46627 | -0.14975 |  | -0.31652 | -0.87921 | 0.51229 | 0.21619 | 0.35849 | 0.0065877 | 0.66083 | 0.43898 |  |  | ok
59959 | Elwood Energy Storage Center | FALSE | <1.5h | CS | 19.8 | 34 | 34 | TRUE | 0.80433 | 0.075531 | 0.38147 | 0.10925 | 0.07436 | 0.091645 | 0.034888 | 0.1762 | 0.74801 | 0.67531 | 0.68111 | 0.93856 | 0.019378 | 0.0034163 | -5.855 | -29.1572 | ok
59960 | Jake Energy Storage Center | FALSE | <1.5h | CS | 19.8 | 24 | 24 | TRUE | 0.82503 | 0.074112 | 0.3743 | 0.082894 | 0.067251 | 0.073205 | 0.015643 | 0.079003 | 0.71521 | 0.52155 | 0.71698 | 0.96759 | 0.027342 | 0.0028918 | 14.6823 | 115.4076 | ok
59993 | Babcock Solar Energy Center Hybrid | TRUE | 2.5-4.5h | CS | 10 | 65 | 65 | TRUE | 0.73129 | 0.029433 | 0.29433 | 0.038589 | 0.024512 | 0.031021 | 0.014077 | 0.14077 | 0.74345 | 0.61317 | 0.76786 | 0.28188 | 0.05593 | 0.0059187 | -0.99052 | 23.349 | ok
60014 | Manatee Solar Energy Center | TRUE | 1.5-2.5h | CS | 409 | 43 | 43 | TRUE | 0.81905 | 1.6858 | 0.41217 | 2.188 | 1.3856 | 2.0706 | 0.80235 | 0.19617 | 0.68416 | 0.60418 | 0.65278 | 0.47491 | 0.098944 | 0.27683 | 8.1847 | -30.3607 | ok
60016 | MESA 1 | FALSE | <1.5h | CS | 2 | 6 |  | FALSE | [9 empty] | 0.69408 | [6 empty] | insufficient_history
60061 | Citrus Solar Energy Center Hybrid | TRUE | 2.5-4.5h | CS | 4 | 82 | 82 | TRUE | 0.8843 | -0.00082767 | -0.020692 | -0.0026579 | -0.00074602 | 0.0027539 | -0.0019119 | -0.047798 | 0.9106 | 0.88461 | 0.92489 | 0.0068744 | 0.020677 | 0.0011122 | -2.9521 | 19.0703 | ok
60092 | Blythe Solar II, LLC | TRUE | >4.5h | CS | 115 | 57 | 57 | TRUE | 0.94801 | 0.80332 | 0.69854 | 0.54346 | 0.85808 | 1.3647 | -0.31462 | -0.27358 | 0.88979 | 0.88554 | 0.90386 | 0.26225 | 0.020698 | 0.18168 | 0.14097 | -23.8238 | ok
60093 | Blythe Solar 110, LLC | TRUE | >4.5h | CS | 63 | 36 | 36 | TRUE | 0.92316 | 0.37724 | 0.59879 | 0.60582 | 0.56582 | 0.40487 | 0.040002 | 0.063496 | 0.8883 | 0.88768 | 0.88568 | 0.15111 | 0.018096 | 0.15334 | 3.2831 | 79.3429 | ok
60094 | Blythe Solar III, LLC Hybrid | TRUE | >4.5h | CS | 115 | 51 | 51 | TRUE | 0.9293 | 0.71105 | 0.61831 | 0.63586 | 0.84646 | 1.3174 | -0.2106 | -0.18313 | 0.88207 | 0.87691 | 0.89214 | 0.21175 | 0.021595 | 0.19599 | -1.3007 | -79.1371 | ok
60095 | Blythe Solar IV, LLC | TRUE | <1.5h | CS | 47 | 35 | 35 | TRUE | 0.83788 | 0.026572 | 0.056537 | 0.24922 | 0.28757 | 0.032908 | -0.038351 | -0.081598 | 0.84086 | 0.82004 | 0.84533 | 0.058027 | 0.014638 | 0.018637 | -3.1368 | -142.6497 | ok
60123 | Castle Gap Solar Hybrid | TRUE | 2.5-4.5h | CS | 9.9 | 61 | 61 | TRUE | 0.57006 | -0.068495 | -0.69187 | -0.21879 | -0.065461 | -0.14227 | -0.15333 | -1.5488 | 0.56768 | 0.63054 | 0.85298 | 0.038134 | 0.10625 | 0.044785 | 6.1909 | -68.0358 | ok
60231 | Genentech-Oceanside Hybrid | TRUE | <1.5h | CS | 2 | 28 | 28 | TRUE | 0.80088 | 0.0028783 | 0.14391 | 0.0020241 | 0.00285 | 0.0073501 | -0.00082586 | -0.041293 | 0.79826 | 0.76576 | 0.8 | 0.81549 | 0.011635 | 0.0002685 | -0.63472 | 96.1605 | ok
60233 | RE Garland | TRUE | 2.5-4.5h | CS | 88 | 36 | 36 | TRUE | 0.91388 | 0.425 | 0.48296 | 0.43473 | 0.28413 | 0.26733 | 0.15061 | 0.17115 | 0.87441 | 0.86901 | 0.87555 | 0.50699 | 0.011263 | 0.071875 | -0.81304 | -18.1153 | ok
60297 | Clinton Battery | FALSE | <1.5h | CS | 10 | 30 | 30 | TRUE | 0.82437 | 0.033484 | 0.33484 | 0.032622 | 0.03061 | 0.033492 | 0.0020116 | 0.020116 | 0.72474 | 0.7252 | 0.72929 | 0.38171 | 0.087892 | 0.0080536 | -9.6279 | 20.2992 | ok
60316 | Scott Solar Farm | TRUE | <1.5h | CS | 40 | 21 | 21 | TRUE | 0.81884 | 0.017842 | 0.044606 | 0.046777 | 0.019142 | 0.04127 | 0.027636 | 0.069089 | 0.80109 | 0.75453 | 0.79583 | 0.38949 | 0.023062 | 0.0051248 | 1.0212 | 74.9105 | ok
60390 | Beech Ridge Energy Storage | TRUE | <1.5h | CT | 31.5 | 22 | 22 | FALSE | 0.43691 | -0.012277 | -0.038976 | -0.012439 | -0.14394 | 0.42142 | 0.1315 | 0.41746 | 0.42195 | 0.28164 | 0.37862 | 0.029484 | 0.17985 | 0.015751 |  |  | ok
60441 | Salem Smart Power Center | TRUE | <1.5h | BL | 5 | 2 |  | FALSE | [9 empty] | 0.13566 | [6 empty] | insufficient_history
60467 | Red Rock | TRUE | 2.5-4.5h | CS | 41 | 12 | 12 | TRUE | 0.91854 | 0.14349 | 0.34998 | 0.17943 | 0.16057 |  | 0.018865 | 0.046011 | 0.89235 | 0.82994 | 0.89334 | 0.23323 | 0.018997 | 0.082276 |  |  | insufficient_history
60491 | Springbok 3 Solar Farm Hybrid | TRUE | <1.5h | CT | 1.5 | 10 | 10 | TRUE | 0.8607 | -0.00015117 | -0.010078 |  | 0.00077659 | -0.00050824 |  |  | 0.86029 | 0.88773 | 0.9 | 0.061439 | 0.052207 | 0.00020889 |  |  | insufficient_history
60506 | ETT Presidio NaS Battery | TRUE | <1.5h | BL | 4 | 45 | 45 | TRUE | 0.86844 | -0.00050212 | -0.012553 | -0.00048155 | 9.0043e-05 | -0.0032318 | -0.0005716 | -0.01429 | 0.88391 | 0.88427 | 0.86047 | 0.067349 | 0.020786 | 0.00028495 | 1.3123 | 65.6391 | ok
60518 | Stafford Hill Solar Hybrid | TRUE | 1.5-2.5h | CS | 2 | 13 | 13 | FALSE | 1.1512 | -0.0019823 | -0.099117 | 0.074356 | 0.0064554 | -0.0014013 | 0.0679 | 3.395 | 2.4572 | 0.77354 | 1.3036 | 0.042055 | 0.19724 | 0.0028526 |  |  | insufficient_history
60546 | KIUC Kapaia PV and BA Storage Project Hy | TRUE | 2.5-4.5h | CS | 13 | 36 | 36 | TRUE | 0.90671 | 0.041256 | 0.31736 | 0.039032 | 0.037318 | 0.041624 | 0.0017141 | 0.013186 | 0.88693 | 0.88635 | 0.88689 | 0.18104 | 0.0093876 | 0.015049 | 0.73524 | 35.9652 | ok
60562 | GMP Solar - Panton Hybrid | TRUE | 2.5-4.5h | OT | 1 | 71 | 71 | FALSE | 1.6267 | 0.02326 | 2.326 | 0.02085 | 0.024963 | 0.021651 | -0.0041133 | -0.41133 | 1.1752 | 0.76864 | 1.5217 | 0.041305 | 0.16836 | 0.01349 | 5.6833 | 32.395 | ok
60565 | Borrego Springs Energy Storage | TRUE | 2.5-4.5h | CS | 1.5 | 21 | 21 | TRUE | 0.60141 | -0.00090114 | -0.060076 | 0.00069362 | -0.00086828 | -0.00032477 | 0.0015619 | 0.10413 | 0.625 | 0.6442 | 0.6087 | 0.53629 | 0.03287 | 0.00019224 |  |  | ok
60566 | Pala Energy Storage Yard | TRUE | 1.5-2.5h | CS | 1 | 12 | 12 | TRUE | 0.92925 | 0.084451 | 8.4451 | 0.12739 | 0.10248 | 0.095138 | 0.024918 | 2.4918 | 0.88273 | 0.87981 | 0.88008 | 0.51019 | 0.019939 | 0.026167 |  |  | insufficient_history
60567 | Ortega Highway Energy Storage | TRUE | 2.5-4.5h | CS | 2 | 6 |  | FALSE | [9 empty] | 0.63095 | [6 empty] | insufficient_history
60568 | Canyon Crest Academy | TRUE | 2.5-4.5h | CS | 1 | 8 |  | FALSE | [9 empty] | 0.73077 | [6 empty] | insufficient_history
60569 | El Cajon Energy Storage | FALSE | 2.5-4.5h | CS | 7.5 | 83 | 83 | TRUE | 0.91281 | 0.032769 | 0.43692 | 0.034514 | 0.033773 | 0.029898 | 0.00074168 | 0.0098891 | 0.86193 | 0.85301 | 0.86 | 0.63522 | 0.0086649 | 0.0027592 | 0.66515 | 9.2678 | ok
60570 | Escondido Energy Storage | FALSE | 2.5-4.5h | CS | 30 | 68 | 68 | TRUE | 0.90928 | 0.10812 | 0.36039 | 0.091866 | 0.13036 | 0.09126 | -0.038497 | -0.12832 | 0.87824 | 0.86094 | 0.87883 | 0.63637 | 0.0064323 | 0.01006 | 1.301 | 18.9664 | ok
60607 | CMEEC - Polaris Park Solar Hybrid | TRUE | 2.5-4.5h | CS | 0.8 | 21 | 21 | TRUE | 0.81112 | 0.0016292 | 0.20366 | 0.0034365 | 0.0043914 | -0.00038973 | -0.00095492 | -0.11937 | 0.76296 | 0.56871 | 1 | 0.033445 | 0.23617 | 0.0020094 |  |  | ok
60609 | CMEEC - Norwich Stott St Solar Hybrid | TRUE | 2.5-4.5h | CS | 0.8 | 20 | 20 | TRUE | 0.7044 | -0.00036458 | -0.045572 | -0.00027581 | 0.00046032 | 0.0034823 | -0.00073613 | -0.092016 | 0.74359 | 0.73805 | 0.75962 | 0.032788 | 0.095056 | 0.00046672 |  |  | insufficient_history
60641 | Henrietta D Energy Storage LLC | FALSE | 2.5-4.5h | CS | 10 | 18 | 18 | TRUE | 0.88452 | 0.10351 | 1.0351 | 0.13367 | 0.097642 | 0.10204 | 0.036027 | 0.36027 | 0.81153 | 0.75991 | 0.81533 | 0.89824 | 0.012962 | 0.0087103 |  |  | ok
60649 | Rabbit Hill Energy Storage Project | FALSE | <1.5h | CS | 9.9 | 31 | 31 | TRUE | 0.90942 | 0.079183 | 0.79983 | 0.089788 | 0.088257 | 0.062665 | 0.0015314 | 0.015468 | 0.65666 | 0.57943 | 0.63874 | 0.73525 | 0.070217 | 0.0088233 | -4.2378 | -13.7081 | ok
60654 | Townsite Solar Project Hybrid | TRUE | 2.5-4.5h | CS | 90 | 48 | 48 | TRUE | 0.84491 | -0.24226 | -0.26917 | 0.15877 | -0.15738 | -0.16797 | 0.31615 | 0.35128 | 0.8609 | 0.86192 | 0.86165 | 0.067142 | 0.013088 | 0.13314 | 0.59411 | 46.2037 | ok
60656 | McHenry Battery Storage | FALSE | <1.5h | CS | 20 | 13 | 13 | TRUE | 0.89847 | 0.059361 | 0.29681 | 0.073571 | 0.057869 | 0.080833 | 0.015702 | 0.078509 | 0.88599 | 0.8851 | 0.88797 | 0.33359 | 0.0075066 | 0.025297 |  |  | insufficient_history
60660 | Willey Battery Utility | FALSE | <1.5h | CS | 6 | 33 | 33 | TRUE | 0.82412 | 0.0096049 | 0.16008 | 0.0029627 | 0.035366 | 0.03051 | -0.032404 | -0.54006 | 0.82071 | 0.81287 | 0.82803 | 0.18314 | 0.024357 | 0.0036433 | 0.4686 | 15.816 | ok
60661 | Mira Loma Energy Storage Facility | FALSE | 2.5-4.5h | CS | 20 | 24 | 24 | TRUE | 0.88062 | 0.057217 | 0.28609 | 0.056765 | 0.079982 | 0.13409 | -0.023217 | -0.11609 | 0.85367 | 0.83324 | 0.85093 | 0.6698 | 0.01861 | 0.008565 | 4.8364 | 115.5094 | ok
60690 | Blue Summit Storage, LLC | FALSE | <1.5h | CS | 30 | 84 | 84 | TRUE | 0.87195 | 0.1476 | 0.49201 | 0.14296 | 0.14361 | 0.18027 | -0.00064278 | -0.0021426 | 0.79917 | 0.78155 | 0.7903 | 0.72119 | 0.012161 | 0.010135 | -2.8372 | -25.5025 | ok
60698 | Stanton Energy Reliability Center Hybrid | TRUE | <1.5h | CS | 20 | 33 | 33 | FALSE | 0.43863 | -0.00040987 | -0.0020493 | -0.0087522 | -0.0096998 | -0.00079697 | 0.00094768 | 0.0047384 | 0.43426 | 0.3611 | 0.41818 | 0.0022354 | 0.13486 | 0.0015552 |  |  | ok
60760 | PPA Grand | FALSE | 2.5-4.5h | BL | 2 | 15 | 15 | TRUE | 0.78976 | 0.011445 | 0.57223 | 0.011431 | 0.012042 | 0.01609 | -0.00061042 | -0.030521 | 0.68491 | 0.59465 | 0.60976 | 0.84291 | 0.070792 | 0.0013703 |  |  | insufficient_history
60815 | Hampshire College Hybrid | TRUE | <1.5h | CS | 1 | 25 | 25 | TRUE | 0.68184 | 0.0014605 | 0.14605 | 0.0011096 | 0.0025969 | 0.0030639 | -0.0014873 | -0.14873 | 0.61472 | 0.51503 | 0.6 | 0.29221 | 0.12021 | 0.00047395 | -4.1516 | 76.2003 | ok
60906 | Mt. Tom Solar Project Hybrid | TRUE | 1.5-2.5h | CS | 3.1 | 29 | 29 | TRUE | 0.85148 | 0.01608 | 0.5187 | 0.015808 | 0.015867 | 0.019085 | -5.9389e-05 | -0.0019158 | 0.64771 | 0.57745 | 0.625 | 0.82082 | 0.05067 | 0.0014458 | -9.4049 | -41.7658 | ok
60959 | Chocksett Rd Energy Storage Project | TRUE | 1.5-2.5h | CS | 2 | 24 | 24 | TRUE | 0.61144 | 0.0053094 | 0.26547 | 0.0052985 | 0.0074262 | 0.010295 | -0.0021277 | -0.10639 | 0.5376 | 0.50937 | 0.51923 | 0.11397 | 0.21138 | 0.0031562 |  |  | ok
60974 | Glendale Battery Energy Storage System | TRUE | <1.5h | CS | 2 | 1 |  | FALSE | [9 empty] | 1 | [6 empty] | insufficient_history
60996 | Iron Horse Battery Storage Hybrid | TRUE | <1.5h | CS | 10 | 12 | 12 | TRUE | 0.82869 | 0.066954 | 0.66954 | 0.072101 | 0.065329 | 0.06002 | 0.0067717 | 0.067717 | 0.52901 | 0.52623 | 0.53763 | 0.79301 | 0.11534 | 0.010817 |  |  | insufficient_history
61068 | AES Lawai Solar Hybrid | TRUE | >4.5h | CS | 20 | 70 | 70 | TRUE | 0.99442 | 0.020298 | 0.10149 | 0.0032111 | 0.020793 | 0.016978 | -0.017582 | -0.087912 | 0.97348 | 0.97195 | 0.97829 | 0.59019 | 0.0063508 | 0.0020512 | -0.23917 | -5.1083 | ok
61098 | Battle Mountain Solar Project | TRUE | <1.5h | CS | 25 | 54 | 54 | TRUE | 0.92801 | -0.0040173 | -0.016069 | -0.0046795 | -0.015378 | 0.042741 | 0.010698 | 0.042793 | 0.92884 | 0.91855 | 0.94161 | 0.0016559 | 0.011021 | 0.013679 | -0.63077 | 6.9559 | ok
61107 | Vanadium Redox Flow Battery Plant | TRUE | 2.5-4.5h | CS | 2 | 23 | 23 | TRUE | 0.68766 | 0.12073 | 6.0364 | 0.11246 | 0.12328 | 0.11696 | -0.010817 | -0.54085 | 0.48739 | 0.39402 | 0.50437 | 0.85568 | 0.066273 | 0.010819 | 2.4203 | 19.3976 | ok
61168 | Eland Solar & Storage Center, Phase 1 Hy | TRUE | 2.5-4.5h | CS | 150 | 14 | 14 | TRUE | 0.91691 | 0.79714 | 0.53143 | 1.2127 | 0.89483 | 1.0534 | 0.31788 | 0.21192 | 0.88188 | 0.87958 | 0.88244 | 0.70814 | 0.0094168 | 0.14773 |  |  | insufficient_history
61169 | Eland Solar & Storage Center, Phase 2 Hy | TRUE | 2.5-4.5h | CS | 150 | 6 |  | FALSE | [9 empty] | 0.89284 | [6 empty] | insufficient_history
61186 | Boston Medical Center CHP Plant | FALSE | <1.5h | CS | 1 | 20 | 20 | TRUE | 0.69749 | 0.0005437 | 0.05437 | 0.00059987 | 0.00037575 |  | 0.00022412 | 0.022412 | 0.7382 | 0.60141 | 0.67614 | 0.11413 | 0.1032 | 0.00035703 |  |  | ok
61197 | Pima Energy Storage System | TRUE | <1.5h | CS | 10 | 8 |  | FALSE | [9 empty] | 0.14559 | [6 empty] | insufficient_history
61204 | AES ES Alamitos, LLC | FALSE | 2.5-4.5h | BL | 100 | 60 | 60 | TRUE | 0.94552 | 0.99627 | 0.99627 | 1.0058 | 0.93049 | 0.97982 | 0.075326 | 0.075326 | 0.87779 | 0.8735 | 0.87991 | 0.49434 | 0.012226 | 0.13231 | -0.19589 | -3.1301 | ok
61334 | Volkman Road Solar Array Hybrid | TRUE | >4.5h | CT | 1 | 22 | 22 | TRUE | 0.90287 | -0.00016941 | -0.016941 | -0.00030993 | -0.00018549 | 0.00091388 | -0.00012444 | -0.012444 | 0.91045 | 0.9205 | 0.91864 | 0.084642 | 0.01987 | 0.00012458 | -0.3436 | -84.5356 | ok
61365 | Fallbrook Energy Storage | FALSE | <1.5h | CS | 40 | 30 | 30 | TRUE | 0.83293 | 0.20466 | 0.51164 | 0.19476 | 0.24069 | 0.24156 | -0.045934 | -0.11484 | 0.80188 | 0.79676 | 0.79788 | 0.46217 | 0.01305 | 0.041722 | 1.3266 | 16.2926 | ok
61366 | Top Gun Energy Storage | FALSE | 2.5-4.5h | CS | 30 | 53 | 53 | TRUE | 0.90905 | 0.28396 | 0.94654 | 0.28485 | 0.29235 | 0.26934 | -0.0075043 | -0.025014 | 0.82993 | 0.80617 | 0.82448 | 0.54878 | 0.016856 | 0.036056 | 0.083991 | -4.8994 | ok
61431 | Beacon BESS 1 | TRUE | <1.5h | CS | 20 | 76 | 76 | TRUE | 0.74977 | 0.063687 | 0.31843 | 0.073099 | 0.04963 | 0.023358 | 0.023469 | 0.11735 | 0.64532 | 0.63963 | 0.66387 | 0.22412 | 0.053942 | 0.013775 | -4.9757 | -23.4022 | ok
61552 | Fort Detrick Solar PV | TRUE | <1.5h | CS | 6 | 20 | 20 | TRUE | 0.85035 | 0.00078915 | 0.013153 | 0.028048 | 0.004112 |  | 0.023936 | 0.39894 | 0.85194 | 0.85003 | 0.85499 | 0.0011855 | 0.015143 | 0.0053991 |  |  | insufficient_history
61661 | Vista Energy Storage System | FALSE | <1.5h | BL | 40 | 84 | 84 | TRUE | 0.94202 | 0.27938 | 0.69845 | 0.275 | 0.30673 | 0.27376 | -0.031724 | -0.079309 | 0.85494 | 0.84268 | 0.84075 | 0.54866 | 0.014268 | 0.027982 | 0.80819 | 16.1317 | ok
61667 | Wimauma Solar and Battery Storage | TRUE | 1.5-2.5h | CS | 40 | 8 |  | FALSE | [9 empty] | 0.71136 | [6 empty] | insufficient_history
61678 | Pinal Central Energy Center Hybrid | TRUE | 2.5-4.5h | CS | 10 | 84 | 84 | FALSE | 1.0232 | 0.26109 | 2.6109 | 0.363 | 0.29431 | 0.28093 | 0.068689 | 0.68689 | 0.87523 | 0.87284 | 0.85983 | 0.088483 | 0.062582 | 0.092542 | -1.5434 | -29.2106 | ok
61721 | Baldwin (CA) | TRUE | >4.5h | CS | 1 | 72 | 72 | TRUE | 0.87837 | -0.00021785 | -0.021785 | -8.8896e-06 | -0.00037532 | -0.00018943 | 0.00036643 | 0.036643 | 0.88127 | 0.89077 | 0.88087 | 0.11163 | 0.0090888 | 7.3454e-05 | -1.3204 | -58.4017 | ok
61722 | HEBT Irvine 1 | FALSE | >4.5h | CS | 5.5 | 36 | 36 | TRUE | 0.856 | -0.0014965 | -0.027209 | -0.0013862 | -0.0015104 | -0.00243 | 0.00012423 | 0.0022587 | 0.85303 | 0.86473 | 0.8794 | 0.15379 | 0.0069101 | 0.00060204 | -4.0305 | -146.158 | ok
61723 | HEBT Irvine 2 | FALSE | >4.5h | CS | 5.8 | 36 | 36 | TRUE | 0.86091 | -0.00042987 | -0.0074115 | -0.00036369 | -0.0009025 | -0.0016281 | 0.00053881 | 0.0092898 | 0.8574 | 0.86364 | 0.8787 | 0.020379 | 0.0062042 | 0.00051113 | -2.5121 | -24.5437 | ok
61730 | MA Solar Storage 1 Hybrid | TRUE | 1.5-2.5h | CS | 1 | 36 | 36 | TRUE | 0.93197 | -0.00018915 | -0.018915 | -0.00017873 | -0.00015197 | 0.00060922 | -2.6762e-05 | -0.0026762 | 0.94376 | 0.95113 | 0.95644 | 0.13613 | 0.011875 | 8.1717e-05 | 1.2673 | -74.2756 | ok
61737 | Navy Yard Peaker Station | TRUE | <1.5h | CS | 6.2 | 12 | 12 | TRUE | 0.91971 | -0.0092706 | -0.14953 | 0.0064015 | 0.0018476 | -0.0039033 | 0.0045539 | 0.07345 | 0.92858 | 0.92878 | 0.92932 | 0.072616 | 0.012158 | 0.010477 |  |  | insufficient_history
61741 | Kingsberry Energy Storage System | TRUE | 1.5-2.5h | CS | 1.5 | 2 |  | FALSE | [9 empty] | 0.585 | [6 empty] | insufficient_history
61763 | Sunshine Gateway Solar Energy Center | TRUE | 2.5-4.5h | CS | 30 | 45 | 45 | TRUE | 0.87795 | 0.14 | 0.46666 | 0.29989 | 0.10291 | 0.12 | 0.19698 | 0.65659 | 0.79913 | 0.79241 | 0.81742 | 0.27873 | 0.045804 | 0.034344 | -0.43133 | -7.0693 | ok
61795 | Pacific Union College BESS | TRUE | 1.5-2.5h | CS | 1 | 12 | 12 | TRUE | 0.5901 | 0.001929 | 0.1929 | 0.003979 | 0.003244 | 0.0022742 | 0.00073501 | 0.073501 | 0.5045 | 0.37843 | 0.45804 | 0.049341 | 0.49561 | 0.0026775 |  |  | insufficient_history
61801 | Cascade Energy Storage, LLC | FALSE | 2.5-4.5h | CS | 25 | 14 | 14 | TRUE | 0.94958 | 0.4177 | 1.6708 | 0.41303 | 0.50544 |  | -0.092414 | -0.36965 | 0.84097 | 0.8381 | 0.83868 | 0.35931 | 0.05741 | 0.16101 |  |  | insufficient_history
61803 | Sierra Energy Storage, LLC | FALSE | 2.5-4.5h | CS | 10 | 4 |  | FALSE | [9 empty] | 0.90196 | [6 empty] | insufficient_history
61861 | AES ES GILBERT | TRUE | 2.5-4.5h | BL | 10 | 39 | 39 | TRUE | 0.87258 | 0.017088 | 0.17088 | 0.017961 | 0.046193 | 0.018598 | -0.028232 | -0.28232 | 0.86369 | 0.86259 | 0.85845 | 0.19363 | 0.01019 | 0.0057328 | -6.0612 | -121.8932 | ok
61891 | Stryker 22, L.L.C. | FALSE | <1.5h | CS | 19.8 | 83 | 83 | TRUE | 0.88438 | 0.087767 | 0.44327 | 0.12623 | 0.092586 | 0.065717 | 0.033644 | 0.16992 | 0.86897 | 0.86853 | 0.86754 | 0.16247 | 0.0053503 | 0.022141 | 0.10758 | 10.8461 | ok
61892 | Plumsted 537 LLC | FALSE | <1.5h | CS | 19.8 | 82 | 82 | TRUE | 0.87781 | 0.0098683 | 0.04984 | 0.010802 | -0.023974 | -0.041803 | 0.034776 | 0.17564 | 0.87577 | 0.87612 | 0.8719 | 0.0065055 | 0.0044675 | 0.013634 | -0.055184 | -17.0144 | ok
61901 | Redstone Arsenal Hybrid | TRUE | 1.5-2.5h | CS | 1 | 10 | 10 | TRUE | 0.8678 | 0.0012579 | 0.12579 | -0.00025948 | 0.00057123 |  | -0.00083071 | -0.083071 | 0.84808 | 0.81458 | 0.84352 | 0.98492 | 0.011761 | 5.5021e-05 |  |  | insufficient_history
61909 | Parkview Battery | FALSE | <1.5h | CS | 1.1 | 9 |  | FALSE | [9 empty] | 0.39608 | [6 empty] | insufficient_history
61923 | ACUA | FALSE | <1.5h | CS | 1 | 30 | 30 | TRUE | 0.79686 | 0.0030477 | 0.30477 | 0.017615 | 0.014637 | 0.0023929 | 0.0029773 | 0.29773 | 0.86646 | 0.78696 | 0.89427 | 0.11268 | 0.063092 | 0.0016162 | 17.6598 | 5.4953 | ok
61925 | Casa Mesa Wind Energy Center Hybrid | FALSE | <1.5h | CS | 1 | 73 | 73 | TRUE | 0.69984 | 0.0031447 | 0.31447 | 0.0045836 | 0.0025498 | 0.0033919 | 0.0020338 | 0.20338 | 0.64993 | 0.62707 | 0.63636 | 0.28412 | 0.04335 | 0.00059241 | 1.6812 | 33.9303 | ok
61956 | MCRD Parris Island PV Hybrid | TRUE | 1.5-2.5h | CS | 4 | 34 | 34 | TRUE | 0.77141 | 0.0050236 | 0.12559 | 0.013621 | 0.011789 | 0.0018615 | 0.0018315 | 0.045788 | 0.76893 | 0.70733 | 0.75412 | 0.22418 | 0.063005 | 0.0016521 | -2.0607 | -7.2781 | ok
61995 | UC Merced Solar Hybrid | TRUE | 1.5-2.5h | CS | 0.5 | 19 | 19 | TRUE | 0.8232 | 0.005576 | 1.1152 | 0.005088 | 0.0054042 | 0.0042572 | -0.00031625 | -0.06325 | 0.60927 | 0.62331 | 0.625 | 0.31524 | 0.18031 | 0.0019932 |  |  | insufficient_history
62147 | KCE NY 1 | FALSE | <1.5h | CS | 20 | 34 | 34 | TRUE | 0.87338 | -0.025964 | -0.12982 | -0.025867 | -0.023821 | -0.02972 | -0.0020459 | -0.01023 | 0.88117 | 0.88162 | 0.88277 | 0.032545 | 0.01044 | 0.025024 | -0.33473 | 29.3536 | ok
62175 | Diablo Energy Storage | FALSE | 2.5-4.5h | CS | 200 | 45 | 45 | TRUE | 0.86028 | 0.44396 | 0.22198 | 1.3097 | -0.095262 | 0.079479 | 1.405 | 0.70248 | 0.84739 | 0.84536 | 0.84811 | 0.043362 | 0.017544 | 0.318 | -3.5545 | -40.9073 | ok
62219 | Ashburnham Energy Storage Project | TRUE | <1.5h | CT | 3 | 36 | 36 | TRUE | 0.92083 | 0.0033025 | 0.11008 | 0.0068631 | 0.0018558 | 0.0070101 | 0.0050073 | 0.16691 | 0.86486 | 0.8425 | 0.84026 | 0.12027 | 0.064168 | 0.0015318 | -4.9584 | -116.5311 | ok
62235 | Lone Star Solar | TRUE | 2.5-4.5h | CS | 66 | 13 | 13 | TRUE | 0.96803 | 0.096543 | 0.14628 | 0.086648 | 0.0596 | 0.14606 | 0.027048 | 0.040982 | 0.93121 | 0.92809 | 0.93453 | 0.38251 | 0.018533 | 0.036985 |  |  | insufficient_history
62248 | Arrow Canyon Solar Hybrid | TRUE | >4.5h | CS | 75 | 25 | 25 | TRUE | 0.82669 | -0.8143 | -1.0857 | -0.25887 | -0.93946 | -0.72551 | 0.68059 | 0.90745 | 0.87848 | 0.88182 | 0.87924 | 0.12019 | 0.042504 | 0.4594 | 15.6296 | 224.6737 | ok
62257 | Station 9 Energy Storage System | FALSE | 1.5-2.5h | CS | 2 | 36 | 36 | TRUE | 0.93403 | 0.0068946 | 0.34473 | 0.0083833 | 0.0065615 | 0.011624 | 0.0018218 | 0.091091 | 0.78231 | 0.75908 | 0.75 | 0.40427 | 0.071426 | 0.0014353 | 0.21588 | -96.2059 | ok
62373 | I25 Battery Storage | FALSE | 2.5-4.5h | CS | 4 | 61 | 61 | TRUE | 0.84071 | 0.010407 | 0.26018 | 0.0085533 | 0.011758 | 0.028408 | -0.0032046 | -0.080115 | 0.87126 | 0.73928 | 0.83562 | 0.23284 | 0.043258 | 0.0024594 | -3.2549 | 92.8285 | ok
62381 | GMP Solar/Storage-Milton Hybrid | TRUE | 2.5-4.5h | OT | 2 | 61 | 61 | FALSE | 2.313 | -0.0011563 | -0.057816 | -0.0098266 | -0.0053538 | 0.031955 | -0.0044729 | -0.22364 | 2.411 | 0.6203 | 6.8333 | 0.00015433 | 0.14211 | 0.012117 |  |  | ok
62382 | GMP Solar/Storage-Ferrisburgh Hybrid | TRUE | 2.5-4.5h | OT | 2 | 60 | 60 | FALSE | 2.158 | -0.012747 | -0.63736 | -0.012336 | -0.013792 | -0.0104 | 0.0014565 | 0.072823 | 2.2658 | 0.62668 | 9.2991 | 0.051875 | 0.088906 | 0.0071558 |  |  | ok
62383 | GMP Solar/Storage-Essex Hybrid | TRUE | 2.5-4.5h | OT | 2 | 60 | 60 | FALSE | 1.5696 | -0.01725 | -0.8625 | -0.022276 | -0.018854 | 0.027641 | -0.0034224 | -0.17112 | 2.4102 | 0.62226 | 4.8514 | 0.031913 | 0.14315 | 0.012475 |  |  | ok
62441 | Kearny Mesa Storage LLC | TRUE | <1.5h | CS | 1 | 24 | 24 | TRUE | 0.93928 | 0.0013094 | 0.13094 | 0.002703 | 0.00041914 | 0.00096007 | 0.0022839 | 0.22839 | 0.92285 | 0.9231 | 0.9294 | 0.022855 | 0.028732 | 0.0018254 | 6.004 | 291.7564 | ok
62444 | Meyersdale Battery | TRUE | <1.5h | CT | 18 | 79 | 79 | TRUE | 0.86145 | 0.050541 | 0.28079 | 0.32878 | 0.15762 | 0.053674 | 0.17117 | 0.95093 | 0.85542 | 0.82431 | 0.85749 | 0.1682 | 0.013964 | 0.012809 | 0.27323 | 18.7212 | ok
62490 | Echo River Solar | TRUE | 2.5-4.5h | CS | 30 | 33 | 33 | TRUE | 0.88945 | 0.094802 | 0.31601 | 0.065761 | 0.095149 | 0.045964 | -0.029388 | -0.09796 | 0.82913 | 0.7778 | 0.8341 | 0.57156 | 0.027215 | 0.014742 | -4.544 | -79.562 | ok
62494 | Skeleton Creek Energy Center Hybrid | TRUE | 2.5-4.5h | CS | 252 | 2 |  | FALSE | [9 empty] | 0.82854 | [6 empty] | insufficient_history
62497 | Orange County Energy Storage 2 | FALSE | 2.5-4.5h | CS | 9 | 7 |  | FALSE | [9 empty] | 0.80933 | [6 empty] | insufficient_history
62499 | Orange County Energy Storage 3 | FALSE | 2.5-4.5h | CS | 6 | 7 |  | FALSE | [9 empty] | 0.84485 | [6 empty] | insufficient_history
62541 | Lake Placid Solar Power Plant | TRUE | 1.5-2.5h | CS | 17.3 | 32 | 32 | TRUE | 0.93299 | 0.0072773 | 0.042065 | 0.00022448 | 0.0023983 | 0.0077461 | -0.0021738 | -0.012566 | 0.91912 | 0.90009 | 0.91251 | 0.36261 | 0.013095 | 0.0017615 | -1.4998 | -86.4219 | ok
62561 | Roadrunner, LLC Hybrid | TRUE | 1.5-2.5h | CS | 63.3 | 9 |  | FALSE | [9 empty] | 0.7522 | [6 empty] | insufficient_history
62562 | High Lonesome Wind Power, LLC Hybrid | FALSE | <1.5h | CS | 63.3 | 13 | 13 | TRUE | 0.86398 | 0.25519 | 0.40314 | 0.17495 | -0.029865 | -0.046073 | 0.20481 | 0.32356 | 0.77521 | 0.76907 | 0.77616 | 0.29777 | 0.076441 | 0.11816 |  |  | insufficient_history
62564 | Elkhorn Battery Energy Storage System | FALSE | 2.5-4.5h | CS | 182.5 | 32 | 32 | TRUE | 0.87699 | 0.38381 | 0.21031 | 0.3851 | 0.5537 | 0.19366 | -0.1686 | -0.092385 | 0.85657 | 0.83198 | 0.85851 | 0.80241 | 0.0074321 | 0.034773 | -1.8848 | -97.4309 | ok
62585 | Beebe Substation Battery Storage | FALSE | <1.5h | CT | 3 | 34 | 34 | TRUE | 0.9757 | 0.0050912 | 0.16971 | 0.0060199 | 0.0047651 | 0.0067512 | 0.0012548 | 0.041826 | 0.86313 | 0.83197 | 0.8545 | 0.28897 | 0.062992 | 0.0014118 |  |  | ok
62604 | Outer Cape Community Battery | FALSE | 1.5-2.5h | BL | 25 | 31 | 31 | TRUE | 0.88863 | 0.0020409 | 0.0081636 | 0.00091549 | 0.00097538 | 0.011761 | -5.989e-05 | -0.00023956 | 0.88883 | 0.79606 | 0.92424 | 0.082616 | 0.062741 | 0.0012629 |  |  | ok
62609 | Commerce ESS | FALSE | <1.5h | CS | 10 | 71 | 71 | TRUE | 0.96341 | 0.094758 | 0.94758 | 0.11013 | 0.099298 | 0.091751 | 0.01083 | 0.1083 | 0.66804 | 0.64967 | 0.671 | 0.77061 | 0.03362 | 0.006224 | -2.6406 | -28.707 | ok
62644 | Minuteman Energy Storage | FALSE | 1.5-2.5h | CS | 5 | 80 | 80 | TRUE | 0.86724 | 0.010084 | 0.20169 | 0.0097027 | 0.010189 | 0.010496 | -0.00048613 | -0.0097227 | 0.76481 | 0.75967 | 0.76986 | 0.29365 | 0.037346 | 0.0017709 | -3.2729 | -16.0083 | ok
62652 | Happy Hollow CSG Hybrid | TRUE | 1.5-2.5h | CS | 3.3 | 24 | 24 | TRUE | 0.92772 | 0.015025 | 0.45531 | 0.014945 | 0.013661 | 0.014793 | 0.0012837 | 0.038899 | 0.84714 | 0.84169 | 0.847 | 0.90546 | 0.0081658 | 0.0010351 | 0.66435 | 6.3046 | ok
62682 | Noland Wastewater Treatment Plant Hybrid | TRUE | 1.5-2.5h | BL | 6 | 35 | 35 | TRUE | 0.64232 | 0.0012491 | 0.020818 | 0.0028162 | 0.0014627 |  | 0.0013534 | 0.022557 | 0.67287 | 0.56556 | 0.64865 | 0.042184 | 0.091266 | 0.0010361 | 2.4601 | -286.0648 | ok
62683 | Westside Wastewater Treatment Plant Hybr | TRUE | 1.5-2.5h | BL | 6 | 31 | 31 | TRUE | 0.69519 | 0.0022993 | 0.038321 | 0.0050301 | 0.0028329 |  | 0.0021971 | 0.036619 | 0.70425 | 0.62122 | 0.68939 | 0.049259 | 0.1116 | 0.0018758 |  |  | ok
62695 | CED Northampton Solar LLC Hybrid | TRUE | 1.5-2.5h | CS | 2.3 | 24 | 24 | TRUE | 0.8787 | 0.00087079 | 0.03786 | -0.0062654 | 0.00061797 | -0.0073614 | -0.0068834 | -0.29928 | 0.88903 | 0.87434 | 0.88889 | 0.089652 | 0.050748 | 0.00059159 | -4.0579 | -100.5053 | ok
62714 | Eyak Service Center BESS | FALSE | <1.5h | CS | 1 | 28 | 28 | TRUE | 0.58822 | 0.0010686 | 0.10686 | 0.00066689 | 0.0010341 | 0.0030471 | -0.00036725 | -0.036725 | 0.60628 | 0.48518 | 0.51471 | 0.12882 | 0.11359 | 0.00054498 | -10.1328 | -137.0129 | ok
62733 | East Hampton Energy Storage Center | FALSE | >4.5h | BL | 5 | 11 | 11 | TRUE | 0.94622 | 0.016416 | 0.32832 | 0.015857 | 0.016397 |  | -0.0005403 | -0.010806 | 0.93002 | 0.83592 | 0.93021 | 0.80375 | 0.016634 | 0.0027039 |  |  | ok
62734 | Montauk Energy Storage Center | FALSE | >4.5h | BL | 5 | 14 | 14 | TRUE | 0.9171 | 0.060909 | 1.2182 | 0.089 |  |  |  |  | 0.87088 | 0.79063 | 0.87391 | 0.094964 | 0.054407 | 0.054281 |  |  | ok
62745 | Wheatridge Hybrid | TRUE | 2.5-4.5h | CS | 30 | 45 | 45 | TRUE | 0.74406 | 0.024342 | 0.081141 | -0.58665 | -0.10769 | -0.040717 | -0.47896 | -1.5965 | 0.74859 | 0.77943 | 0.77838 | 0.00022064 | 0.11874 | 0.24988 | -10.5602 | 22.3372 | ok
62753 | Prospect Storage | TRUE | <1.5h | CS | 9.9 | 54 | 54 | FALSE | 1.294 | 0.038063 | 0.38447 | 0.039993 | 0.040273 | 0.035181 | -0.00028034 | -0.0028317 | 0.54501 | 0.48047 | 0.48913 | 0.74736 | 0.10772 | 0.0030689 | -1.1118 | 11.1889 | ok
62754 | San Diego International Airport BESS | FALSE | 1.5-2.5h | CS | 2 | 7 |  | FALSE | [9 empty] | 0.86271 | [6 empty] | insufficient_history
62801 | Vallecito | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.88121 | 0.051598 | 0.51598 | 0.063707 | 0.057411 | 0.052713 | 0.0062962 | 0.062962 | 0.8504 | 0.84809 | 0.85024 | 0.472 | 0.011161 | 0.011635 | -4.1007 | -70.5698 | ok
62835 | Acushnet Ball Plant 2 | FALSE | 1.5-2.5h | CS | 1.5 | 22 | 22 | TRUE | 0.75316 | -0.0012365 | -0.082435 | -0.00092413 | -0.0012629 | -0.0017095 | 0.00033876 | 0.022584 | 0.7543 | 0.81051 | 0.78506 | 0.34893 | 0.034637 | 0.00037769 | 6.1225 | -110.5905 | ok
62839 | 98th Street Battery Storage Station | TRUE | >4.5h | CS | 2 | 10 | 10 | TRUE | 0.78195 | 0.0095459 | 0.4773 | -0.0049134 |  | 0.0079234 |  |  | 0.71466 | 0.46421 | 0.73428 | 0.67767 | 0.098539 | 0.0023276 |  |  | ok
62844 | Cranberry Point Energy Storage | FALSE | 1.5-2.5h | CS | 150 | 8 |  | FALSE | [9 empty] | 0.84369 | [6 empty] | insufficient_history
62856 | Marengo Battery Storage LLC | TRUE | <1.5h | CS | 20 | 21 | 21 | TRUE | 0.83514 | -0.071729 | -0.35864 | -0.054766 | -0.071075 | -0.0093879 | 0.016309 | 0.081547 | 0.85791 | 0.85532 | 0.85671 | 0.96289 | 0.0068794 | 0.0032306 |  |  | ok
62862 | Nabb Battery Energy Storage System | FALSE | <1.5h | CS | 5 | 15 | 15 | TRUE | 0.86897 | -0.00093027 | -0.018605 | -0.00073817 | 0.0045031 | -0.0001507 | -0.0052413 | -0.10483 | 0.88148 | 0.83464 | 0.89157 | 0.053483 | 0.018493 | 0.0010854 |  |  | insufficient_history
62874 | Acorn I Energy Storage LLC | FALSE | 2.5-4.5h | CS | 2 | 36 | 36 | TRUE | 0.89439 | -0.00037965 | -0.018982 | 0.012486 | 0.007985 | -0.00040378 | 0.0045012 | 0.22506 | 0.90682 | 0.90023 | 0.92267 | 0.005039 | 0.014396 | 0.0009149 | -5.5586 | -123.0232 | ok
62875 | Wildcat I Energy Storage LLC | FALSE | 2.5-4.5h | CS | 3 | 36 | 36 | TRUE | 0.99712 | 0.019731 | 0.6577 | 0.019081 | 0.023176 | 0.019441 | -0.0040945 | -0.13648 | 0.90504 | 0.89369 | 0.91616 | 0.7226 | 0.013579 | 0.0020966 | 0.34951 | 102.7453 | ok
62889 | Hecate Energy Johanna Facility | FALSE | 2.5-4.5h | CS | 20 | 24 | 24 | TRUE | 0.95564 | 0.28125 | 1.4063 | 0.25823 | 0.205 | 0.26672 | 0.05323 | 0.26615 | 0.85773 | 0.85703 | 0.85849 | 0.2584 | 0.043941 | 0.10158 |  |  | ok
62907 | Hinesburg | FALSE | <1.5h | CS | 1.9 | 34 | 34 | TRUE | 0.87893 | 0.0027265 | 0.1435 | 0.0049417 | 0.010051 | 0.033992 | -0.0051097 | -0.26893 | 0.87312 | 0.87243 | 0.88184 | 0.013308 | 0.029574 | 0.0041502 | 5.0569 | 143.9647 | ok
62908 | Anoka BESS | FALSE | 1.5-2.5h | CS | 6 | 35 | 35 | TRUE | 0.53603 | 0.010459 | 0.17431 | 0.0041943 | 0.011575 | 0.024822 | -0.0073808 | -0.12301 | 0.48677 | 0.34262 | 0.44706 | 0.28936 | 0.10456 | 0.0028531 | -11.9115 | -56.7825 | ok
62937 | Athens BESS | TRUE | 1.5-2.5h | CS | 6 | 30 | 30 | TRUE | 0.50827 | 0.0039861 | 0.066435 | 0.0010258 | 0.0084334 |  | -0.0074076 | -0.12346 | 0.49652 | 0.33472 | 0.4641 | 0.03301 | 0.13549 | 0.0040772 | -7.9067 | -43.6672 | ok
62964 | El Sol BESS | FALSE | <1.5h | CS | 50 | 16 | 16 | TRUE | 0.89498 | 0.10307 | 0.20615 | 0.1341 | 0.11385 | 0.13996 | 0.020247 | 0.040494 | 0.88103 | 0.88028 | 0.88082 | 0.18948 | 0.011162 | 0.056975 |  |  | insufficient_history
62968 | Syncarpha Tewksbury Hybrid CSG | TRUE | 1.5-2.5h | CT | 2 | 32 | 32 | TRUE | 0.87589 | 0.0024944 | 0.12472 | 0.00087734 | 0.0028572 | 0.0029734 | -0.0019799 | -0.098995 | 0.84885 | 0.84094 | 0.84127 | 0.47728 | 0.013356 | 0.00047659 | 1.7372 | 59.9847 | ok
62969 | Syncarpha Puddon I Hybrid CSG | TRUE | 1.5-2.5h | CT | 4 | 24 | 24 | TRUE | 0.87987 | -0.00035005 | -0.0087511 | 0.00055632 | -0.0015021 | -0.0001086 | 0.0020584 | 0.051459 | 0.88384 | 0.88429 | 0.88792 | 0.0032544 | 0.018123 | 0.0013061 | -0.77618 | -9.9378 | ok
62970 | Syncarpha Puddon II Hybrid CSG | TRUE | 1.5-2.5h | CT | 4 | 23 | 23 | TRUE | 0.79998 | 0.0011774 | 0.029436 | 0.01757 | 0.033533 | 0.0015038 | -0.015963 | -0.39908 | 0.84013 | 0.81058 | 0.86885 | 0.19494 | 0.076199 | 0.00052214 |  |  | insufficient_history
62971 | Syncarpha Westminster Hybrid CSG | TRUE | 1.5-2.5h | CT | 2.9 | 12 | 12 | TRUE | 0.9531 | 0.0060876 | 0.20992 | 0.0079133 | 0.0091208 | 0.006264 | -0.0012075 | -0.041638 | 0.89192 | 0.85805 | 0.91768 | 0.41676 | 0.12301 | 0.0022774 |  |  | insufficient_history
62972 | Syncarpha Leicester Hybrid CSG | TRUE | 1.5-2.5h | CT | 2 | 36 | 36 | TRUE | 0.99352 | 0.00035611 | 0.017806 | 7.9981e-05 | 0.0012497 | 0.00024367 | -0.0011697 | -0.058484 | 0.98958 | 0.98465 | 0.98274 | 0.0041352 | 0.017594 | 0.00094777 | 1.1468 | 225.1189 | ok
62973 | Syncarpha Halifax Hybrid CSG | TRUE | 1.5-2.5h | CT | 1.6 | 36 | 36 | FALSE | 1.0152 | 0.0061183 | 0.3824 | 0.0040074 | 0.0080848 | 0.0064996 | -0.0040774 | -0.25483 | 0.91212 | 0.8974 | 0.89833 | 0.32427 | 0.037921 | 0.0015147 | 2.3701 | 51.9221 | ok
62974 | Syncarpha Millbury Hybrid (CSG) | TRUE | 1.5-2.5h | CT | 3.8 | 12 | 12 | TRUE | 0.96517 | 0.01548 | 0.40736 | 0.013815 | 0.016544 | 0.015289 | -0.0027292 | -0.07182 | 0.89617 | 0.88181 | 0.90981 | 0.88901 | 0.013809 | 0.0017296 |  |  | insufficient_history
62975 | Syncarpha Blandford Hybrid CSG | TRUE | 1.5-2.5h | CT | 3.9 | 35 | 35 | TRUE | 0.94598 | 0.0074893 | 0.19203 | -0.0035186 | 0.004834 | 0.0076135 | -0.0083526 | -0.21417 | 0.89894 | 0.88709 | 0.90503 | 0.51194 | 0.018908 | 0.001273 | 4.0723 | 120.7982 | ok
62976 | Syncarpha Northampton Hybrid CSG | TRUE | 1.5-2.5h | CT | 2 | 24 | 24 | TRUE | 0.94786 | 0.0073688 | 0.36844 | 0.0061667 | 0.0072779 | 0.0076205 | -0.0011112 | -0.055558 | 0.75921 | 0.73519 | 0.76279 | 0.71901 | 0.060425 | 0.00098211 | -7.1633 | 28.7753 | ok
62977 | Syncarpha Northbridge I Hybrid(CSG) | TRUE | 1.5-2.5h | CT | 4 | 12 | 12 | TRUE | 0.87668 | 0.0068867 | 0.17217 | 0.0057044 | 0.0080927 | 0.0068535 | -0.0023883 | -0.059708 | 0.81635 | 0.79914 | 0.80952 | 0.8072 | 0.020211 | 0.0010643 |  |  | insufficient_history
62978 | Syncarpha Northbridge II Hybrid CSG | TRUE | 1.5-2.5h | CT | 3 | 34 | 34 | TRUE | 0.83908 | 0.00012412 | 0.0041375 | 0.0002709 | 0.0036735 | 0.0024948 | -0.0034027 | -0.11342 | 0.84318 | 0.83904 | 0.8387 | 0.0020706 | 0.011801 | 0.0004817 | 2.7626 | 117.4722 | ok
62981 | East Pulaski BESS | FALSE | 1.5-2.5h | CS | 2 | 24 | 24 | FALSE | 0.4105 | -0.025257 | -1.2628 | -0.032663 | -0.021038 | -0.030672 | -0.011625 | -0.58125 | 0.54118 | 0.60609 | 0.81293 | 0.26286 | 0.30289 | 0.0090175 | -16.2101 | 75.0577 | ok
62999 | Finchville Solar, LLC Hybrid CSG | TRUE | <1.5h | CT | 3 | 23 | 23 | TRUE | 0.9681 | -7.1018e-06 | -0.00023673 | 0.0021266 | -1.6291e-05 | 4.6453e-05 | 0.0021428 | 0.071428 | 1.0063 | 0.90699 | 0.98 | 5.7999e-05 | 0.045215 | 0.00020349 |  |  | ok
63000 | RT 52 Walden Solar 1, LLC Hybrid | TRUE | 1.5-2.5h | CT | 4 | 15 | 15 | TRUE | 0.73823 | -2.13e-05 | -0.00053251 | 0.00064223 | -0.00016297 |  | 0.0008052 | 0.02013 | 0.87518 | 0.76323 | 0.84071 | 0.00010255 | 0.13147 | 0.00058335 |  |  | ok
63011 | Cronin Road Solar 1, LLC CSG Hybrid | TRUE | >4.5h | CT | 1.5 | 32 | 32 | TRUE | 0.98201 | 0.0014219 | 0.094792 | 0.0065379 | 0.005683 | 0.00023569 | 0.00085486 | 0.056991 | 0.9716 | 0.96953 | 0.97933 | 0.026922 | 0.022908 | 0.0015607 | -0.57911 | -26.8994 | ok
63022 | Fort Carson Battery Energy Storage Syste | FALSE | 1.5-2.5h | CS | 4.2 | 31 | 31 | TRUE | 0.50472 | -0.0070776 | -0.16851 | -0.0053857 | -0.0067539 | -0.01063 | 0.0013682 | 0.032577 | 0.5375 | 0.49727 | 0.54839 | 0.056834 | 0.073388 | 0.0053539 | 17.7593 | 135.6206 | ok
63044 | Ryan Road Solar LLC Hybrid(CSG) | TRUE | 2.5-4.5h | CT | 4.3 | 35 | 35 | TRUE | 0.9518 | 0.0026316 | 0.061199 | -0.0023541 | 0.0026099 | 0.0021736 | -0.004964 | -0.11544 | 0.94444 | 0.90262 | 0.94815 | 0.94085 | 0.0071092 | 0.00011486 | 1.6636 | 32.2313 | ok
63064 | Asheville-Rock Hill Battery | FALSE | <1.5h | CS | 8.8 | 58 | 58 | TRUE | 0.86318 | 0.018088 | 0.20554 | 0.014358 | 0.021555 | 0.024361 | -0.0071971 | -0.081785 | 0.65074 | 0.58221 | 0.63393 | 0.69743 | 0.060473 | 0.001592 | -0.93322 | -2.4556 | ok
63090 | Athens - Coopers Corner BESS | TRUE | 1.5-2.5h | CS | 3 | 2 |  | FALSE | [9 empty] | 0.23598 | [6 empty] | insufficient_history
63172 | Arroyo Solar Energy Storage Hybrid | TRUE | 2.5-4.5h | CS | 150 | 30 | 30 | TRUE | 0.96594 | 1.4481 | 0.96542 | 1.3925 | 1.4376 | 1.232 | -0.045038 | -0.030026 | 0.90386 | 0.9033 | 0.90398 | 0.28875 | 0.02152 | 0.42952 | 1.2852 | 18.9747 | ok
63186 | Imeson Solar | TRUE | <1.5h | CS | 5 | 12 | 12 | TRUE | 0.98801 | 0.0013046 | 0.026091 | 0.0010561 | 0.0012932 | 0.00088663 | -0.0002371 | -0.004742 | 0.96095 | 0.92399 | 0.96306 | 0.99024 | 0.0048506 | 4.0959e-05 |  |  | insufficient_history
63214 | Middleton Solar Park | TRUE | 1.5-2.5h | CS | 3 | 24 | 24 | TRUE | 0.96937 | 0.014724 | 0.49081 | 0.01687 | 0.012975 | 0.014945 | 0.0038953 | 0.12984 | 0.69957 | 0.66701 | 0.66728 | 0.81987 | 0.060264 | 0.0014714 |  |  | ok
63238 | Willis Battery Storage | FALSE | <1.5h | CS | 20 | 9 |  | FALSE | [9 empty] | 0.34329 | [6 empty] | insufficient_history
63255 | 2W Permian Solar Project Hybrid | TRUE | <1.5h | BL | 40 | 45 | 45 | FALSE | 0.45877 | -0.003097 | -0.0077424 | 0.0018181 | -0.020646 | 0.0073373 | 0.022464 | 0.056161 | 0.49708 | 0.4508 | 0.4619 | 0.0015451 | 0.095104 | 0.012006 | -2.6302 | 16.2808 | ok
63264 | Partridge Hill Solar Hybrid | TRUE | <1.5h | CS | 1.3 | 35 | 35 | TRUE | 0.92058 | 0.0033308 | 0.25622 | 0.001042 | 0.0026467 | 0.0031529 | -0.0016047 | -0.12344 | 0.86097 | 0.83664 | 0.86047 | 0.6738 | 0.020397 | 0.00040344 | 2.78 | 8.3906 | ok
63280 | AES Kekaha Solar, LLC Hybrid | TRUE | >4.5h | CT | 14 | 36 | 36 | TRUE | 0.96814 | -0.0010092 | -0.0072085 | -0.016719 | -0.031431 | -0.0013065 | 0.014712 | 0.10509 | 0.9709 | 0.96153 | 0.95943 | 0.0080843 | 0.010281 | 0.0019171 |  |  | ok
63324 | Camp Atterbury Microgrid Hybrid | TRUE | <1.5h | BL | 5 | 22 | 22 | TRUE | 0.89809 | 0.0037108 | 0.074217 | 0.0058928 | 0.0037621 | -0.00014364 | 0.0021307 | 0.042614 | 0.88723 | 0.80749 | 0.89522 | 0.50752 | 0.01795 | 0.00081738 | -4.5142 | -37.6726 | ok
63337 | Lansing Renewables, LLC | TRUE | <1.5h | CT | 3 | 36 | 36 | TRUE | 0.91175 | 0.0010695 | 0.035651 | -0.00086614 | 0.0010556 | 4.9797e-05 | -0.0019217 | -0.064057 | 0.9181 | 0.88942 | 0.89915 | 0.20802 | 0.019062 | 0.00035789 | 2.0358 | 114.0044 | ok
63338 | Granby Solar, LLC CSG | TRUE | <1.5h | CT | 2 | 36 | 36 | TRUE | 0.88598 | -0.00012564 | -0.0062818 | -5.6235e-05 | 0.00091009 | 0.0023329 | -0.00096633 | -0.048316 | 0.88889 | 0.88803 | 0.89348 | 0.0019094 | 0.0088487 | 0.00049262 | 1.3743 | 87.689 | ok
63339 | Hales Mills Solar, LLC | TRUE | 2.5-4.5h | CS | 3 | 11 | 11 | TRUE | 0.91669 | 0.00067064 | 0.022355 | 0.00051963 | 0.00095597 |  | -0.00043633 | -0.014544 | 0.89971 | 0.85358 | 0.89286 | 0.2761 | 0.034101 | 0.00036197 |  |  | insufficient_history
63340 | Owlville Creek Solar 2, LLC | TRUE | 2.5-4.5h | CS | 3 | 33 | 33 | TRUE | 0.90468 | 0.001005 | 0.0335 | -0.00080188 | 0.0009938 | 0.00018268 | -0.0017957 | -0.059856 | 0.89013 | 0.88261 | 0.89796 | 0.2139 | 0.01563 | 0.00034603 | -0.7857 | 56.4682 | ok
63341 | Owlville Creek Solar, LLC | TRUE | 2.5-4.5h | CS | 3 | 33 | 33 | TRUE | 0.90149 | -9.1441e-05 | -0.003048 | -0.00052328 | -0.00010581 | -4.1034e-05 | -0.00041746 | -0.013915 | 0.9078 | 0.9059 | 0.89655 | 0.0086898 | 0.010543 | 0.00017541 | 4.6436 | 119.6162 | ok
63352 | Gemini Solar Hybrid | TRUE | <1.5h | CS | 380 | 21 | 21 | TRUE | 0.92882 | 3.0546 | 0.80384 | 1.7882 | 0.11031 | -0.20249 | 1.6779 | 0.44155 | 0.87717 | 0.87728 | 0.8758 | 0.065689 | 0.056192 | 2.6429 |  |  | insufficient_history
63398 | Kearsarge Amesbury Hybrid | TRUE | 1.5-2.5h | CS | 1.6 | 36 | 36 | TRUE | 0.89396 | 0.0042947 | 0.26842 | 0.0057286 | 0.0044682 | 0.0045384 | 0.0012604 | 0.078775 | 0.86887 | 0.8641 | 0.86999 | 0.66222 | 0.0054023 | 0.00052604 | -2.64 | -62.7479 | ok
63415 | Middletown Solar 1, LLC Hybrid CSG | TRUE | 2.5-4.5h | CS | 1.6 | 4 |  | FALSE | [9 empty] | 1.0137 | [6 empty] | insufficient_history
63420 | Fresno Bullard High School Hybrid | TRUE | <1.5h | CS | 0.4 | 27 | 27 | FALSE | 1.0297 | 0.0013745 | 0.34362 | 0.0013829 | 0.0013453 | 0.0013945 | 3.7674e-05 | 0.0094186 | 0.87027 | 0.80246 | 0.85714 | 0.92416 | 0.02919 | 7.8751e-05 |  |  | ok
63421 | Fresno Hoover High School Hybrid | TRUE | <1.5h | CS | 0.2 | 12 | 12 | FALSE | 1.2561 | 0.00051157 | 0.25578 | 0.00096303 | 0.00051785 | 0.00047265 | 0.00044518 | 0.22259 | 1.1685 | 1.0887 | 1.1716 | 0.40124 | 0.038882 | 0.00019762 |  |  | insufficient_history
63422 | Fresno Sunnyside High School Hybrid | TRUE | <1.5h | CS | 0.3 | 12 | 12 | TRUE | 0.7655 | -0.0011916 | -0.39721 | -0.0012258 | -0.0011964 | -0.0011692 | -2.9364e-05 | -0.009788 | 0.8642 | 0.87351 | 0.85714 | 0.27015 | 0.08383 | 0.00061937 |  |  | insufficient_history
63458 | Rush Springs Energy Storage (BA) | FALSE | 1.5-2.5h | CS | 10 | 20 | 20 | TRUE | 0.90277 | 0.050926 | 0.50926 | 0.05163 | 0.052966 | 0.058394 | -0.0013355 | -0.013355 | 0.86882 | 0.86291 | 0.87072 | 0.67133 | 0.0095664 | 0.0083988 | 0.026554 | 19.91 | ok
63468 | Hurteau Solar Project Hybrid | TRUE | <1.5h | CS | 1.3 | 23 | 23 | TRUE | 0.71176 | 0.0055396 | 0.42612 | 0.020456 | 0.019569 | -0.00067404 | 0.00088667 | 0.068205 | 0.62837 | 0.38701 | 0.55 | 0.016958 | 0.41332 | 0.0092038 |  |  | ok
63469 | Alicea Solar Project Hybrid CSG | TRUE | 1.5-2.5h | CS | 1.5 | 32 | 32 | TRUE | 0.94598 | 0.0014046 | 0.09364 | 0.0012906 | 0.0031695 | 0.002844 | -0.0018789 | -0.12526 | 0.92647 | 0.88929 | 0.92308 | 0.58101 | 0.016444 | 0.00021777 | 7.2098 | 44.1074 | ok
63470 | McDougle-Mitchell Solar Project Hybrid C | TRUE | 1.5-2.5h | CS | 2.9 | 36 | 36 | FALSE | 1.0146 | 0.0055038 | 0.18979 | 0.0077086 | 0.0081132 | 0.0058227 | -0.00040459 | -0.013951 | 0.92334 | 0.89984 | 0.93222 | 0.5571 | 0.033348 | 0.00084161 | 5.6214 | -80.5994 | ok
63472 | Cycz Solar Project CSG Hybrid | TRUE | 1.5-2.5h | CS | 1.3 | 36 | 36 | TRUE | 0.7645 | -0.00033773 | -0.025979 | -0.0016035 | -0.0013994 | -0.00030117 | -0.00020407 | -0.015697 | 0.78614 | 0.79899 | 0.83772 | 0.034365 | 0.042827 | 0.00030702 | -6.9254 | -11.7978 | ok
63473 | West A&B Solar Project Hybrid CSG | TRUE | 1.5-2.5h | CS | 1.8 | 34 | 34 | TRUE | 0.93143 | 0.0011315 | 0.062861 | 0.00057947 | 0.0010628 | 0.0011955 | -0.00048334 | -0.026852 | 0.9189 | 0.9119 | 0.91667 | 0.1408 | 0.014714 | 0.0004941 | 4.113 | 110.8715 | ok
63474 | Annese Solar Project Hybrid CSG | TRUE | 1.5-2.5h | CS | 3.5 | 36 | 36 | TRUE | 0.92816 | 0.0066041 | 0.18869 | 0.0054961 | 0.013916 | 0.006678 | -0.0084202 | -0.24058 | 0.86631 | 0.83801 | 0.87539 | 0.49965 | 0.047725 | 0.0011334 | 5.7129 | -3.2516 | ok
63475 | Randall Solar Project Hybrid | TRUE | 1.5-2.5h | CT | 3.3 | 36 | 36 | TRUE | 0.95998 | 0.0040793 | 0.12361 | 0.0063111 | 0.0057299 | 0.0040948 | 0.00058122 | 0.017613 | 0.91043 | 0.89712 | 0.90826 | 0.39999 | 0.022129 | 0.00085682 | 4.6659 | -25.8584 | ok
63486 | D'Arrigo Brothers - Phase 4 | TRUE | 1.5-2.5h | CS | 0.5 | 36 | 36 | FALSE | 1.2724 | 0.0099631 | 1.9926 | 0.010625 | 0.010797 | 0.01037 | -0.00017159 | -0.034319 | 0.84047 | 0.84153 | 0.84605 | 0.11993 | 0.18871 | 0.0046285 |  |  | ok
63510 | Walnut Unified School District Walnut HS | TRUE | <1.5h | CS | 0.5 | 23 | 23 | TRUE | 0.95797 | 0.0011682 | 0.23364 | 0.0011729 | 0.0011715 | 0.00010014 | 1.4155e-06 | 0.0002831 | 0.88131 | 0.85407 | 0.89655 | 0.75119 | 0.036122 | 0.00014672 | 3.1803 | 11.4844 | ok
63522 | Hickory Park Solar Hybrid | TRUE | 1.5-2.5h | OT | 40 | 43 | 43 | TRUE | 0.94086 | 0.24958 | 0.62394 | 0.31041 | 0.24891 | 0.026061 | 0.061503 | 0.15376 | 0.8496 | 0.83382 | 0.82165 | 0.024488 | 0.12221 | 0.24601 | -3.3197 | -2.1648 | ok
63535 | Solar BESS Hybrid | TRUE | 2.5-4.5h | BL | 1 | 36 | 36 | TRUE | 0.95822 | 0.0056134 | 0.56134 | 0.0093716 | 0.0058684 | 0.0029474 | 0.0035032 | 0.35032 | 0.88893 | 0.86588 | 0.89639 | 0.85891 | 0.019938 | 0.00039018 | -6.0242 | -149.8016 | ok
63585 | NY3 Battery | TRUE | 2.5-4.5h | CS | 3 | 30 | 30 | TRUE | 0.98465 | 0.015476 | 0.51585 | 0.0024608 | 0.015774 | 0.013761 | -0.013313 | -0.44377 | 0.864 | 0.75097 | 0.86533 | 0.79503 | 0.039028 | 0.001485 | -2.1452 | -19.6158 | ok
63609 | Allergan | FALSE | >4.5h | CS | 1.5 | 24 | 24 | TRUE | 0.8658 | 0.00016476 | 0.010984 | -0.00037734 | -7.6269e-05 | 4.5184e-05 | -0.00030107 | -0.020072 | 0.86405 | 0.86527 | 0.85641 | 0.00071913 | 0.017724 | 0.0013094 | -9.7856 | -217.013 | ok
63610 | Baker | FALSE | >4.5h | CS | 1.2 | 24 | 24 | TRUE | 0.819 | -0.0017171 | -0.14309 | -0.0069959 | -0.0045088 | -0.0028366 | -0.0024871 | -0.20726 | 0.83397 | 0.84023 | 0.83556 | 0.068364 | 0.025022 | 0.0013514 | -13.0107 | -230.8643 | ok
63611 | CSU Long Beach | FALSE | >4.5h | CS | 2.5 | 24 | 24 | TRUE | 0.8125 | -0.0060754 | -0.24302 | -0.024794 | -0.017067 | -0.0094238 | -0.0077268 | -0.30907 | 0.82986 | 0.83942 | 0.83773 | 0.12458 | 0.023703 | 0.0034336 | -14.6603 | -275.0669 | ok
63612 | DATS | FALSE | >4.5h | CS | 1 | 24 | 24 | TRUE | 0.86012 | 0.0020414 | 0.20414 | 0.0082232 | 0.0056555 | 0.0028894 | 0.0025677 | 0.25677 | 0.83812 | 0.82779 | 0.84034 | 0.19736 | 0.024817 | 0.00087769 | -11.9537 | -108.0091 | ok
63613 | Downey | FALSE | >4.5h | CS | 2 | 24 | 24 | TRUE | 0.87656 | 0.0037954 | 0.18977 | 0.010145 | 0.0077194 | 0.0043708 | 0.0024259 | 0.12129 | 0.85466 | 0.84344 | 0.84074 | 0.39077 | 0.014836 | 0.0010103 | -7.5485 | -55.2288 | ok
63614 | LAWRP | FALSE | >4.5h | CS | 1 | 24 | 24 | TRUE | 0.84181 | -0.00050064 | -0.050064 | -0.0036374 | -0.002459 | -0.0011889 | -0.0011784 | -0.11784 | 0.84651 | 0.85122 | 0.84815 | 0.0069857 | 0.028261 | 0.0012726 | -14.6083 | -172.2932 | ok
63615 | Long Beach Convention Center | FALSE | >4.5h | CS | 1.5 | 24 | 24 | TRUE | 0.80681 | -0.0051181 | -0.34121 | -0.015838 | -0.011119 | -0.0060298 | -0.0047197 | -0.31465 | 0.82387 | 0.83988 | 0.85124 | 0.29696 | 0.018118 | 0.001679 | -12.5422 | -187.5423 | ok
63616 | OCSD | FALSE | >4.5h | CS | 4.9 | 24 | 24 | TRUE | 0.88272 | 0.0012045 | 0.024582 | 0.0024052 | 0.0011947 | 0.0014443 | 0.0012104 | 0.024703 | 0.8801 | 0.87967 | 0.88016 | 0.33851 | 0.0013289 | 0.00035898 | -0.15345 | 11.1561 | ok
63617 | SOCCD | FALSE | >4.5h | CS | 1.3 | 24 | 24 | TRUE | 0.8073 | -0.003878 | -0.29831 | -0.01162 | -0.0086554 | -0.004618 | -0.002965 | -0.22808 | 0.82444 | 0.83737 | 0.83388 | 0.32013 | 0.015678 | 0.0012049 | -10.4276 | -198.6628 | ok
63685 | Luna Storage | FALSE | 2.5-4.5h | CT | 100 | 41 | 41 | TRUE | 0.88704 | 0.54806 | 0.54806 | 1.046 | 1.0088 | 0.5617 | 0.037229 | 0.037229 | 0.858 | 0.84873 | 0.86013 | 0.9698 | 0.0045958 | 0.015486 | -4.3194 | -71.0164 | ok
63721 | Cool Springs Solar (Hybrid) | TRUE | 1.5-2.5h | CS | 40 | 49 | 49 | FALSE | 1.0376 | 0.23648 | 0.5912 | 0.39609 | 0.34358 | 0.24564 | 0.05251 | 0.13128 | 0.96175 | 0.95389 | 0.97518 | 0.20391 | 0.027668 | 0.068157 | -0.74943 | -36.933 | ok
63722 | Rawhide Prairie Solar Hybrid | TRUE | 1.5-2.5h | CS | 1 | 26 | 26 | TRUE | 0.82907 | 3.6514e-05 | 0.0036514 | -0.0001904 | 0.003415 | 0.00042378 | -0.0036054 | -0.36054 | 0.8362 | 0.83207 | 0.83772 | 0.00012402 | 0.023743 | 0.00066924 |  |  | ok
63723 | Ho'Ohana Solar 1 | TRUE | 2.5-4.5h | CS | 52 | 6 |  | FALSE | [9 empty] | 0.93927 | [6 empty] | insufficient_history
63727 | Slate Hybrid | TRUE | 2.5-4.5h | CS | 140.3 | 38 | 38 | TRUE | 0.87239 | 0.47226 | 0.33661 | 0.61701 | 0.48663 | 0.49009 | 0.13038 | 0.092932 | 0.85262 | 0.84894 | 0.8505 | 0.45419 | 0.0068574 | 0.086284 | -2.6583 | -45.6324 | ok
63728 | Taos Mesa Energy Facility Hybrid | TRUE | 1.5-2.5h | CS | 12.5 | 38 | 38 | TRUE | 0.86069 | 0.01259 | 0.10072 | 0.023216 | 0.013294 | 0.023227 | 0.0099219 | 0.079376 | 0.84943 | 0.84841 | 0.84492 | 0.058362 | 0.013063 | 0.0084286 | -4.191 | -74.985 | ok
63731 | Neptune Energy Center Hybrid | TRUE | 2.5-4.5h | CS | 125 | 31 | 31 | TRUE | 0.8846 | 0.67875 | 0.543 | 1.0078 | 0.67049 | 0.65973 | 0.33728 | 0.26983 | 0.84248 | 0.8397 | 0.83989 | 0.21144 | 0.022977 | 0.24341 | -10.1527 | -176.1761 | ok
63735 | Silverstrand Grid Energy Storage System | FALSE | 2.5-4.5h | CS | 11 | 21 | 21 | TRUE | 0.85423 | -0.016932 | -0.15393 | 0.0022774 | 0.015375 | -0.014943 | -0.013098 | -0.11907 | 0.86269 | 0.86319 | 0.86534 | 0.0083627 | 0.029516 | 0.0423 |  |  | insufficient_history
63737 | Chisholm Grid Energy Storage System | FALSE | <1.5h | CS | 100 | 49 | 49 | TRUE | 0.9422 | 0.2945 | 0.2945 | 0.30517 | 0.29425 | 0.2911 | 0.010926 | 0.010926 | 0.90812 | 0.89922 | 0.91094 | 0.74332 | 0.0061497 | 0.025243 | -0.064721 | 32.6787 | ok
63757 | Madero Grid | FALSE | <1.5h | CS | 100 | 31 | 31 | TRUE | 0.87641 | 0.36863 | 0.36863 | 0.38676 | 0.094567 | -0.019514 | 0.29219 | 0.29219 | 0.8388 | 0.83133 | 0.83906 | 0.43544 | 0.015648 | 0.077943 | 4.6381 | 135.9276 | ok
63763 | CES Agawam Tuckahoe Solar Hybrid | TRUE | 1.5-2.5h | CS | 2.6 | 36 | 36 | FALSE | 1 | -3.1915e-18 | -1.2275e-16 | -5.2495e-19 | 1.0375e-17 | 9.9552e-18 | -1.09e-17 | -4.1922e-16 | 1 | 1 | 1 |  | 7.9172e-17 | 1.595e-18 | -2.109e-14 | -19.9571 | ok
63774 | Mount Kisco Landfill Solar & Storage CSG | TRUE | 2.5-4.5h | CS | 0.7 | 6 |  | FALSE | [9 empty] | 0.85397 | [6 empty] | insufficient_history
63776 | Thunder Wolf Energy Center Hybrid | TRUE | 2.5-4.5h | CS | 100 | 31 | 31 | TRUE | 0.90489 | 0.83382 | 0.83382 | 0.81294 | 0.66786 | 0.66022 | 0.14507 | 0.14507 | 0.84269 | 0.84154 | 0.84072 | 0.19518 | 0.032221 | 0.31441 | 0.91062 | 47.0278 | ok
63804 | Partridgeville Hybrid CSG | TRUE | 1.5-2.5h | CS | 2 | 36 | 36 | TRUE | 0.85026 | 0.00084537 | 0.042268 | 0.0011772 | 0.00063091 | 0.0011956 | 0.00054633 | 0.027316 | 0.85924 | 0.81116 | 0.87689 | 0.35957 | 0.045444 | 0.00019349 | -10.2197 | -124.9275 | ok
63805 | Williamsville Hybrid CSG | TRUE | 1.5-2.5h | CS | 3.3 | 36 | 36 | TRUE | 0.83948 | 0.0020053 | 0.060767 | 0.00075238 | 0.0020119 | 0.0062791 | -0.0012595 | -0.038168 | 0.8327 | 0.81636 | 0.87576 | 0.23273 | 0.044536 | 0.00062445 | -2.3483 | -98.889 | ok
63834 | Gateway Energy Storage System | FALSE | 2.5-4.5h | BL | 250 | 63 | 63 | TRUE | 0.86801 | 0.40044 | 0.16018 | 0.25273 | 0.82638 | 1.2003 | -0.57365 | -0.22946 | 0.87239 | 0.83184 | 0.86722 | 0.50423 | 0.024619 | 0.050839 | -1.7726 | -23.1259 | ok
63843 | Johanna Energy Center, LLC | TRUE | 2.5-4.5h | CS | 80 | 24 | 24 | TRUE | 0.91242 | 0.39978 | 0.49972 | 0.52051 | 0.4338 | 0.48939 | 0.086707 | 0.10838 | 0.88274 | 0.88276 | 0.88327 | 0.054775 | 0.032855 | 0.35406 | -1.6256 | -45.4648 | ok
63848 | Solar Blue | TRUE | 2.5-4.5h | CS | 225 | 23 | 23 | TRUE | 0.89726 | 0.30176 | 0.13411 | 0.68404 | 0.52669 | 0.43373 | 0.15735 | 0.069934 | 0.8907 | 0.89035 | 0.88972 | 0.022033 | 0.013029 | 0.43871 |  |  | insufficient_history
63849 | Chestnut | TRUE | 2.5-4.5h | CS | 135 | 23 | 23 | TRUE | 0.95066 | 1.6301 | 1.2075 | 1.6471 | 1.6068 | 1.7789 | 0.040286 | 0.029842 | 0.89057 | 0.89023 | 0.88893 | 0.52044 | 0.015026 | 0.34146 |  |  | insufficient_history
63859 | Golden Field Solar III, LLC | TRUE | <1.5h | CS | 147 | 22 | 22 | TRUE | 0.87827 | -0.09792 | -0.066612 | -0.45127 | -0.094331 | 1.8656 | -0.35693 | -0.24281 | 0.89552 | 0.89583 | 0.89618 | 0.026146 | 0.031258 | 0.13363 |  |  | insufficient_history
63891 | Saticoy | TRUE | 2.5-4.5h | CS | 100 | 57 | 57 | TRUE | 0.89344 | 0.45391 | 0.45391 | 0.40492 | -0.12892 | 0.22204 | 0.53383 | 0.53383 | 0.86599 | 0.86475 | 0.86596 | 0.11245 | 0.01675 | 0.17195 | 0.5843 | 21.8534 | ok
63892 | Lily Solar Hybrid | TRUE | <1.5h | CS | 55.2 | 51 | 51 | TRUE | 0.91371 | 0.13943 | 0.25259 | 0.11823 | 0.15592 | 0.12311 | -0.037691 | -0.068281 | 0.80875 | 0.7779 | 0.80343 | 0.78627 | 0.017557 | 0.010385 | -0.60966 | 1.7831 | ok
63900 | AES Waikoloa Solar Hybrid | TRUE | 2.5-4.5h | CS | 30 | 24 | 24 | FALSE | 1.2168 | 0.84342 | 2.8114 | 0.39139 | 0.38935 | 0.66369 | 0.0020378 | 0.0067926 | 0.97001 | 0.97376 | 0.98523 | 0.089809 | 0.14587 | 0.57245 |  |  | ok
63905 | Azure Sky Solar | TRUE | <1.5h | CS | 91.2 | 41 | 41 | TRUE | 0.9299 | 0.62066 | 0.68055 | 0.63275 | 0.59587 | 0.59513 | 0.036881 | 0.040439 | 0.71329 | 0.65298 | 0.68441 | 0.97354 | 0.013171 | 0.016385 | -1.2279 | -3.1597 | ok
63913 | Dodge Flat | TRUE | 2.5-4.5h | CS | 50 | 45 | 45 | TRUE | 0.9346 | 0.16344 | 0.32688 | 0.16258 | 0.10411 | 0.012839 | 0.058461 | 0.11692 | 0.91356 | 0.90165 | 0.90586 | 0.29134 | 0.0096735 | 0.038873 | 0.57722 | 4.5797 | ok
63930 | Cal Flats BESS | TRUE | 2.5-4.5h | CS | 60 | 50 | 50 | TRUE | 0.89865 | 0.23822 | 0.39703 | 0.3733 | 0.32548 | -0.41491 | 0.047816 | 0.079694 | 0.87008 | 0.83936 | 0.84164 | 0.0072056 | 0.071386 | 0.4036 | -3.1229 | -57.0042 | ok
63933 | Dry Lake Solar Energy Center | TRUE | 1.5-2.5h | CS | 100 | 20 | 20 | TRUE | 0.91803 | 0.53381 | 0.53381 | 1.1148 | 0.86606 | 0.90036 | 0.24872 | 0.24872 | 0.88891 | 0.88895 | 0.89117 | 0.017222 | 0.063967 | 0.95048 |  |  | insufficient_history
63943 | Coso Battery Storage | FALSE | 2.5-4.5h | CS | 60 | 45 | 45 | TRUE | 0.946 | 0.93635 | 1.5606 | 0.95078 | 0.81963 | 0.72795 | 0.13115 | 0.21859 | 0.86278 | 0.85862 | 0.8593 | 0.4073 | 0.020234 | 0.17225 | -1.6376 | -9.0035 | ok
63995 | Trenton | FALSE | <1.5h | CS | 11 | 13 | 13 | TRUE | 0.67784 | 0.0040787 | 0.037079 | 0.007154 | 0.0023528 |  | 0.0048012 | 0.043647 | 0.65359 | 0.52735 | 0.57143 | 0.21867 | 0.20318 | 0.0023246 |  |  | insufficient_history
63996 | Cape San Blas | FALSE | 2.5-4.5h | CS | 5.5 | 22 | 22 | TRUE | 0.82172 | 4.4219e-05 | 0.00080398 | 0.0050334 | -0.00016732 | 0.00089134 | 0.0052007 | 0.094559 | 0.84536 | 0.78838 | 0.84707 | 6.2572e-05 | 0.050578 | 0.0012499 | -11.67 | 260.4586 | ok
63998 | Jennings Energy Storage Facility | FALSE | <1.5h | CS | 5.5 | 20 | 20 | TRUE | 0.59505 | -0.00030688 | -0.0055796 | -0.00035309 | 0.011498 | 0.0071062 | -0.011851 | -0.21547 | 0.6737 | 0.57126 | 0.65357 | 0.010826 | 0.12338 | 0.0006914 | -40.5547 | -297.4297 | ok
63999 | Micanopy Energy Storage Facility | FALSE | <1.5h | CS | 8.3 | 21 | 21 | TRUE | 0.93355 | 0.016632 | 0.20038 | 0.015765 | 0.018054 | 0.016949 | -0.0022891 | -0.027579 | 0.72663 | 0.66454 | 0.70909 | 0.72681 | 0.078609 | 0.0023392 | -8.5505 | -11.8579 | ok
64000 | Amaterasu LLC | TRUE | 1.5-2.5h | CT | 3.2 | 34 | 34 | TRUE | 0.86535 | 0.00020485 | 0.0064016 | -0.014028 | 8.6095e-05 | -0.0007956 | -0.014114 | -0.44107 | 0.90749 | 0.85116 | 0.90765 | 0.0088797 | 0.050051 | 0.00038258 | 4.578 | 136.4041 | ok
64050 | Fort Bragg - Camp Mackall PV BESS System | TRUE | <1.5h | CS | 2 | 6 |  | FALSE | [9 empty] | 0.55208 | [6 empty] | insufficient_history
64084 | Blanchard Road 1 Community Solar | TRUE | 2.5-4.5h | CS | 5 | 9 |  | FALSE | [9 empty] | 1 | [6 empty] | insufficient_history
64087 | Blanchard Road 2 Community Solar | TRUE | 2.5-4.5h | CS | 5 | 9 |  | FALSE | [9 empty] | 1 | [6 empty] | insufficient_history
64089 | Ignacio Grid Energy Storage System | FALSE | <1.5h | CS | 100 | 31 | 31 | TRUE | 0.87735 | 0.41668 | 0.41668 | 0.37254 | 0.18904 | 0.061092 | 0.1835 | 0.1835 | 0.83808 | 0.83431 | 0.83875 | 0.35629 | 0.01565 | 0.104 | 6.2439 | 156.2702 | ok
64090 | NYS Rte 12 Community Solar | TRUE | 2.5-4.5h | CS | 5 | 9 |  | FALSE | [9 empty] | 1 | [6 empty] | insufficient_history
64092 | Great Lakes Seaway Community Solar | TRUE | 2.5-4.5h | CS | 5 | 9 |  | FALSE | [9 empty] | 1 | [6 empty] | insufficient_history
64103 | Desert Harvest II LLC | TRUE | 2.5-4.5h | CS | 35 | 55 | 55 | TRUE | 0.94985 | 0.36413 | 1.0404 | 0.33194 | 0.36843 | 0.31835 | -0.036494 | -0.10427 | 0.8299 | 0.77789 | 0.82081 | 0.69797 | 0.023694 | 0.032902 | 3.5857 | 11.326 | ok
64105 | Maverick Solar 6, LLC | TRUE | 2.5-4.5h | CS | 50 | 42 | 42 | TRUE | 0.86791 | -0.074377 | -0.14875 | -0.075792 | -0.27707 | 0.069101 | 0.20127 | 0.40255 | 0.88077 | 0.88705 | 0.87968 | 0.34466 | 0.019132 | 0.016216 | -9.2272 | -119.3714 | ok
64128 | Ware Palmer Road Solar LLC CSG | TRUE | 1.5-2.5h | CS | 2 | 28 | 28 | FALSE | 1.0047 | 0.0039627 | 0.19813 | 0.0037823 | 0.0040952 | 0.0044099 | -0.0003129 | -0.015645 | 0.91867 | 0.55504 | 0.45 | 0.96596 | 0.040151 | 0.00014589 | -33.1872 | -11.5973 | ok
64129 | East Brookfield Adams Road Solar LLC CSG | TRUE | 1.5-2.5h | CS | 3.1 | 24 | 24 | TRUE | 0.97088 | 0.0024355 | 0.078566 | 0.0043751 | 0.0020032 | 0.0058956 | 0.0023719 | 0.076514 | 0.95804 | 0.95569 | 0.96478 | 0.043096 | 0.019343 | 0.0024468 | -2.4105 | -105.3243 | ok
64140 | BWC Stony Brook, LLC Hybrid | TRUE | 1.5-2.5h | CT | 0.7 | 35 | 35 | TRUE | 0.93082 | 0.001941 | 0.27729 | 0.0035824 | 0.0025244 | 0.0020541 | 0.0010579 | 0.15114 | 0.8527 | 0.81579 | 0.85714 | 0.52687 | 0.042903 | 0.00032019 | 0.27518 | -144.6866 | ok
64147 | ZPD-PT Solar Project 2017-038 Hybrid LLC | TRUE | 1.5-2.5h | CT | 3.5 | 36 | 36 | TRUE | 0.98358 | 0.0064526 | 0.18436 | 0.0059881 | 0.0057911 | 0.0065851 | 0.00019695 | 0.0056273 | 0.91573 | 0.88871 | 0.92612 | 0.21223 | 0.060126 | 0.002132 | -0.2909 | 23.9847 | ok
64148 | Fish Springs | TRUE | 2.5-4.5h | CS | 25 | 44 | 44 | TRUE | 0.88043 | -0.023365 | -0.093461 | 0.28467 | -0.016458 | 0.10143 | 0.30113 | 1.2045 | 0.88981 | 0.87831 | 0.90391 | 0.0021968 | 0.034075 | 0.076838 | -0.47258 | -5.9027 | ok
64164 | Azure Sky Wind Project, LLC Hybrid | FALSE | 1.5-2.5h | CS | 120 | 12 | 12 | TRUE | 0.9122 | 1.3114 | 1.0928 | 1.237 | 1.3082 | 1.2171 | -0.071258 | -0.059382 | 0.77246 | 0.76329 | 0.77505 | 0.98205 | 0.0099632 | 0.05607 |  |  | insufficient_history
64170 | BWC Muddy Brook, LLC Hybrid | TRUE | 1.5-2.5h | CT | 0.9 | 35 | 35 | TRUE | 0.88556 | 9.0235e-05 | 0.010026 | 0.00060717 | 0.00094636 | 8.4064e-05 | -0.00033919 | -0.037688 | 0.90835 | 0.87609 | 0.9 | 0.010603 | 0.036681 | 0.00015173 | 4.8739 | 67.2248 | ok
64182 | BWC Lake Lashaway, LLC Hybrid | TRUE | 1.5-2.5h | CT | 3.7 | 34 | 34 | TRUE | 0.97252 | 0.003181 | 0.085974 | 0.0047014 | 0.0038564 | 0.0033447 | 0.00084501 | 0.022838 | 0.94699 | 0.93659 | 0.94444 | 0.30757 | 0.014159 | 0.00084375 | -0.48126 | -39.174 | ok
64185 | ZPD-PT Solar Project 2017-023 LLC Hybrid | TRUE | 1.5-2.5h | CT | 1.9 | 35 | 35 | TRUE | 0.93051 | 0.0020567 | 0.10825 | 0.00038351 | -0.00092568 | 0.0018858 | 0.0013092 | 0.068905 | 0.90196 | 0.89464 | 0.94118 | 0.1096 | 0.042446 | 0.0010205 | 5.9842 | 32.1905 | ok
64187 | ZPD-PT Solar Project 2017-021 LLC Hybrid | TRUE | 2.5-4.5h | CT | 0.7 | 36 | 36 | TRUE | 0.98679 | 0.0009178 | 0.13111 | 0.0016367 | 0.0016226 | 0.00098702 | 1.417e-05 | 0.0020243 | 0.95044 | 0.92371 | 0.94868 | 0.21945 | 0.032362 | 0.00029686 | 3.2725 | 120.5093 | ok
64197 | Fifth Standard Solar PV, LLC (Hybrid) | TRUE | <1.5h | CS | 137 | 28 | 28 | TRUE | 0.93238 | 1.5425 | 1.1259 | 1.5237 | 1.0728 | 1.2203 | 0.45088 | 0.32911 | 0.85795 | 0.85451 | 0.85694 | 0.57542 | 0.017334 | 0.25984 | 0.19589 | 6.9229 | ok
64198 | Horn Rapids Solar, Storage and Training | TRUE | 2.5-4.5h | CS | 1 | 36 | 36 | FALSE | 1.0803 | 0.0017637 | 0.17637 | 0.0021115 | 0.011893 | 0.01632 | -0.0097818 | -0.97818 | 1.1123 | 0.79371 | 0.79998 | 0.0024876 | 0.10716 | 0.0060569 | 2.218 | 232.1889 | ok
64207 | Crane Battery Energy Storage System | FALSE | <1.5h | CS | 5 | 23 | 23 | TRUE | 0.91335 | 0.0050732 | 0.10146 | 0.0053395 | 0.0070135 | 0.0020686 | -0.001674 | -0.03348 | 0.88804 | 0.87986 | 0.8984 | 0.21892 | 0.020323 | 0.0020911 | -1.3195 | 309.0985 | ok
64213 | Auburn Solar Project | TRUE | 1.5-2.5h | CS | 3.8 | 33 | 33 | TRUE | 0.8986 | 0.0025503 | 0.067113 | 0.0010135 | 0.0012633 | 0.0032572 | -0.00024975 | -0.0065724 | 0.8824 | 0.86372 | 0.89116 | 0.35278 | 0.027433 | 0.00062042 | 4.4218 | 25.9025 | ok
64222 | Burt County Solar Hybrid | TRUE | 2.5-4.5h | CS | 0.7 | 36 | 36 | TRUE | 0.91067 | -9.1812e-05 | -0.013116 | -9.0129e-05 | -0.00013296 | 1.0853e-05 | 4.2834e-05 | 0.0061192 | 0.91868 | 0.92105 | 0.91667 | 0.033827 | 0.013247 | 8.415e-05 | -4.9068 | -158.6772 | ok
64223 | Dodge County Solar Hybrid | TRUE | 2.5-4.5h | CS | 0.7 | 35 | 35 | TRUE | 0.89278 | -0.0004452 | -0.0636 | -0.00044217 | -0.0004323 | -0.00041526 | -9.8752e-06 | -0.0014107 | 0.91435 | 0.92692 | 0.90909 | 0.27475 | 0.013438 | 0.00012591 | -0.3402 | -31.0113 | ok
64231 | Hadley 3 Solar (North) | TRUE | 2.5-4.5h | CS | 1 | 12 | 12 | TRUE | 0.90893 | 0.0030493 | 0.30493 | 0.012905 | 0.013013 | 0.0090824 | -0.0001081 | -0.01081 | 0.85287 | 0.85178 | 0.8554 | 0.21459 | 0.046217 | 0.0018447 |  |  | insufficient_history
64256 | AES Maui Kuihelani Solar Hybrid | TRUE | 2.5-4.5h | CS | 60 | 17 | 17 | FALSE | 1.0479 | 0.56966 | 0.94944 | 0.54434 | 0.6351 | 0.54307 | -0.090763 | -0.15127 | 0.97462 | 0.97448 | 0.97832 | 0.10593 | 0.054399 | 0.42731 |  |  | insufficient_history
64293 | Alvin | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.94288 | 0.015546 | 0.15703 | 0.015786 | 0.013693 | 0.015436 | 0.0020927 | 0.021138 | 0.92388 | 0.92006 | 0.9215 | 0.85789 | 0.0028883 | 0.001349 | -2.9445 | -61.5833 | ok
64294 | Odessa | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.95354 | 0.022859 | 0.2309 | 0.020787 | 0.024069 | 0.022796 | -0.0032815 | -0.033146 | 0.92422 | 0.92073 | 0.92338 | 0.88852 | 0.0032486 | 0.0017263 | -3.1998 | -90.7806 | ok
64295 | Angleton | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.93027 | 0.010999 | 0.1111 | 0.025507 | 0.014596 | 0.013437 | 0.010911 | 0.11022 | 0.91718 | 0.91542 | 0.92049 | 0.085759 | 0.013751 | 0.0076567 | -1.3634 | 4.796 | ok
64296 | Brazoria | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.9418 | 0.013996 | 0.14137 | 0.0029711 | 0.0067744 | 0.011444 | -0.0038033 | -0.038417 | 0.9239 | 0.92175 | 0.92292 | 0.37711 | 0.006869 | 0.003835 | -1.1939 | -24.9447 | ok
64297 | Heights | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.93018 | 0.0074034 | 0.074782 | 0.0054551 | 0.0038859 | 0.0067324 | 0.0015692 | 0.015851 | 0.92177 | 0.92037 | 0.91974 | 0.13463 | 0.0067488 | 0.0040017 | -2.9192 | -46.0156 | ok
64298 | Magnolia TX | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.91928 | -0.0019587 | -0.019784 | -0.0033577 | 0.0017166 | 0.00553 | -0.0050744 | -0.051256 | 0.92437 | 0.92299 | 0.92228 | 0.030565 | 0.0062036 | 0.0023518 | -9.354 | -276.8144 | ok
64312 | Bat Cave | FALSE | <1.5h | CS | 100 | 51 | 51 | TRUE | 0.85162 | 0.68933 | 0.68933 | 0.86515 | 0.74508 | 0.62918 | 0.12007 | 0.12007 | 0.76758 | 0.75705 | 0.76642 | 0.72544 | 0.014871 | 0.060583 | 2.7566 | 34.3119 | ok
64314 | Dickinson | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.9263 | 0.0023861 | 0.024102 | 0.0063989 | 0.0077751 | 0.0029213 | -0.0013762 | -0.013901 | 0.92396 | 0.9228 | 0.92467 | 0.046683 | 0.004686 | 0.0022988 | -4.6362 | -174.3227 | ok
64315 | Loop 463 | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.94573 | 0.019251 | 0.19446 | 0.014855 | 0.015326 | 0.018323 | -0.0004705 | -0.0047526 | 0.92143 | 0.9189 | 0.92077 | 0.724 | 0.0044896 | 0.0025342 | -0.10245 | 5.0165 | ok
64316 | Lopeno | FALSE | <1.5h | CS | 9.9 | 36 | 36 | TRUE | 0.96808 | 0.028848 | 0.29139 | 0.036767 | 0.038187 | 0.029464 | -0.0014198 | -0.014342 | 0.92831 | 0.91199 | 0.90336 | 0.8486 | 0.0091602 | 0.0020897 | -2.2123 | -85.3568 | ok
64317 | North Fork TX | FALSE | <1.5h | CS | 100 | 50 | 50 | TRUE | 0.80552 | 0.40881 | 0.40881 | 0.86437 | 0.59969 | 0.38293 | 0.26469 | 0.26469 | 0.7633 | 0.74578 | 0.75845 | 0.24023 | 0.025366 | 0.10493 | 6.7575 | 62.7073 | ok
64318 | Pueblo BA | FALSE | <1.5h | CS | 19.8 | 36 | 36 | TRUE | 0.92569 | 0.060505 | 0.30558 | 0.068595 | 0.067128 | 0.061231 | 0.0014673 | 0.0074104 | 0.88672 | 0.87259 | 0.88273 | 0.9645 | 0.0034516 | 0.0019909 | -1.6454 | -25.9747 | ok
64319 | Ranchtown | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.93547 | 0.018885 | 0.19076 | 0.017363 | 0.014623 | 0.018444 | 0.0027401 | 0.027678 | 0.91072 | 0.9086 | 0.91053 | 0.64239 | 0.0055667 | 0.0030041 | -2.8921 | -88.6541 | ok
64321 | Sweeny | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.92051 | -0.0007423 | -0.007498 | 0.0052719 | 0.0083386 | 4.7678e-05 | -0.0030667 | -0.030977 | 0.9228 | 0.92198 | 0.92417 | 0.00087054 | 0.011141 | 0.0053615 | -4.1713 | -75.652 | ok
64322 | Zapata | FALSE | <1.5h | CS | 19.8 | 36 | 36 | TRUE | 0.93268 | 0.05446 | 0.27505 | 0.063152 | 0.05176 | 0.054625 | 0.011392 | 0.057535 | 0.8965 | 0.88901 | 0.8952 | 0.95111 | 0.0034878 | 0.0021176 | -1.8836 | -93.3452 | ok
64374 | Norwich Solar and Energy Storage CSG | TRUE | 2.5-4.5h | CS | 5 | 15 | 15 | TRUE | 0.83305 | 7.854e-05 | 0.0015708 | 0.0036791 | 0.0002378 |  | 0.0034413 | 0.068825 | 0.88235 | 0.77867 | 0.83333 | 0.00035342 | 0.11044 | 0.0011585 |  |  | insufficient_history
64395 | ZPD-PT Solar Project 2017-006 LLC Hybrid | TRUE | 1.5-2.5h | CT | 2.5 | 35 | 35 | TRUE | 0.78096 | -0.00047134 | -0.018853 | -0.0044 | -0.0017709 | 0.0016467 | -0.0026291 | -0.10516 | 0.83402 | 0.79906 | 0.84783 | 0.0046787 | 0.07126 | 0.0011967 | 9.8891 | 157.1732 | ok
64400 | BYU - Hawaii | TRUE | <1.5h | CS | 1.9 | 12 | 12 | TRUE | 0.89749 | 0.0076518 | 0.40272 | 0.0091577 | 0.01061 | 0.0085879 | -0.0014524 | -0.076443 | 0.85566 | 0.85559 | 0.85663 | 0.07519 | 0.061354 | 0.0084861 |  |  | insufficient_history
64423 | TX7 Flat Top | FALSE | 1.5-2.5h | CS | 9.9 | 17 | 17 | TRUE | 0.85489 | -0.00038398 | -0.0038786 | 0.00060229 | 0.0097743 | 0.0039445 | -0.009172 | -0.092647 | 0.86014 | 0.8564 | 0.85382 | 0.00059035 | 0.014064 | 0.0040792 | -5.0812 | -160.7191 | ok
64424 | TX8 Worsham | FALSE | 1.5-2.5h | CS | 9.9 | 19 | 19 | TRUE | 0.89225 | 0.028488 | 0.28775 | 0.027747 | 0.036899 | 0.033172 | -0.0091523 | -0.092448 | 0.81616 | 0.64287 | 0.82014 | 0.97034 | 0.025713 | 0.001208 |  |  | insufficient_history
64425 | TX2 Port Lavaca | FALSE | <1.5h | CS | 9.9 | 8 |  | FALSE | [9 empty] | 0.31955 | [6 empty] | insufficient_history
64426 | Wilmot Energy Center LLC | TRUE | 1.5-2.5h | CS | 30 | 55 | 55 | TRUE | 0.95268 | 0.22939 | 0.76463 | 0.23875 | 0.17635 | 0.32616 | 0.062409 | 0.20803 | 0.85653 | 0.84331 | 0.87713 | 0.64186 | 0.026228 | 0.023537 | 1.2347 | -0.24275 | ok
64432 | Breckenridge Solar | TRUE | 1.5-2.5h | CS | 2.2 | 32 | 32 | TRUE | 0.85091 | 0.0040385 | 0.18357 | 0.0036453 | 0.0044962 | 0.0043685 | -0.00085094 | -0.038679 | 0.79401 | 0.73757 | 0.77184 | 0.61248 | 0.049439 | 0.00058648 | 12.1231 | 78.7071 | ok
64436 | Wilmarth Solar | TRUE | 1.5-2.5h | CS | 2.3 | 26 | 26 | TRUE | 0.90288 | 0.0056009 | 0.24352 | 0.0045054 | 0.0046886 | 0.007985 | -0.00018328 | -0.0079689 | 0.82491 | 0.67152 | 0.8 | 0.65858 | 0.056876 | 0.00082318 | -5.6644 | -20.223 | ok
64442 | Mt Pleasant Community Center | TRUE | 2.5-4.5h | CS | 0.7 | 5 |  | FALSE | [9 empty] | 0.90218 | [6 empty] | insufficient_history
64446 | Arlington Microgrid | TRUE | <1.5h | CS | 1 | 29 | 29 | TRUE | 0.73878 | 0.00028455 | 0.028455 | 0.0029152 | 0.0022603 | 0.00030257 | 0.00065491 | 0.065491 | 0.80882 | 0.71272 | 0.85714 | 0.012009 | 0.14353 | 0.0004967 | -3.5772 | 81.8706 | ok
64450 | Grissom Solar, LLC | TRUE | <1.5h | CS | 10 | 33 | 33 | TRUE | 0.85338 | 0.0018346 | 0.018346 | 0.00012409 | 0.0013653 | 0.0017135 | -0.0012412 | -0.012412 | 0.83644 | 0.83842 | 0.875 | 0.036921 | 0.040383 | 0.0016828 | -4.1141 | 96.6121 | ok
64481 | Arlington Energy Center II | TRUE | 2.5-4.5h | CT | 132 | 41 | 41 | TRUE | 0.84763 | 0.048473 | 0.036722 | 0.32299 | -0.0071637 | -0.075552 | 0.33015 | 0.25011 | 0.84733 | 0.84657 | 0.84453 | 0.0014257 | 0.017559 | 0.20542 | -1.8737 | -111.7583 | ok
64489 | Resurgence Solar | TRUE | 2.5-4.5h | CS | 75 | 29 | 29 | TRUE | 0.84459 | -0.095791 | -0.12772 | 0.27417 | -0.059312 | -0.037348 | 0.33348 | 0.44464 | 0.85331 | 0.85494 | 0.85815 | 0.033827 | 0.015134 | 0.098523 | 1.0405 | 70.2629 | ok
64508 | Hall Solar Energy Storage | TRUE | 1.5-2.5h | CS | 2.5 | 31 | 31 | TRUE | 0.76372 | 0.0060685 | 0.24274 | 0.01523 | 0.0090662 | 0.0066908 | 0.0061637 | 0.24655 | 0.66185 | 0.60531 | 0.625 | 0.3623 | 0.092169 | 0.001495 | -10.9083 | -6.7309 | ok
64509 | South River H4 Solar Energy Storage | TRUE | 1.5-2.5h | CS | 0.6 | 28 | 28 | TRUE | 0.73349 | -2.0245e-05 | -0.0033741 | -0.00039207 | 0.00029196 | 0.0010811 | -0.00068403 | -0.11401 | 0.7551 | 0.76698 | 0.75 | 0.00012827 | 0.10357 | 0.00035053 | 20.0483 | 155.4621 | ok
64510 | Arba Solar Energy Storage | TRUE | 1.5-2.5h | CS | 5.1 | 36 | 36 | TRUE | 0.92772 | 0.01325 | 0.2598 | 0.014895 | 0.011556 | 0.014141 | 0.003339 | 0.065471 | 0.75973 | 0.73878 | 0.75623 | 0.69647 | 0.038423 | 0.0015001 | -0.82563 | 0.39108 | ok
64511 | Rose Acre Solar Energy Storage | TRUE | 1.5-2.5h | CS | 2.5 | 34 | 34 | TRUE | 0.85206 | 0.012372 | 0.49489 | 0.014605 | 0.013136 | 0.0084751 | 0.0014692 | 0.058768 | 0.64233 | 0.62036 | 0.63174 | 0.53658 | 0.091945 | 0.0020326 | -1.4444 | 15.4543 | ok
64512 | Hamlet Solar Energy Storage | TRUE | 1.5-2.5h | CS | 0.5 | 35 | 35 | TRUE | 0.786 | 0.00075965 | 0.15193 | 0.00081662 | 0.0018054 | 0.0024373 | -0.00098879 | -0.19776 | 0.70857 | 0.69364 | 0.71429 | 0.17553 | 0.090225 | 0.00028659 | 8.5707 | 94.4743 | ok
64513 | Wake RJ3 Solar Energy Storage | TRUE | 1.5-2.5h | CS | 0.6 | 28 | 28 | TRUE | 0.69068 | 0.00020504 | 0.034174 | 5.306e-05 | 0.0007327 | 0.0023556 | -0.00067964 | -0.11327 | 0.69565 | 0.66572 | 0.73214 | 0.011615 | 0.13846 | 0.00037095 | 15.4839 | 180.9181 | ok
64514 | Ludie Brown Solar Energy Storage | TRUE | <1.5h | CS | 2.5 | 35 | 35 | TRUE | 0.77384 | 0.0070566 | 0.28226 | 0.013154 | 0.00782 | 0.0047825 | 0.0053342 | 0.21337 | 0.65271 | 0.62634 | 0.64865 | 0.29563 | 0.10043 | 0.0018961 | -3.3724 | 23.0906 | ok
64516 | Lowe Solar Energy Storage | TRUE | 1.5-2.5h | CS | 2.5 | 35 | 35 | TRUE | 0.80414 | 0.0076733 | 0.30693 | 0.013491 | 0.0076517 | 0.0067297 | 0.0058397 | 0.23359 | 0.65774 | 0.63645 | 0.65385 | 0.29248 | 0.10781 | 0.0020775 | -5.0093 | 21.5959 | ok
64520 | Spencer Meadow Solar Energy Storage | TRUE | 1.5-2.5h | CS | 2.5 | 34 | 34 | TRUE | 0.87253 | 0.0068754 | 0.27502 | 0.0094544 | 0.0061297 | 0.004854 | 0.0033248 | 0.13299 | 0.71492 | 0.68485 | 0.69848 | 0.53879 | 0.07081 | 0.0011245 | -0.5373 | 15.1054 | ok
64522 | Old Cedar Solar Energy Storage | TRUE | 1.5-2.5h | CS | 1.3 | 35 | 35 | TRUE | 0.83516 | 0.003318 | 0.25523 | 0.005536 | 0.0031182 | 0.0035925 | 0.0024178 | 0.18598 | 0.69709 | 0.67027 | 0.69231 | 0.59599 | 0.05267 | 0.00047555 | -9.7326 | -48.9338 | ok
64528 | Gambit Energy Storage - Angleton Storage | FALSE | 1.5-2.5h | CS | 100 | 54 | 54 | TRUE | 0.7849 | 0.34527 | 0.34527 | 0.30585 | 0.72283 | 0.42136 | -0.41698 | -0.41698 | 0.75432 | 0.74463 | 0.74514 | 0.15972 | 0.037545 | 0.10982 | 3.454 | 41.0069 | ok
64529 | Golden Triangle | TRUE | 2.5-4.5h | CS | 50 | 11 | 11 | TRUE | 0.88343 | 0.30477 | 0.60953 | 0.28233 | 0.30053 |  | -0.018195 | -0.036391 | 0.82945 | 0.82221 | 0.83646 | 0.38448 | 0.039763 | 0.12854 |  |  | insufficient_history
64545 | Ranchland Wind Storage | FALSE | <1.5h | CS | 73 | 16 | 16 | TRUE | 0.97981 | 0.69123 | 0.9469 | 0.70713 | 0.73563 | 0.87258 | -0.028502 | -0.039043 | 0.79949 | 0.79215 | 0.80959 | 0.70045 | 0.044339 | 0.12081 |  |  | insufficient_history
64546 | Wynwood Energy Storage | FALSE | 2.5-4.5h | BL | 10 | 24 | 24 | TRUE | 0.83396 | 0.044218 | 0.44218 | 0.051136 | 0.041386 | 0.041385 | 0.0097496 | 0.097496 | 0.75466 | 0.75132 | 0.75031 | 0.55923 | 0.025763 | 0.0083695 | 17.657 | 152.9185 | ok
64564 | Arlington Energy Center III | TRUE | 2.5-4.5h | CT | 110 | 41 | 41 | TRUE | 0.83188 | 0.12898 | 0.11726 | 0.47952 | 0.24176 | -0.091 | 0.23776 | 0.21615 | 0.82544 | 0.82531 | 0.83189 | 0.00724 | 0.028865 | 0.24185 | 0.40332 | -103.4428 | ok
64601 | County of San Diego COC Hybrid | TRUE | 2.5-4.5h | CS | 0.4 | 32 | 32 | TRUE | 0.87494 | -0.0037306 | -0.93265 | -0.0042482 | -0.0086196 | -0.009217 | 0.0043714 | 1.0928 | 1.1152 | 0.75129 | 0.81653 | 0.050575 | 0.22866 | 0.0029511 |  |  | ok
64611 | SEPV Sierra | TRUE | <1.5h | CS | 8.3 | 36 | 36 | FALSE | 1.4631 | 0.046024 | 0.55451 | 0.02664 | -0.089152 | -0.10969 | 0.11579 | 1.3951 | 1.3414 | 0.93648 | 0.94378 | 0.0026616 | 0.18872 | 0.15279 | -5.8137 | -283.4072 | ok
64612 | Kearny North Energy Storage | FALSE | 2.5-4.5h | CS | 10 | 16 | 16 | TRUE | 0.86576 | 0.052993 | 0.52993 | 0.047047 | 0.057882 | 0.035148 | -0.010835 | -0.10835 | 0.8126 | 0.80896 | 0.81085 | 0.2767 | 0.03863 | 0.022899 |  |  | insufficient_history
64614 | Kearny South Energy Storage | FALSE | 2.5-4.5h | CS | 10 | 24 | 24 | TRUE | 0.85693 | 0.037152 | 0.37152 | 0.055785 | 0.037848 | 0.046782 | 0.017937 | 0.17937 | 0.83114 | 0.81905 | 0.82882 | 0.76717 | 0.0089124 | 0.0043636 | 5.2175 | 74.6177 | ok
64617 | Kearsarge William Way | TRUE | 2.5-4.5h | CS | 2.6 | 36 | 36 | TRUE | 0.9249 | 0.0096706 | 0.37195 | 0.010991 | 0.0098138 | 0.0093389 | 0.0011768 | 0.045263 | 0.89239 | 0.88451 | 0.89353 | 0.92799 | 0.0036361 | 0.00046201 | -1.3935 | -26.2825 | ok
64618 | Kearsarge Haverhill | TRUE | >4.5h | CS | 2 | 30 | 30 | TRUE | 0.85219 | 0.0053492 | 0.26746 | 0.005366 | 0.0079378 | 0.013801 | -0.0025717 | -0.12859 | 0.83658 | 0.82231 | 0.84029 | 0.84595 | 0.008819 | 0.00043139 | -3.1706 | -36.1693 | ok
64619 | Kearsarge Upper Union | TRUE | >4.5h | CS | 0.8 | 33 | 33 | TRUE | 0.92088 | 0.00219 | 0.27375 | 0.0033791 | 0.0016694 | 0.0010157 | 0.0017097 | 0.21371 | 0.89725 | 0.892 | 0.91549 | 0.1515 | 0.025502 | 0.00093086 | 1.3116 | -30.8791 | ok
64620 | Kearsarge Montague BD(CSG) | TRUE | 2.5-4.5h | CS | 1.3 | 36 | 36 | TRUE | 0.9263 | 0.013159 | 1.0122 | 0.014348 | 0.01394 | 0.013415 | 0.00040781 | 0.03137 | 0.84123 | 0.82941 | 0.84502 | 0.83729 | 0.010947 | 0.00099481 | -1.7482 | -8.7984 | ok
64624 | Hudson - High Desert Hybrid | TRUE | <1.5h | CS | 50 | 49 | 49 | TRUE | 0.88818 | 0.10156 | 0.20312 | 0.08361 | 0.0012441 | 0.093488 | 0.082366 | 0.16473 | 0.87548 | 0.87525 | 0.87497 | 0.055427 | 0.011977 | 0.061154 | 2.5336 | 65.5819 | ok
64627 | Blodgett Solar CSG | TRUE | <1.5h | CS | 5 | 19 | 19 | TRUE | 0.90951 | 0.0053695 | 0.10739 | 0.0052543 | 0.0036824 | -0.0039943 | 0.0015718 | 0.031437 | 0.82484 | 0.46017 | 0.81579 | 0.62293 | 0.054913 | 0.0010132 |  |  | insufficient_history
64630 | Rabbitbrush Solar, LLC | TRUE | 2.5-4.5h | CS | 20 | 39 | 39 | TRUE | 0.8556 | 0.017078 | 0.085388 | 0.028154 | 0.01826 | 0.01105 | 0.0098947 | 0.049473 | 0.85049 | 0.84891 | 0.85621 | 0.020371 | 0.015195 | 0.019469 | 2.6376 | 48.5133 | ok
64633 | Rexford Solar Farm | TRUE | 2.5-4.5h | CS | 240 | 11 | 11 | TRUE | 0.93155 | 1.7248 | 0.71869 | 4.14 | 3.2385 |  | 0.90149 | 0.37562 | 0.88711 | 0.88265 | 0.87108 | 0.38912 | 0.029554 | 0.72039 |  |  | insufficient_history
64636 | Big Rock Solar Farm | FALSE | <1.5h | CS | 200 | 7 |  | FALSE | [9 empty] | 0.70547 | [6 empty] | insufficient_history
64640 | Hot Springs Energy Storage & Microgrid | TRUE | <1.5h | CS | 4.4 | 28 | 28 | TRUE | 0.8571 | 0.0061293 | 0.1393 | 0.0058077 | 0.010212 | 0.0084705 | -0.0044041 | -0.10009 | 0.78799 | 0.7097 | 0.78679 | 0.58516 | 0.060756 | 0.0010121 |  |  | ok
64656 | AES West Oahu Solar Hybrid | TRUE | 2.5-4.5h | CS | 12.5 | 18 | 18 | FALSE | 1.0887 | 0.16767 | 1.3414 | 0.19519 | 0.25906 | 0.20613 | -0.063874 | -0.51099 | 0.9846 | 0.98454 | 0.97714 | 0.092844 | 0.076932 | 0.13103 |  |  | insufficient_history
64664 | Clark Road Solar 1, LLC | TRUE | <1.5h | CS | 3.3 | 36 | 36 | FALSE | 1.0072 | 0.015664 | 0.47465 | 0.023344 | 0.020469 | 0.01709 | 0.0028748 | 0.087115 | 0.88747 | 0.87813 | 0.89859 | 0.75724 | 0.017436 | 0.001521 | 5.0416 | 148.7778 | ok
64672 | Blue Jay Solar I, LLC | TRUE | 1.5-2.5h | CS | 51.6 | 31 | 31 | TRUE | 0.75549 | 0.1624 | 0.31472 | 0.16534 | 0.29241 | 0.31631 | -0.12707 | -0.24626 | 0.71564 | 0.68284 | 0.6888 | 0.48529 | 0.04147 | 0.031057 | 7.4084 | 24.1872 | ok
64686 | Orangeville Storage | TRUE | <1.5h | OT | 24.7 | 36 | 36 | TRUE | 0.86179 | 0.12772 | 0.51707 | 0.17419 | 0.040507 | 0.093321 | 0.13368 | 0.54122 | 0.81003 | 0.82644 | 0.82476 | 0.017559 | 0.12862 | 0.16384 | -0.99321 | -5.4219 | ok
64695 | Angel Fire Energy Facility | TRUE | 2.5-4.5h | CS | 3.7 | 28 | 28 | TRUE | 0.89142 | 0.02132 | 0.57621 | 0.015098 | 0.02088 | 0.022044 | -0.0057815 | -0.15626 | 0.822 | 0.76354 | 0.82933 | 0.94268 | 0.0091419 | 0.001031 | -3.2687 | -31.4653 | ok
64696 | Dunstable Solar 1, LLC | TRUE | 2.5-4.5h | CS | 4.5 | 36 | 36 | FALSE | 1.006 | 0.0045351 | 0.10078 | -0.020656 | 0.0030178 | 0.0042135 | -0.023674 | -0.5261 | 0.97918 | 0.95613 | 0.96895 | 0.030673 | 0.040459 | 0.0043722 | 0.89603 | 185.9976 | ok
64701 | LeConte Energy Storage | FALSE | 1.5-2.5h | CS | 125 | 40 | 40 | TRUE | 0.86386 | 0.58065 | 0.46452 | 0.48785 | 0.3321 | 0.49886 | 0.15574 | 0.1246 | 0.82117 | 0.82203 | 0.80411 | 0.033129 | 0.055255 | 0.50886 | -2.4742 | 29.5818 | ok
64712 | Sanborn BESS 1 | FALSE | 1.5-2.5h | CS | 100 | 50 | 50 | TRUE | 0.93574 | 1.2689 | 1.2689 | 1.4628 | 1.4219 | 1.1932 | 0.040973 | 0.040973 | 0.82321 | 0.82106 | 0.81801 | 0.41431 | 0.026237 | 0.21776 | 1.0726 | 11.9496 | ok
64713 | Sanborn BESS 2 | FALSE | 2.5-4.5h | CS | 100 | 50 | 50 | TRUE | 0.9207 | 1.2883 | 1.2883 | 1.4285 | 1.309 | 1.1326 | 0.11948 | 0.11948 | 0.85497 | 0.85239 | 0.85456 | 0.38783 | 0.016416 | 0.23362 | -0.62767 | -5.7973 | ok
64719 | Glenmere Lake | TRUE | 2.5-4.5h | CT | 2 | 34 | 34 | TRUE | 0.91193 | 2.5886e-05 | 0.0012943 | 2.6534e-05 | 0.0002683 | 0.00028131 | -0.00024176 | -0.012088 | 0.93814 | 0.93009 | 0.92821 | 0.00028168 | 0.036836 | 0.00027262 | -6.7815 | -134.1362 | ok
64726 | West Haydenville PJ Community Solar | TRUE | 1.5-2.5h | CT | 3.6 | 32 | 32 | TRUE | 0.96924 | 0.0057377 | 0.15938 | -0.0010175 | 0.0024914 | 0.009776 | -0.0035089 | -0.09747 | 0.90743 | 0.84646 | 0.90238 | 0.26938 | 0.044649 | 0.0017252 | 1.4478 | -67.4908 | ok
64727 | Brookwood Drive Community Solar | TRUE | 2.5-4.5h | OT | 3 | 34 | 34 | TRUE | 0.89038 | 0.00048959 | 0.01632 | 0.00054955 | 0.00016199 | 0.00049566 | 0.00038757 | 0.012919 | 0.86459 | 0.8888 | 0.94338 | 0.12464 | 0.040549 | 0.00022937 | -5.6493 | 5.2983 | ok
64731 | Maple(CSG) | TRUE | 1.5-2.5h | CS | 2.3 | 20 | 20 | FALSE | 0.44174 | -0.0013654 | -0.059366 | -0.0017319 | -0.0010001 | -0.0017093 | -0.0007318 | -0.031818 | 0.48456 | 0.63784 | 0.50714 | 0.48139 | 0.1558 | 0.00033404 |  |  | ok
64743 | Tierra Buena Energy Storage | FALSE | <1.5h | CS | 5 | 36 | 36 | TRUE | 0.93867 | 0.070261 | 1.4052 | 0.084507 | 0.071683 | 0.070736 | 0.012824 | 0.25648 | 0.84019 | 0.83346 | 0.84958 | 0.52681 | 0.023945 | 0.01142 | 1.8418 | 41.2586 | ok
64752 | John Hopkins Middle School Microgrid | TRUE | >4.5h | CS | 2.5 | 22 | 22 | TRUE | 0.81709 | 0.001213 | 0.048521 | 0.0035667 | 0.010798 | 0.0012159 | -0.007231 | -0.28924 | 0.86024 | 0.79224 | 0.83375 | 0.16472 | 0.051292 | 0.0006108 | 3.2873 | 45.6838 | ok
64759 | Old Middleboro Road Solar | TRUE | 2.5-4.5h | CS | 4.5 | 23 | 23 | TRUE | 0.89665 | -0.002003 | -0.044511 | -0.0040452 | -0.0024038 | -0.0020363 | -0.0016413 | -0.036474 | 0.90454 | 0.90606 | 0.90099 | 0.023257 | 0.01651 | 0.0028326 | -0.51481 | 100.3791 | ok
64760 | Ocean State BTM | FALSE | 2.5-4.5h | CS | 3 | 36 | 36 | TRUE | 0.92292 | 0.030392 | 1.0131 | 0.035756 | 0.027725 | 0.039923 | 0.0080311 | 0.2677 | 0.74864 | 0.74123 | 0.74408 | 0.42787 | 0.057519 | 0.0060273 | -14.114 | -77.0562 | ok
64761 | Patchogue ESS | FALSE | >4.5h | CS | 2 | 5 |  | FALSE | [9 empty] | 0.90286 | [6 empty] | insufficient_history
64763 | Rumford ESS | FALSE | 1.5-2.5h | CS | 4.9 | 22 | 22 | TRUE | 0.59848 | -0.0055185 | -0.11262 | -0.0050089 | -0.0068736 | -0.0064666 | 0.0018647 | 0.038054 | 0.64476 | 0.66294 | 0.63917 | 0.096819 | 0.1322 | 0.0037689 | 0.095003 | 161.0853 | ok
64764 | Madison BTM | FALSE | 1.5-2.5h | CS | 1.5 | 22 | 22 | TRUE | 0.6542 | -0.00080733 | -0.053822 | -0.0012881 | -0.00080778 | 0.00053534 | -0.00048034 | -0.032023 | 0.63443 | 0.70224 | 0.64832 | 0.11632 | 0.082835 | 0.00049758 | -16.3247 | 13.4586 | ok
64765 | Madison ESS | FALSE | 1.5-2.5h | CS | 4.9 | 22 | 22 | TRUE | 0.58379 | -0.004273 | -0.087204 | -0.00049638 | -0.015089 | -0.013848 | 0.014592 | 0.2978 | 0.60698 | 0.66099 | 0.57163 | 0.017564 | 0.21265 | 0.0071458 |  |  | ok
64766 | Redwood Coast Airport Microgrid | TRUE | 2.5-4.5h | CS | 2.2 | 19 | 19 | TRUE | 0.87677 | 0.034564 | 1.5711 | 0.083022 | 0.038991 | 0.021092 | 0.044031 | 2.0014 | 0.78012 | 0.5 | 0.85561 | 0.16853 | 0.15959 | 0.01862 |  |  | ok
64811 | Upton County BESS | FALSE | <1.5h | CS | 24.8 | 23 | 23 | TRUE | 0.83197 | 0.058708 | 0.23673 | 0.11508 | 0.12418 | 0.049079 | -0.0091081 | -0.036726 | 0.77778 | 0.73303 | 0.77623 | 0.63505 | 0.051467 | 0.0097117 |  |  | insufficient_history
64844 | Three Rivers Solar LLC | TRUE | 1.5-2.5h | CS | 1.4 | 8 |  | FALSE | [9 empty] | 0.84727 | [6 empty] | insufficient_history
64851 | Daggett 2 | TRUE | <1.5h | CS | 131 | 23 | 23 | TRUE | 0.96015 | 1.0556 | 0.80581 | 0.43451 | -0.16736 | 0.9782 | 0.60187 | 0.45944 | 0.9063 | 0.90806 | 0.91757 | 0.03192 | 0.084667 | 1.2686 |  |  | insufficient_history
64852 | Daggett 3 | TRUE | <1.5h | CS | 149 | 28 | 28 | TRUE | 0.91085 | -0.20654 | -0.13862 | -0.22031 | 0.24027 | 0.35247 | -0.46058 | -0.30912 | 0.92155 | 0.92395 | 0.93696 | 0.022768 | 0.019675 | 0.26537 | -3.6916 | 94.1363 | ok
64864 | Chaparral Springs | TRUE | 2.5-4.5h | CS | 88 | 9 |  | FALSE | [9 empty] | 0.85812 | [6 empty] | insufficient_history
64875 | 276 Federal Rd(CSG) | TRUE | 1.5-2.5h | CS | 3.3 | 35 | 35 | TRUE | 0.73674 | 0.0050719 | 0.1537 | 0.0016971 | 0.0061698 | 0.0050983 | -0.0044727 | -0.13554 | 0.74108 | 0.66638 | 0.76923 | 0.16237 | 0.12987 | 0.0020053 | 8.7771 | -96.8655 | ok
64876 | 0 Hammond St CSG | TRUE | <1.5h | CS | 5 | 36 | 36 | TRUE | 0.91732 | 0.0076463 | 0.15293 | 0.0039274 | 0.0098489 | 0.0088835 | -0.0059215 | -0.11843 | 0.88939 | 0.87455 | 0.88036 | 0.16655 | 0.042779 | 0.0029335 | -2.6009 | 27.234 | ok
64877 | Edwards Sanborn E3 | TRUE | 2.5-4.5h | CS | 11 | 44 | 44 | TRUE | 0.88596 | 0.068176 | 0.61978 | 0.079969 | 0.071723 | 0.056778 | 0.0082459 | 0.074963 | 0.83427 | 0.83259 | 0.82114 | 0.11901 | 0.033259 | 0.028622 | 4.4142 | 74.0167 | ok
64878 | Edwards Sanborn E1A | TRUE | 1.5-2.5h | CS | 144 | 41 | 41 | TRUE | 0.81487 | -0.20823 | -0.14461 | -0.20792 | -0.25781 | -0.059455 | 0.049893 | 0.034648 | 0.83134 | 0.83161 | 0.82168 | 0.93534 | 0.008015 | 0.0087671 | 1.9295 | 13.3609 | ok
64879 | Edwards Sanborn E2 | TRUE | 1.5-2.5h | CS | 120 | 44 | 44 | TRUE | 0.88516 | 0.78251 | 0.65209 | 1.0052 | 0.90972 | 0.74916 | 0.095498 | 0.079582 | 0.81288 | 0.811 | 0.8106 | 0.28319 | 0.026438 | 0.1921 | -6.5877 | -68.2979 | ok
64908 | Scarlet Solar (CA) | TRUE | >4.5h | CS | 40 | 19 | 19 | TRUE | 0.87465 | 0.26794 | 0.66984 | 0.33669 | 0.57392 | 0.40345 | -0.23723 | -0.59307 | 0.8278 | 0.82575 | 0.83731 | 0.10331 | 0.052137 | 0.19145 |  |  | insufficient_history
64915 | Flower Valley I | FALSE | 1.5-2.5h | CS | 9.9 | 24 | 24 | TRUE | 0.9258 | 0.035179 | 0.35535 | 0.031783 | 0.032682 | 0.02862 | -0.00089937 | -0.0090846 | 0.88568 | 0.88563 | 0.88369 | 0.041691 | 0.050659 | 0.035959 | 12.8531 | 252.9179 | ok
64916 | Swoose I | FALSE | 1.5-2.5h | CS | 9.9 | 24 | 24 | TRUE | 0.93017 | 0.037949 | 0.38332 | 0.033868 | 0.033505 | 0.026802 | 0.00036349 | 0.0036716 | 0.88411 | 0.88356 | 0.88253 | 0.145 | 0.029787 | 0.019647 | 0.45947 | 34.2483 | ok
64917 | Triple Butte I | FALSE | 1.5-2.5h | CS | 7.5 | 24 | 24 | TRUE | 0.91182 | 0.018965 | 0.25286 | 0.01837 | 0.017002 | 0.018802 | 0.0013685 | 0.018247 | 0.88445 | 0.88433 | 0.88538 | 0.034723 | 0.039025 | 0.021318 | 8.6065 | 274.7674 | ok
64921 | Santa Ana Storage 2 | FALSE | 2.5-4.5h | CS | 20 | 12 | 12 | TRUE | 0.88991 | -0.06213 | -0.31065 | -0.083587 | -0.059645 | -0.08 | -0.023942 | -0.11971 | 0.89494 | 0.89544 | 0.89628 | 0.046943 | 0.010207 | 0.088527 |  |  | insufficient_history
64928 | Edwards Sanborn S3 | TRUE | 1.5-2.5h | CS | 33 | 42 | 42 | FALSE | 1.1125 | 0.77312 | 2.3428 | 0.85184 | 0.85425 | 0.76336 | -0.0024166 | -0.0073231 | 0.82097 | 0.82026 | 0.81535 | 0.41764 | 0.061684 | 0.14435 | 2.8411 | 12.2844 | ok
64929 | Edwards Sanborn S1 | TRUE | 1.5-2.5h | CS | 40 | 42 | 42 | TRUE | 0.83076 | -0.038845 | -0.097112 | -0.0353 | -0.05734 | -0.028634 | 0.02204 | 0.0551 | 0.84455 | 0.84854 | 0.85153 | 0.0095529 | 0.033997 | 0.062539 | -3.7 | -98.1388 | ok
64970 | 59 Federal Rd(CSG) | TRUE | 2.5-4.5h | CS | 5 | 21 | 21 | TRUE | 0.88007 | 0.040926 | 0.81852 | 0.057489 | 0.097704 | 0.036703 | -0.040215 | -0.8043 | 0.73674 | 0.61347 | 0.74257 | 0.48478 | 0.083285 | 0.0096793 | -8.609 | -28.152 | ok
64980 | UMass Boston | TRUE | 2.5-4.5h | BL | 0.5 | 27 | 27 | TRUE | 0.77373 | 0.0026009 | 0.52018 | 0.0019004 | 0.0026864 | 0.0066733 | -0.00078605 | -0.15721 | 0.72973 | 0.5892 | 0.72727 | 0.27226 | 0.13494 | 0.00085046 | 18.0811 | 133.708 | ok
64993 | BigBeau Solar, LLC | TRUE | 2.5-4.5h | CS | 40 | 36 | 36 | FALSE | 1.0491 | 0.41346 | 1.0336 | 0.40831 | 0.38627 | 0.45394 | 0.022043 | 0.055108 | 0.92737 | 0.91991 | 0.93027 | 0.31416 | 0.036864 | 0.10477 | 2.7267 | 241.5472 | ok
65014 | ASD Cotuit MA Solar LLC | TRUE | 1.5-2.5h | CS | 2.5 | 12 | 12 | TRUE | 0.97643 | 0.00064001 | 0.0256 | 0.00063863 | 0.00066708 | 0.0012682 | -2.8451e-05 | -0.001138 | 0.92424 | 0.64149 | 0.9075 | 0.31065 | 0.099096 | 0.00030149 |  |  | insufficient_history
65015 | ASD Wallum MA Solar LLC(CSG) | TRUE | 2.5-4.5h | CS | 3.8 | 33 | 33 | FALSE | 1.0065 | 0.0083307 | 0.21923 | 0.0059361 | 0.0098217 | 0.010782 | -0.0038855 | -0.10225 | 0.9554 | 0.77954 | 0.9548 | 0.85226 | 0.045105 | 0.00062296 | 0.10761 | 47.6376 | ok
65018 | Mossy Branch Battery Facility | FALSE | 2.5-4.5h | OT | 65 | 14 | 14 | TRUE | 0.89205 | 0.33081 | 0.50893 | 0.49485 | 0.44791 | 0.3922 | 0.046937 | 0.072211 | 0.86547 | 0.86396 | 0.86355 | 0.31349 | 0.016057 | 0.14132 |  |  | insufficient_history
65028 | Roseland Solar Project, LLC | TRUE | 1.5-2.5h | CS | 51.8 | 30 | 30 | TRUE | 0.79994 | 0.38853 | 0.75006 | 0.3822 | 0.50811 | 0.50929 | -0.12591 | -0.24306 | 0.67586 | 0.63692 | 0.64763 | 0.87763 | 0.034405 | 0.027418 | 10.7744 | 20.1882 | ok
65029 | Bissell Solar and Battery Generator | TRUE | 1.5-2.5h | BL | 0.3 | 12 | 12 | TRUE | 0.8708 | 0.0012043 | 0.40144 | 0.00082679 | 0.001062 | 0.001276 | -0.00023521 | -0.078405 | 0.73438 | 0.55306 | 0.66667 | 0.85898 | 0.072409 | 0.00015431 |  |  | ok
65035 | Fox Hills Battery Station | FALSE | 2.5-4.5h | CS | 7.5 | 15 | 15 | TRUE | 0.90022 | 0.05724 | 0.7632 | 0.025837 | 0.078979 | 0.11755 | -0.053143 | -0.70857 | 0.84668 | 0.80906 | 0.85939 | 0.28757 | 0.042622 | 0.024988 |  |  | insufficient_history
65044 | Dry Bridge Storage | FALSE | 2.5-4.5h | CS | 20 | 24 | 24 | TRUE | 0.95431 | 0.1684 | 0.842 | 0.15595 | 0.10711 | 0.1139 | 0.048845 | 0.24422 | 0.89957 | 0.89685 | 0.91525 | 0.16864 | 0.034729 | 0.079717 | -5.6905 | -243.4666 | ok
65053 | Blythe Mesa Solar II | TRUE | 2.5-4.5h | CS | 112 | 34 | 34 | TRUE | 0.93093 | 0.67341 | 0.60126 | 0.9538 | 0.69605 | 0.87224 | 0.25775 | 0.23013 | 0.89552 | 0.89402 | 0.89176 | 0.29557 | 0.01273 | 0.18378 | 2.6387 | 56.3078 | ok
65054 | 71 Charlotte Furnace Rd Hybrid(CSG) | TRUE | >4.5h | CS | 1 | 36 | 36 | TRUE | 0.88448 | 0.0016668 | 0.16668 | 0.00070199 | 0.0020118 | 0.0022599 | -0.0013099 | -0.13099 | 0.87011 | 0.85077 | 0.87088 | 0.2463 | 0.054765 | 0.00050006 | 0.6925 | 20.4573 | ok
65055 | 77 Farm to Market Rd Hybrid(CSG) | TRUE | 1.5-2.5h | CS | 2.2 | 30 | 30 | TRUE | 0.87578 | 0.0019113 | 0.086878 | 0.0032253 | 0.001851 | 0.0015294 | 0.0013742 | 0.062465 | 0.90403 | 0.6495 | 0.76389 | 0.44982 | 0.080934 | 0.00039947 | 6.5802 | 51.8561 | ok
65056 | 160 Tihonet Rd Hybrid(CSG) | TRUE | 1.5-2.5h | CS | 3.3 | 21 | 21 | TRUE | 0.9428 | 0.0029212 | 0.088521 | 0.005065 | -0.00025164 | 0.0037897 | 0.0053166 | 0.16111 | 0.8984 | 0.77737 | 0.91139 | 0.47557 | 0.082982 | 0.00070374 | -7.8839 | 27.3931 | ok
65057 | 299 Farm to Market Rd Hybrid(CSG) | TRUE | 1.5-2.5h | CS | 2.3 | 36 | 36 | TRUE | 0.84668 | -0.0049457 | -0.21503 | -0.0058803 | -0.00444 | -0.0045396 | -0.0014403 | -0.062624 | 0.98283 | 0.9371 | 1.0709 | 0.2742 | 0.068708 | 0.0013799 | 4.1933 | -79.5357 | ok
65058 | Waiawa Solar Power Hybrid | TRUE | <1.5h | CS | 36 | 30 | 30 | TRUE | 0.96914 | 0.18946 | 0.52627 | 0.12026 | 0.28225 | 0.12103 | -0.16199 | -0.44997 | 0.9239 | 0.91306 | 0.97594 | 0.33864 | 0.029372 | 0.050035 | -6.4196 | 182.2887 | ok
65098 | South Sioux City Energy Storage | FALSE | 1.5-2.5h | CS | 1.5 | 18 | 18 | TRUE | 0.78582 | -3.3491e-05 | -0.0022327 | -0.0001428 | -0.00031312 | 0.0023554 | 0.00017031 | 0.011354 | 0.87382 | 0.79099 | 0.81935 | 3.0593e-05 | 0.10328 | 0.0015137 |  |  | insufficient_history
65114 | 196 Tremont St(CSG) | TRUE | >4.5h | CS | 1.5 | 31 | 31 | TRUE | 0.7903 | -9.6719e-05 | -0.006448 | -0.00015773 | 0.0002512 | -0.00047026 | -0.00040893 | -0.027262 | 0.81606 | 0.77163 | 0.888 | 0.0053336 | 0.066247 | 0.00024527 | -1.6019 | 158.5156 | ok
65140 | Crimson | FALSE | 2.5-4.5h | CS | 350 | 39 | 39 | TRUE | 0.87457 | -0.48569 | -0.13877 | -0.35525 | -0.44527 | -0.29655 | 0.090012 | 0.025718 | 0.88212 | 0.88237 | 0.88298 | 0.0398 | 0.0083619 | 0.39219 | -1.1164 | -61.7587 | ok
65154 | UMass PV Lot 22 | TRUE | 1.5-2.5h | CS | 2 | 11 | 11 | TRUE | 0.77745 | 0.0058351 | 0.29175 | 0.0054804 | 0.0085986 | 0.0057377 | -0.0031181 | -0.15591 | 0.69679 | 0.6333 | 0.7 | 0.49371 | 0.17625 | 0.0019697 |  |  | insufficient_history
65174 | Cranberry Highway Solar LLC | TRUE | 1.5-2.5h | CS | 2 | 36 | 36 | TRUE | 0.94094 | 0.0003669 | 0.018345 | -0.0035813 | 0.0012584 | 2.7682e-05 | -0.0048397 | -0.24199 | 0.93608 | 0.95244 | 0.97466 | 0.0010038 | 0.064772 | 0.001985 | 10.1385 | 171.5639 | ok
65217 | South Goshen Community Solar | TRUE | 2.5-4.5h | OT | 4.5 | 33 | 33 | TRUE | 0.84243 | 0.0026557 | 0.059015 | 0.0025109 | 0.0091904 | 0.0085609 | -0.0066795 | -0.14843 | 0.86376 | 0.81149 | 0.82143 | 0.35577 | 0.031299 | 0.00064184 | -4.0842 | -56.5645 | ok
65239 | AE-ESS NWS 1, LLC | FALSE | >4.5h | CS | 5 | 7 |  | FALSE | [9 empty] | 0.86399 | [6 empty] | insufficient_history
65240 | Maysville BESS | FALSE | 1.5-2.5h | CS | 5 | 24 | 24 | TRUE | 0.76641 | 0.02573 | 0.5146 | 0.044968 | 0.028846 | 0.024459 | 0.016122 | 0.32245 | 0.61884 | 0.60601 | 0.6311 | 0.54981 | 0.079378 | 0.0049639 | -12.5287 | -56.8912 | ok
65241 | McKinney BESS | FALSE | 1.5-2.5h | CS | 5 | 24 | 24 | TRUE | 0.75647 | 0.02975 | 0.595 | 0.050933 | 0.033944 | 0.029114 | 0.016989 | 0.33978 | 0.57368 | 0.55359 | 0.5366 | 0.59406 | 0.10408 | 0.0052432 | -19.1091 | -62.175 | ok
65242 | Charlemont A | TRUE | 1.5-2.5h | CS | 2.5 | 14 | 14 | TRUE | 0.92833 | 0.00096191 | 0.038476 |  | -0.00010523 | 0.0047381 |  |  | 0.92481 | 0.89599 | 0.91349 | 0.12621 | 0.070653 | 0.00073062 |  |  | insufficient_history
65243 | New Rosewood BESS | FALSE | 2.5-4.5h | CS | 2.5 | 23 | 23 | TRUE | 0.80712 | 0.015574 | 0.62295 | 0.024372 | 0.015887 | 0.013918 | 0.0084851 | 0.3394 | 0.60837 | 0.58296 | 0.5942 | 0.63008 | 0.08833 | 0.002604 |  |  | ok
65244 | Queens Creek BESS | FALSE | 1.5-2.5h | CS | 2.5 | 23 | 23 | TRUE | 0.74284 | 0.013073 | 0.52291 | 0.026143 | 0.014828 | 0.013562 | 0.011315 | 0.45262 | 0.59502 | 0.56978 | 0.58333 | 0.54089 | 0.09372 | 0.0026282 | -4.2644 | -15.0072 | ok
65245 | Rocky Point BESS | FALSE | <1.5h | CS | 5 | 22 | 22 | TRUE | 0.77489 | 0.01398 | 0.27959 | 0.031091 | 0.016352 | 0.015448 | 0.014739 | 0.29478 | 0.60957 | 0.57105 | 0.60339 | 0.52063 | 0.099569 | 0.0029995 | -13.9171 | -63.3737 | ok
65246 | Walkers Crossroads BESS | FALSE | 1.5-2.5h | CS | 5 | 24 | 24 | TRUE | 0.76413 | 0.027513 | 0.55027 | 0.049795 | 0.028105 | 0.025405 | 0.021691 | 0.43382 | 0.60984 | 0.58837 | 0.58571 | 0.59931 | 0.088724 | 0.0047963 | -19.6192 | -75.0727 | ok
65247 | Zion Hill BESS | FALSE | 1.5-2.5h | CS | 5 | 24 | 24 | TRUE | 0.84647 | 0.037825 | 0.75651 | 0.054239 | 0.033375 | 0.028016 | 0.020864 | 0.41728 | 0.60143 | 0.57685 | 0.56955 | 0.65201 | 0.11429 | 0.0058916 | -21.0861 | -51.5355 | ok
65248 | Collier BESS | FALSE | 1.5-2.5h | CS | 2.5 | 24 | 24 | TRUE | 0.78737 | 0.014631 | 0.58524 | 0.021904 | 0.015552 | 0.013608 | 0.0063515 | 0.25406 | 0.61316 | 0.58869 | 0.60644 | 0.74225 | 0.069261 | 0.0018381 | -13.88 | -39.947 | ok
65249 | Docs Road BESS | FALSE | 1.5-2.5h | CS | 5 | 22 | 22 | TRUE | 0.73752 | 0.023906 | 0.47812 | 0.031202 | 0.022169 | 0.023105 | 0.0090328 | 0.18066 | 0.59829 | 0.55415 | 0.60081 | 0.8206 | 0.056247 | 0.0024994 | -14.5652 | -48.1898 | ok
65250 | Five Points BESS | FALSE | 1.5-2.5h | CS | 5 | 23 | 23 | TRUE | 0.87328 | 0.034364 | 0.68729 | 0.044506 | 0.02606 | 0.025305 | 0.018446 | 0.36892 | 0.63319 | 0.62118 | 0.64516 | 0.65701 | 0.088523 | 0.0054182 |  |  | ok
65259 | Byrd Ranch Storage | FALSE | <1.5h | CS | 50 | 29 | 29 | TRUE | 0.86009 | 0.22217 | 0.44434 | 0.21198 | 0.204 | 0.25128 | 0.0079761 | 0.015952 | 0.73898 | 0.6037 | 0.76234 | 0.92685 | 0.030631 | 0.012012 | 1.2934 | -6.7221 | ok
65271 | Noble Solar | TRUE | <1.5h | CS | 125 | 31 | 31 | TRUE | 0.88097 | 0.18293 | 0.14635 | 0.18901 | 0.21601 | 0.15274 | -0.026995 | -0.021596 | 0.79696 | 0.65553 | 0.83347 | 0.44476 | 0.076973 | 0.037955 | 5.948 | -105.4531 | ok
65291 | Golden Triangle II | TRUE | 2.5-4.5h | CS | 50 | 19 | 19 | TRUE | 0.99357 | 0.65242 | 1.3048 | 0.96759 | 0.83862 | 0.66421 | 0.12897 | 0.25795 | 0.81418 | 0.79495 | 0.81377 | 0.70442 | 0.047145 | 0.1025 |  |  | insufficient_history
65382 | Lincoln WWTF Hybrid | TRUE | 1.5-2.5h | CS | 1 | 12 | 12 | TRUE | 0.79206 | 0.0009945 | 0.09945 | 0.0066807 | 0.002291 | 0.0010694 | 0.0043897 | 0.43897 | 0.78481 | 0.75764 | 0.78117 | 0.91057 | 0.021278 | 9.8557e-05 |  |  | insufficient_history
65396 | Black Walnut Energy Storage LLC | FALSE | <1.5h | CS | 15 | 2 |  | FALSE | [9 empty] | 0.89259 | [6 empty] | insufficient_history
65397 | Santa Paula Energy Storage LLC | FALSE | <1.5h | CS | 30 | 14 | 14 | TRUE | 0.87257 | -0.074002 | -0.24667 | -0.065687 | -0.11124 | -0.11962 | 0.045558 | 0.15186 | 0.89956 | 0.9019 | 0.90324 | 0.040613 | 0.051643 | 0.10383 |  |  | insufficient_history
65408 | Gilead Oceanside Solar Project | TRUE | 2.5-4.5h | CT | 0.7 | 7 |  | FALSE | [9 empty] | 0.85504 | [6 empty] | insufficient_history
65409 | Gilead Foster City Solar Project | TRUE | 1.5-2.5h | CT | 0.5 | 36 | 36 | TRUE | 0.81278 | -0.0025527 | -0.51053 | -0.0036165 | -0.0034798 | -0.0027699 | -0.00013673 | -0.027346 | 0.87542 | 0.87323 | 0.875 | 0.54851 | 0.016515 | 0.00039718 | -8.2075 | -107.7373 | ok
65410 | Cunningham Storage | FALSE | 1.5-2.5h | CS | 190 | 29 | 29 | TRUE | 0.91724 | 0.69003 | 0.36317 | 0.65664 | 0.51938 | 0.67168 | 0.13725 | 0.072239 | 0.85443 | 0.84784 | 0.85571 | 0.73884 | 0.011378 | 0.078952 | -3.9994 | -42.6671 | ok
65422 | FPL Chipola River Solar Energy Center | TRUE | 2.5-4.5h | CS | 74.5 | 1 |  | FALSE | [9 empty] | 0.7489 | [6 empty] | insufficient_history
65429 | FPL Shirer Branch Solar Energy Center | TRUE | 2.5-4.5h | CS | 74.5 | 1 |  | FALSE | [9 empty] | 0.78501 | [6 empty] | insufficient_history
65433 | Blackwater River Solar Energy Center | TRUE | 2.5-4.5h | CS | 74.5 | 1 |  | FALSE | [9 empty] | 0.78165 | [6 empty] | insufficient_history
65441 | USS Itasca Clean Energy Solar LLC | TRUE | 2.5-4.5h | CS | 1 | 33 | 33 | TRUE | 0.7807 | 0.0020507 | 0.20507 | 0.00040076 | 0.0027485 | 0.0015911 | -0.0023477 | -0.23477 | 0.66061 | 0.63604 | 0.64286 | 0.11808 | 0.14878 | 0.0010065 | 2.9957 | 57.0581 | ok
65456 | Separator (Etiwanda) BESS | FALSE | 2.5-4.5h | CS | 112.5 | 11 | 11 | TRUE | 0.83033 | -0.19419 | -0.17261 | -0.73504 | -0.60208 |  | -0.13296 | -0.11819 | 0.84098 | 0.84309 | 0.83324 | 0.094359 | 0.020155 | 0.20053 |  |  | insufficient_history
65457 | Cathode (Hinson) BESS | FALSE | 2.5-4.5h | CS | 200 | 11 | 11 | TRUE | 0.84594 | 0.63173 | 0.31586 | 1.232 | 0.79459 |  | 0.43742 | 0.21871 | 0.82707 | 0.80782 | 0.82966 | 0.96341 | 0.0090859 | 0.041039 |  |  | insufficient_history
65468 | Highland Park Borough Solar | TRUE | 2.5-4.5h | BL | 0.6 | 8 |  | FALSE | [9 empty] | 0.62578 | [6 empty] | insufficient_history
65469 | Sealed Air Madera Solar Project | TRUE | 2.5-4.5h | CS | 0.8 | 36 | 36 | FALSE | 1.1201 | 0.015675 | 1.9594 | 0.0083667 | 0.011029 | 0.019382 | -0.002662 | -0.33275 | 0.87608 | 0.86616 | 0.8906 | 0.55245 | 0.056387 | 0.0024197 | 9.3463 | 218.9901 | ok
65472 | Chukar Battery Energy Storage System | FALSE | 2.5-4.5h | CS | 10 | 24 | 24 | TRUE | 0.93037 | 0.15973 | 1.5973 | 0.19051 | 0.17727 | 0.16314 | 0.013242 | 0.13242 | 0.8357 | 0.83531 | 0.83289 | 0.18409 | 0.055407 | 0.071694 | 2.3594 | 37.0681 | ok
65489 | Dickens | FALSE | <1.5h | CS | 200 | 11 | 11 | TRUE | 0.9098 | -0.26798 | -0.13399 | 0.14433 | 0.11726 |  | 0.02707 | 0.013535 | 0.92503 | 0.92555 | 0.92106 | 0.011665 | 0.056571 | 0.82223 |  |  | insufficient_history
65490 | Hydra | FALSE | <1.5h | CS | 200 | 11 | 11 | TRUE | 0.93013 | 0.73225 | 0.36612 | 0.11206 | -0.11028 |  | 0.22234 | 0.11117 | 0.89204 | 0.88779 | 0.87623 | 0.2638 | 0.031249 | 0.40775 |  |  | insufficient_history
65491 | Paleo | FALSE | <1.5h | CS | 200 | 11 | 11 | TRUE | 0.98965 | 2.0723 | 1.0362 | -0.16678 | -0.44637 |  | 0.27959 | 0.13979 | 0.86124 | 0.84096 | 0.82596 | 0.65066 | 0.046084 | 0.50616 |  |  | insufficient_history
65492 | Pavo | FALSE | <1.5h | CS | 175 | 13 | 13 | TRUE | 0.95828 | 0.14889 | 0.085082 | 0.85463 | 0.25409 | 0.23493 | 0.60054 | 0.34317 | 0.93806 | 0.94767 | 0.93846 | 0.02763 | 0.025181 | 0.26632 |  |  | insufficient_history
65493 | Tortolas | FALSE | <1.5h | CS | 50 | 10 | 10 | TRUE | 0.94856 | 0.28688 | 0.57376 | 0.29955 | 0.31836 |  | -0.018807 | -0.037614 | 0.87958 | 0.87924 | 0.87771 | 0.43069 | 0.033974 | 0.11661 |  |  | insufficient_history
65499 | Danville BESS 1 | FALSE | 1.5-2.5h | CS | 10.5 | 33 | 33 | TRUE | 0.8863 | 0.03742 | 0.35639 | 0.049026 | 0.038019 | 0.036653 | 0.011007 | 0.10483 | 0.86774 | 0.8252 | 0.86856 | 0.97605 | 0.0022234 | 0.0010528 | -0.1557 | 10.7661 | ok
65530 | Portage Industrial Battery | FALSE | 1.5-2.5h | CS | 5 | 24 | 24 | TRUE | 0.88173 | 0.033317 | 0.66634 | 0.035674 | 0.041822 | 0.032274 | -0.0061483 | -0.12297 | 0.75719 | 0.75196 | 0.75889 | 0.66139 | 0.031714 | 0.0050824 | -5.3216 | -23.3216 | ok
65531 | Deer Run Battery | FALSE | 1.5-2.5h | CS | 5 | 24 | 24 | TRUE | 0.77427 | 0.0085555 | 0.17111 | 0.0098592 | 0.014196 | 0.017078 | -0.0043369 | -0.086737 | 0.74536 | 0.74313 | 0.74183 | 0.12094 | 0.035556 | 0.0049176 | -17.3698 | -200.5584 | ok
65562 | Amazon Bakersfield 1 Solar Project | TRUE | 2.5-4.5h | BL | 1.6 | 22 | 22 | TRUE | 0.8696 | 0.0022021 | 0.13763 | 0.0049031 | 0.0015778 | 0.0018242 | 0.0033253 | 0.20783 | 0.85863 | 0.79709 | 0.8533 | 0.17462 | 0.015149 | 0.0010705 | -0.23984 | -30.5925 | ok
65568 | Google Moffett Park Solar Project | TRUE | 1.5-2.5h | CS | 0.6 | 36 | 36 | TRUE | 0.89537 | 0.00017763 | 0.029605 | 0.0016073 | 0.0022142 | 0.00040336 | -0.00060686 | -0.10114 | 0.8912 | 0.89218 | 0.89087 | 0.010751 | 0.01433 | 0.00029222 | 3.8783 | 177.5847 | ok
65588 | Antlia | FALSE | 1.5-2.5h | CS | 70 | 5 |  | FALSE | [9 empty] | 0.86297 | [6 empty] | insufficient_history
65589 | Carina | FALSE | 1.5-2.5h | CS | 150 | 4 |  | FALSE | [9 empty] | 0.87442 | [6 empty] | insufficient_history
65591 | AVEP BESS | FALSE | 2.5-4.5h | CS | 126 | 9 |  | FALSE | [9 empty] | 0.82952 | [6 empty] | insufficient_history
65614 | Orange Coast College PH2 Solar Project | TRUE | 1.5-2.5h | CS | 2.1 | 36 | 36 | TRUE | 0.51731 | -0.082572 | -3.932 | -0.080699 | -0.086144 | -0.090021 | 0.0054448 | 0.25927 | 1.149 | 0.85881 | 0.8643 | 0.40805 | 0.24764 | 0.017056 | 13.1996 | 205.7822 | ok
65633 | Boaz Microgrid Battery | FALSE | <1.5h | CS | 3.6 | 8 |  | FALSE | [9 empty] | 0.34706 | [6 empty] | insufficient_history
65635 | Hecate Energy Desert Storage 1 LLC | FALSE | 1.5-2.5h | CS | 10 | 7 |  | FALSE | [9 empty] | 0.78637 | [6 empty] | insufficient_history
65644 | Lumina II Solar Project | TRUE | 1.5-2.5h | CS | 160 | 3 |  | FALSE | [9 empty] | 0.84179 | [6 empty] | insufficient_history
65645 | Lumina Solar Project | TRUE | 1.5-2.5h | CS | 160 | 4 |  | FALSE | [9 empty] | 0.83476 | [6 empty] | insufficient_history
65650 | Brockelman Road Solar 2 | TRUE | <1.5h | CT | 2 | 24 | 24 | TRUE | 0.92922 | 0.0010771 | 0.053857 | 0.00057544 | 0.00059969 | 0.00096611 | -2.4252e-05 | -0.0012126 | 0.90676 | 0.90533 | 0.90803 | 0.13025 | 0.019071 | 0.00059342 | 8.7138 | 124.8994 | ok
65656 | Ortega Grid, LLC | FALSE | 1.5-2.5h | CS | 20 | 6 |  | FALSE | [9 empty] | 0.7988 | [6 empty] | insufficient_history
65657 | San Jacinto Grid, LLC | FALSE | <1.5h | CS | 65 | 3 |  | FALSE | [9 empty] | 0.79631 | [6 empty] | insufficient_history
65669 | Faunce Corner Community Solar | TRUE | 2.5-4.5h | CS | 1 | 29 | 29 | TRUE | 0.76918 | 0.0029527 | 0.29527 | 0.0018349 | 0.0035223 | 0.0038842 | -0.0016874 | -0.16874 | 0.75018 | 0.61269 | 0.71429 | 0.71403 | 0.046693 | 0.00035961 | 12.0474 | 67.9477 | ok
65670 | Ventura | TRUE | >4.5h | CS | 1 | 30 | 30 | TRUE | 0.77168 | 0.00051479 | 0.051479 | -0.00036521 | 0.00094273 | 0.00090825 | -0.0013079 | -0.13079 | 0.7791 | 0.77371 | 0.74006 | 0.15821 | 0.052449 | 0.0002244 | -7.9832 | -1.5545 | ok
65672 | Sanborn BESS 3 | FALSE | 2.5-4.5h | CS | 169 | 26 | 26 | TRUE | 0.87625 | 0.16185 | 0.095771 | 0.29608 | 0.11952 | 0.64051 | 0.17656 | 0.10448 | 0.87217 | 0.87156 | 0.86832 | 0.0077954 | 0.016593 | 0.37273 | 5.3859 | 81.795 | ok
65673 | Sanborn BESS 4 | FALSE | 2.5-4.5h | CS | 47 | 26 | 26 | TRUE | 0.95292 | 0.6339 | 1.3487 | 0.63724 | 0.45719 | 0.96998 | 0.18005 | 0.38308 | 0.87258 | 0.87047 | 0.87474 | 0.14481 | 0.052909 | 0.31445 |  |  | ok
65674 | Edwards Sanborn E1B | TRUE | <1.5h | CS | 136 | 26 | 26 | TRUE | 0.94939 | 1.3348 | 0.98147 | 1.9805 | 1.538 | 1.7202 | 0.44256 | 0.32541 | 0.85548 | 0.85349 | 0.8525 | 0.42981 | 0.028677 | 0.31382 | 1.9858 | 9.2546 | ok
65675 | Edwards Sanborn E4 | TRUE | <1.5h | CS | 100 | 26 | 26 | FALSE | 1.0514 | 0.85621 | 0.85621 | 1.4174 | 1.3024 | 1.0708 | 0.11503 | 0.11503 | 0.82621 | 0.83358 | 0.82378 | 0.097362 | 0.16621 | 0.53215 | 11.7913 | 148.229 | ok
65677 | Edwards Sanborn S4 | TRUE | <1.5h | CS | 18.8 | 30 | 30 | TRUE | 0.92792 | 0.014421 | 0.076706 | 0.0079728 | 0.0031497 | 0.011958 | 0.0048232 | 0.025655 | 0.90967 | 0.90896 | 0.90393 | 0.036061 | 0.023478 | 0.01409 | 1.0708 | -2.7472 | ok
65692 | NY6 Battery | FALSE | 1.5-2.5h | CS | 20 | 24 | 24 | TRUE | 0.90135 | 0.16228 | 0.81142 | 0.15964 | 0.15393 | 0.14376 | 0.0057087 | 0.028543 | 0.86303 | 0.86174 | 0.86226 | 0.66094 | 0.0079677 | 0.024781 | 0.083518 | 18.583 | ok
65693 | TX10 Hummingbird Storage | TRUE | 1.5-2.5h | CS | 100 | 15 | 15 | TRUE | 0.87929 | 0.53806 | 0.53806 | 0.65755 | 0.53712 | 0.46987 | 0.12043 | 0.12043 | 0.82997 | 0.81243 | 0.83015 | 0.94515 | 0.0099433 | 0.035951 |  |  | insufficient_history
65694 | TX11 Republic Road Storage | FALSE | <1.5h | CS | 50 | 31 | 31 | TRUE | 0.88423 | 0.37064 | 0.74128 | 0.40167 | 0.36024 | 0.36355 | 0.041425 | 0.082851 | 0.63017 | 0.51616 | 0.58595 | 0.95796 | 0.028697 | 0.014418 | 4.0929 | 11.1248 | ok
65695 | TX12 Silicon Hill Storage | TRUE | <1.5h | CS | 100 | 34 | 34 | TRUE | 0.58996 | 0.075363 | 0.075363 | 0.54637 | 0.081027 | 0.091175 | 0.46534 | 0.46534 | 0.62542 | 0.53913 | 0.61642 | 0.10114 | 0.098037 | 0.039716 | 12.1497 | 37.8778 | ok
65696 | TX13 Endurance Park Storage | FALSE | <1.5h | CS | 50 | 30 | 30 | TRUE | 0.89675 | 0.30023 | 0.60047 | 0.29639 | 0.17199 | 0.20785 | 0.1244 | 0.2488 | 0.80715 | 0.77802 | 0.80778 | 0.9674 | 0.012617 | 0.010415 | -1.0733 | 0.19078 | ok
65698 | TX15 Limousin Oak Storage | TRUE | 1.5-2.5h | CS | 100 | 15 | 15 | TRUE | 0.90276 | 0.75482 | 0.75482 | 0.79192 | 0.64897 | 0.65834 | 0.14296 | 0.14296 | 0.82944 | 0.81985 | 0.83379 | 0.73174 | 0.020988 | 0.12676 |  |  | insufficient_history
65699 | TX19 River Valley Storage 1 | FALSE | 1.5-2.5h | CS | 50 | 30 | 30 | TRUE | 0.82307 | 0.20379 | 0.40757 | 0.1034 | 0.27529 | 0.29499 | -0.17189 | -0.34378 | 0.79485 | 0.71118 | 0.75871 | 0.69596 | 0.057136 | 0.025455 | 7.9602 | 52.4238 | ok
65700 | TX21 River Valley Storage 2 | FALSE | 1.5-2.5h | CS | 50 | 29 | 29 | TRUE | 0.83567 | 0.18845 | 0.3769 | 0.07691 | 0.22351 | 0.27249 | -0.1466 | -0.29319 | 0.80294 | 0.72038 | 0.78071 | 0.66065 | 0.054216 | 0.025993 | 11.3861 | 74.3987 | ok
65701 | TX23 Roughneck Storage | FALSE | <1.5h | CS | 50 | 27 | 27 | TRUE | 0.87222 | 0.31299 | 0.62599 | 0.32163 | 0.30137 | 0.32121 | 0.020267 | 0.040534 | 0.65027 | 0.56578 | 0.63084 | 0.9566 | 0.029218 | 0.013333 | -1.3946 | 5.2597 | ok
65711 | Vikings Energy Farm | TRUE | 2.5-4.5h | CS | 150 | 17 | 17 | TRUE | 0.89164 | 0.066252 | 0.044168 | 0.063561 | 0.1527 | -0.028607 | -0.089139 | -0.059426 | 0.88848 | 0.88766 | 0.88633 | 0.050887 | 0.0075518 | 0.073877 |  |  | insufficient_history
65733 | Carris Storage I | FALSE | 1.5-2.5h | CS | 10 | 7 |  | FALSE | [9 empty] | 0.79029 | [6 empty] | insufficient_history
65734 | Oberon Solar Project | TRUE | 2.5-4.5h | CS | 125 | 28 | 28 | TRUE | 0.93729 | 0.7898 | 0.63184 | 0.91874 | 0.76804 | 0.60039 | 0.1507 | 0.12056 | 0.89895 | 0.89182 | 0.89729 | 0.79058 | 0.0074659 | 0.07972 | 4.7709 | 114.4222 | ok
65735 | Oberon II Solar Project | TRUE | 2.5-4.5h | CS | 125 | 28 | 28 | TRUE | 0.93835 | 0.81362 | 0.6509 | 0.92117 | 0.79515 | 0.61332 | 0.12602 | 0.10082 | 0.89716 | 0.88999 | 0.89266 | 0.74805 | 0.0089157 | 0.092603 | -1.5296 | -149.0146 | ok
65743 | Victory Pass | TRUE | 2.5-4.5h | CT | 50 | 22 | 22 | TRUE | 0.85045 | -0.24713 | -0.49425 | -0.58073 | -0.29316 | 0.61754 | -0.28757 | -0.57515 | 0.88312 | 0.89551 | 0.86295 | 0.029719 | 0.065411 | 0.31574 |  |  | insufficient_history
65744 | Arica Solar | TRUE | 2.5-4.5h | CT | 136 | 22 | 22 | TRUE | 0.82595 | -0.3466 | -0.25485 | -3.0108 | -0.59012 | 4.3066 | -2.4207 | -1.7799 | 0.85104 | 0.86919 | 0.91818 | 0.011408 | 0.072332 | 0.72146 |  |  | insufficient_history
65809 | Caterina | FALSE | <1.5h | CS | 9.9 | 36 | 36 | TRUE | 0.93041 | 0.021586 | 0.21804 | 0.021518 | 0.022556 | 0.023084 | -0.0010377 | -0.010482 | 0.85265 | 0.84911 | 0.84539 | 0.45547 | 0.020113 | 0.0040479 | -4.8961 | -41.7998 | ok
65810 | Cedarville (TX) | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.9257 | 0.020865 | 0.21076 | 0.0207 | 0.020288 | 0.019373 | 0.00041128 | 0.0041543 | 0.85074 | 0.84579 | 0.85746 | 0.85749 | 0.0095752 | 0.0018135 | -11.9661 | -255.3337 | ok
65811 | Coyote Springs (TX) | FALSE | <1.5h | CS | 9.9 | 24 | 24 | FALSE | 1.0193 | 0.040541 | 0.40951 | 0.040191 | 0.038356 | 0.03868 | 0.0018343 | 0.018528 | 0.85746 | 0.84961 | 0.88067 | 0.9056 | 0.014423 | 0.0027907 | -12.5926 | -285.7033 | ok
65812 | Farmersville (TX) | FALSE | <1.5h | CS | 9.9 | 21 | 21 | TRUE | 0.95493 | 0.024923 | 0.25175 | 0.024409 | 0.024864 | 0.020594 | -0.00045463 | -0.0045922 | 0.82233 | 0.80652 | 0.84146 | 0.9347 | 0.013782 | 0.0015113 |  |  | insufficient_history
65813 | Faulkner | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.92551 | 0.016628 | 0.16796 | 0.016499 | 0.017164 | 0.014114 | -0.00066438 | -0.0067109 | 0.86204 | 0.85588 | 0.86795 | 0.88328 | 0.0076808 | 0.0012887 | -6.1697 | -167.1057 | ok
65814 | Gomez | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.93615 | 0.02365 | 0.23889 | 0.023335 | 0.023872 | 0.020666 | -0.00053705 | -0.0054247 | 0.84654 | 0.8397 | 0.85914 | 0.88708 | 0.010167 | 0.001799 | -5.4337 | -73.9608 | ok
65829 | Holcomb (TX) | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.94324 | 0.028957 | 0.2925 | 0.029426 | 0.028643 | 0.028506 | 0.0007824 | 0.007903 | 0.82144 | 0.81292 | 0.83617 | 0.87057 | 0.014931 | 0.0023804 | -5.1909 | -46.3082 | ok
65830 | Junction (TX) | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.94883 | 0.02142 | 0.21636 | 0.021347 | 0.021471 | 0.021633 | -0.00012424 | -0.001255 | 0.85539 | 0.85162 | 0.86417 | 0.63973 | 0.020167 | 0.0034271 | -18.2485 | -277.4608 | ok
65831 | Lonestar | FALSE | <1.5h | CS | 9.9 | 36 | 36 | TRUE | 0.93843 | 0.017327 | 0.17502 | 0.016724 | 0.015501 | 0.019343 | 0.0012238 | 0.012361 | 0.8735 | 0.86837 | 0.87696 | 0.67321 | 0.011034 | 0.0020704 | -4.0012 | -82.5727 | ok
65832 | Olney | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.92372 | 0.022908 | 0.23139 | 0.023762 | 0.020935 | 0.023196 | 0.0028272 | 0.028558 | 0.80331 | 0.7934 | 0.81271 | 0.87677 | 0.015439 | 0.0018311 | -5.2081 | -72.1088 | ok
65833 | Rattlesnake (TX) | FALSE | <1.5h | CS | 9.9 | 24 | 24 | FALSE | 1.005 | 0.038743 | 0.39134 | 0.037209 | 0.024542 | 0.019685 | 0.012667 | 0.12795 | 0.84875 | 0.84306 | 0.87534 | 0.52667 | 0.041932 | 0.0078306 | -9.4883 | -159.8658 | ok
65834 | Saddleback BESS2 | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.93469 | 0.031411 | 0.31729 | 0.031028 | 0.028708 | 0.028225 | 0.0023196 | 0.023431 | 0.82336 | 0.81658 | 0.83243 | 0.94162 | 0.0088617 | 0.0016675 | -11.3146 | -153.0926 | ok
65835 | Screwbean | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.91427 | 0.010366 | 0.1047 | 0.01049 | 0.012811 | 0.010749 | -0.0023208 | -0.023442 | 0.87583 | 0.87346 | 0.87941 | 0.60855 | 0.0093247 | 0.0017725 | -6.5913 | -224.6717 | ok
65836 | Toyah Power Station | FALSE | <1.5h | CS | 10.4 | 24 | 24 | TRUE | 0.99762 | 0.008979 | 0.086336 | 0.0088144 | 0.014471 | 0.011165 | -0.0056564 | -0.054389 | 0.95886 | 0.95644 | 0.96395 | 0.24444 | 0.017383 | 0.0033656 |  |  | ok
65837 | Val Verde | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.92187 | 0.011494 | 0.1161 | 0.011405 | 0.0093232 | 0.010352 | 0.002082 | 0.02103 | 0.85146 | 0.84573 | 0.86019 | 0.84414 | 0.0097169 | 0.001053 | -1.7712 | -49.2525 | ok
65857 | Sunlight Storage | FALSE | 2.5-4.5h | CS | 230 | 30 | 30 | TRUE | 0.93992 | 3.3807 | 1.4699 | 4.5361 | 3.0669 | 3.3991 | 1.4692 | 0.63878 | 0.83251 | 0.82755 | 0.83929 | 0.41515 | 0.03589 | 0.75831 | -4.8496 | -49.3562 | ok
65860 | Avila | FALSE | 1.5-2.5h | CS | 160 | 4 |  | FALSE | [9 empty] | 0.87659 | [6 empty] | insufficient_history
65861 | Cachi | FALSE | 1.5-2.5h | CS | 200 | 4 |  | FALSE | [9 empty] | 0.86563 | [6 empty] | insufficient_history
65866 | Canoe | TRUE | 2.5-4.5h | CS | 74.5 | 1 |  | FALSE | [9 empty] | 0.77822 | [6 empty] | insufficient_history
65888 | Kayak | TRUE | 2.5-4.5h | CS | 74.5 | 1 |  | FALSE | [9 empty] | 0.75179 | [6 empty] | insufficient_history
65927 | Fourmile Creek | TRUE | 2.5-4.5h | CS | 74.5 | 1 |  | FALSE | [9 empty] | 0.76397 | [6 empty] | insufficient_history
65933 | Sagebrush ESS | FALSE | 2.5-4.5h | CS | 80 | 32 | 32 | TRUE | 0.8332 | 0.37173 | 0.46467 | 0.84154 | 0.37408 | 0.59895 | 0.46747 | 0.58433 | 0.80338 | 0.80079 | 0.78465 | 0.084293 | 0.042225 | 0.2237 | 6.5875 | -45.0531 | ok
65945 | Brookville Smart Bus Depot Microgrid | TRUE | 2.5-4.5h | CS | 1.5 | 32 | 32 | TRUE | 0.92614 | 0.00083745 | 0.05583 | 6.9043e-05 | -0.0011942 | 0.00054314 | 0.0012633 | 0.084217 | 0.91556 | 0.90988 | 0.91078 | 0.096521 | 0.014995 | 0.00046779 | -1.9391 | -44.0217 | ok
65950 | Kearsarge 100 Sohier Rd | TRUE | 2.5-4.5h | CS | 1.8 | 30 | 30 | TRUE | 0.94223 | 0.0087754 | 0.48752 | 0.0088594 | 0.0075471 | 0.0166 | 0.0013123 | 0.072907 | 0.88505 | 0.84405 | 0.89452 | 0.73948 | 0.020167 | 0.00098434 | -0.065887 | -55.5202 | ok
65951 | Bowling Green Energy Storage Project | FALSE | <1.5h | CS | 12 | 24 | 24 | TRUE | 0.90494 | -0.012802 | -0.10668 | 0.012817 | -0.0046825 | -0.0048701 | 0.017499 | 0.14583 | 0.9088 | 0.90889 | 0.90883 | 0.039137 | 0.0051635 | 0.013524 | -3.1009 | -83.6818 | ok
65952 | Andover Energy Storage Project | FALSE | <1.5h | CS | 20 | 24 | 24 | TRUE | 0.89744 | -0.010783 | -0.053916 | 0.035998 | 0.0086761 | -0.00091552 | 0.027322 | 0.13661 | 0.89946 | 0.89959 | 0.89966 | 0.032857 | 0.0032005 | 0.012473 | 1.0565 | 83.1862 | ok
65953 | Howell Energy Storage Project | FALSE | <1.5h | CS | 7 | 24 | 24 | TRUE | 0.89693 | -0.0030635 | -0.043764 | -0.0078379 | -0.0090429 | 0.0016649 | 0.001205 | 0.017215 | 0.8985 | 0.89879 | 0.90081 | 0.00083694 | 0.015519 | 0.022567 | 3.1448 | 197.751 | ok
65956 | Storey Solar and Storage | TRUE | 2.5-4.5h | CS | 88 | 26 | 26 | TRUE | 0.84183 | -0.24472 | -0.27809 | -0.10241 | -0.43522 | -0.20021 | 0.33282 | 0.3782 | 0.86277 | 0.86373 | 0.85905 | 0.057509 | 0.024945 | 0.20223 | -2.075 | -11.3173 | ok
65962 | Mesquite Solar 4, LLC | TRUE | >4.5h | CS | 10 | 18 | 18 | TRUE | 0.9267 | 0.034555 | 0.34555 | 0.13728 | 0.046044 | 0.032307 | 0.09124 | 0.9124 | 0.86128 | 0.64453 | 0.86105 | 0.7153 | 0.073947 | 0.00545 |  |  | ok
65963 | Mesquite Solar 5, LLC | TRUE | 2.5-4.5h | CS | 60 | 30 | 30 | TRUE | 0.88294 | -0.095722 | -0.15954 | -0.085373 | 0.033908 | 0.080779 | -0.11928 | -0.1988 | 0.89337 | 0.89366 | 0.88892 | 0.089457 | 0.0094782 | 0.057713 | 9.2523 | 124.3598 | ok
65980 | CED West Side Canal Battery Storage | FALSE | 2.5-4.5h | CS | 131 | 31 | 31 | TRUE | 0.84016 | 0.60833 | 0.46437 | 0.58359 | -0.30109 | -0.25994 | 0.88469 | 0.67533 | 0.8147 | 0.80035 | 0.81981 | 0.90014 | 0.011137 | 0.037626 | -2.9449 | -128.3266 | ok
65987 | Desert Peak Energy Storage I | TRUE | 2.5-4.5h | CS | 325 | 30 | 30 | TRUE | 0.87936 | 0.0032255 | 0.00099246 | -0.047272 | -0.0469 | 0.10683 | -0.00037113 | -0.00011419 | 0.87593 | 0.88329 | 0.87619 | 0.00069757 | 0.017738 | 0.023071 | 1.9223 | 193.9445 | ok
65988 | Desert Peak Energy Storage II | TRUE | 2.5-4.5h | CS | 75 | 30 | 30 | TRUE | 0.87529 | -0.018617 | -0.024823 | -0.047235 | -0.070211 | 0.026742 | 0.022976 | 0.030635 | 0.87621 | 0.88018 | 0.87598 | 0.019063 | 0.010002 | 0.025238 | 1.3871 | 190.0377 | ok
66006 | House Mountain | FALSE | 1.5-2.5h | CS | 73.2 | 23 | 23 | TRUE | 0.79801 | -0.64542 | -0.88172 | -0.71116 | -0.88406 | -0.92004 | 0.1729 | 0.2362 | 0.90355 | 0.90931 | 0.91568 | 0.12034 | 0.089594 | 0.38078 |  |  | insufficient_history
66007 | Flower Valley II | FALSE | 1.5-2.5h | CS | 101 | 36 | 36 | TRUE | 0.90959 | 0.4307 | 0.42644 | 0.57305 | 0.43367 | 0.40741 | 0.13939 | 0.13801 | 0.85294 | 0.84987 | 0.8557 | 0.41372 | 0.016943 | 0.08793 | -0.19288 | 12.2522 | ok
66008 | Swoose II | FALSE | 1.5-2.5h | CS | 101 | 36 | 36 | TRUE | 0.9039 | 0.41214 | 0.40806 | 0.2988 | 0.17678 | 0.090683 | 0.12202 | 0.12081 | 0.85231 | 0.85199 | 0.85508 | 0.080112 | 0.040274 | 0.23951 | -1.8256 | -1.0738 | ok
66009 | Crossett Power Management LLC | FALSE | 1.5-2.5h | CS | 203 | 36 | 36 | TRUE | 0.87845 | 0.015587 | 0.0076782 | 0.0057049 | -0.030556 | -0.093142 | 0.036261 | 0.017863 | 0.87705 | 0.87691 | 0.88325 | 0.0015343 | 0.011357 | 0.068191 | -5.7583 | -210.8828 | ok
66050 | Lancaster Area Battery | FALSE | 2.5-4.5h | CT | 127 | 40 | 40 | TRUE | 0.91274 | 0.85584 | 0.67389 | 1.5163 | 1.3604 | 1.117 | 0.15591 | 0.12276 | 0.87191 | 0.87176 | 0.8735 | 0.1312 | 0.022135 | 0.35726 | 0.84046 | 19.6776 | ok
66067 | Kapolei Energy Storage | FALSE | 2.5-4.5h | CS | 185 | 24 | 24 | TRUE | 0.93927 | 0.84404 | 0.45624 | 0.51359 | 0.568 | 0.62859 | -0.054413 | -0.029413 | 0.90444 | 0.90432 | 0.90275 | 0.095168 | 0.027205 | 0.55487 | 0.19039 | 7.1219 | ok
66075 | Blacksmith Road Solar 1 | TRUE | 1.5-2.5h | CT | 2 | 36 | 36 | TRUE | 0.91492 | 0.0010539 | 0.052694 | 0.00060787 | 0.00078661 | 0.0013659 | -0.00017873 | -0.0089366 | 0.90844 | 0.90753 | 0.90294 | 0.054631 | 0.0071922 | 0.00075185 | 3.7115 | 196.419 | ok
66076 | Electric Avenue Lunenburg Solar 1 | TRUE | <1.5h | CT | 1 | 24 | 24 | TRUE | 0.9461 | 0.0016839 | 0.16839 | 0.0092711 | 0.0085552 | 0.0050596 | 0.00071599 | 0.071599 | 0.92995 | 0.92905 | 0.91507 | 0.029032 | 0.026348 | 0.0020762 | 13.1457 | 234.2955 | ok
66128 | Lake Mabel Solar and Battery Storage | TRUE | 2.5-4.5h | CS | 40 | 9 |  | FALSE | [9 empty] | 0.76409 | [6 empty] | insufficient_history
66129 | Dover Solar and Battery Storage | TRUE | 1.5-2.5h | CS | 15 | 10 | 10 | TRUE | 0.88093 | 0.063311 | 0.42208 | 0.092254 | 0.20895 |  | -0.11669 | -0.77795 | 0.78288 | 0.77742 | 0.80176 | 0.071979 | 0.25883 | 0.080373 |  |  | insufficient_history
66137 | Zier Solar | TRUE | 1.5-2.5h | CS | 40.4 | 21 | 21 | TRUE | 0.87698 | 0.25348 | 0.62743 | 0.2509 | 0.27176 | 0.27944 | -0.020861 | -0.051636 | 0.81156 | 0.80575 | 0.80598 | 0.56685 | 0.021457 | 0.050834 |  |  | insufficient_history
66163 | Jicarilla Solar 1 LLC | TRUE | 2.5-4.5h | CS | 20 | 30 | 30 | TRUE | 0.84002 | -0.040051 | -0.20026 | -0.078091 | -0.058541 | -0.22014 | -0.01955 | -0.097748 | 0.85498 | 0.85841 | 0.86261 | 0.019217 | 0.030914 | 0.054073 | -1.8832 | 38.1259 | ok
66170 | Revolution | FALSE | 1.5-2.5h | CS | 150 | 24 | 24 | TRUE | 0.86359 | 0.13356 | 0.089038 | 0.066597 | 0.11867 | 0.12679 | -0.052075 | -0.034717 | 0.85375 | 0.85128 | 0.84837 | 0.28237 | 0.0070886 | 0.045394 | -3.6788 | -72.1175 | ok
66180 | Huxley Solar | TRUE | <1.5h | CS | 5 | 15 | 15 | TRUE | 0.78454 | 0.00050802 | 0.01016 | 0.00057786 | 0.014358 | 0.00092254 | -0.01378 | -0.2756 | 0.80013 | 0.79581 | 0.81068 | 0.0030689 | 0.077651 | 0.0025395 |  |  | insufficient_history
66181 | Beacon Solar, LLC | TRUE | 1.5-2.5h | CS | 5 | 16 | 16 | TRUE | 0.94614 | 0.0035222 | 0.070443 | 0.0088636 | 0.0044698 | 0.0048146 | 0.0043938 | 0.087877 | 0.92037 | 0.92097 | 0.93249 | 0.019257 | 0.063756 | 0.0067179 |  |  | insufficient_history
66182 | Town of Amherst Solar | TRUE | <1.5h | CS | 2.5 | 20 | 20 | TRUE | 0.69192 | -0.00098809 | -0.039523 | -0.0018042 | -0.0012716 | -0.00039104 | -0.00053253 | -0.021301 | 0.72133 | 0.72898 | 0.73661 | 0.059548 | 0.094217 | 0.00092553 |  |  | insufficient_history
66208 | North Central Valley | FALSE | 2.5-4.5h | CS | 132 | 28 | 28 | TRUE | 0.89239 | 0.23848 | 0.18067 | 0.47852 | 0.14151 | 0.31365 | 0.33701 | 0.25531 | 0.88408 | 0.88326 | 0.88682 | 0.010875 | 0.025347 | 0.44604 | -1.9931 | -125.6156 | ok
66218 | Dubois Solar (Hybrid) | TRUE | 1.5-2.5h | CS | 2 | 15 | 15 | TRUE | 0.99165 | 0.0044273 | 0.22136 | 0.0042833 | 0.0041941 |  | 8.9173e-05 | 0.0044586 | 0.93633 | 0.92618 | 0.93478 | 0.38437 | 0.032374 | 0.001554 |  |  | ok
66222 | Landau II Solar (Hybrid) | TRUE | 1.5-2.5h | CS | 4 | 16 | 16 | TRUE | 0.85568 | -0.0010354 | -0.025886 | 0.0039341 | 0.0027563 | -0.0011782 | 0.0011779 | 0.029446 | 0.92426 | 0.87992 | 0.91723 | 0.11359 | 0.05682 | 0.00077306 |  |  | ok
66228 | Salt Point Solar (Hybrid) | TRUE | <1.5h | CS | 2 | 20 | 20 | TRUE | 0.93738 | 0.0011547 | 0.057736 | 0.00011389 | 0.0012039 | 0.0018148 | -0.00109 | -0.054498 | 0.92722 | 0.90946 | 0.92893 | 0.43947 | 0.027298 | 0.00030738 |  |  | ok
66232 | Svenski Solar (Hybrid) | TRUE | 1.5-2.5h | CS | 2 | 11 | 11 | TRUE | 0.91985 | 0.00053422 | 0.026711 | 0.00052599 | 0.0015145 |  | -0.00098853 | -0.049427 | 0.9382 | 0.90822 | 0.94495 | 0.072691 | 0.04765 | 0.00063602 |  |  | ok
66263 | Eleven Mile Solar Center | TRUE | 2.5-4.5h | CS | 300 | 19 | 19 | TRUE | 0.92159 | 0.96564 | 0.32188 | 0.94042 | 0.77621 | 0.71168 | 0.16421 | 0.054735 | 0.90322 | 0.90196 | 0.90385 | 0.85305 | 0.0025965 | 0.097204 |  |  | insufficient_history
66265 | Paradise Energy Storage | FALSE | <1.5h | CS | 10 | 22 | 22 | TRUE | 0.91835 | 0.088346 | 0.88346 | 0.17177 | 0.081997 | 0.090438 | 0.089774 | 0.89774 | 0.85528 | 0.84672 | 0.86281 | 0.29624 | 0.040077 | 0.030448 |  |  | insufficient_history
66266 | Clairemont Energy Storage | FALSE | <1.5h | CS | 10 | 22 | 22 | TRUE | 0.90596 | 0.065575 | 0.65575 | 0.06512 | 0.069135 | 0.057183 | -0.0040154 | -0.040154 | 0.84461 | 0.84075 | 0.85163 | 0.4625 | 0.021967 | 0.015807 |  |  | insufficient_history
66270 | Proxima | TRUE | 2.5-4.5h | CS | 162 | 18 | 18 | TRUE | 0.92791 | 1.5729 | 0.97091 | 1.0017 | 1.2754 | 1.6892 | -0.27375 | -0.16898 | 0.85577 | 0.85074 | 0.8706 | 0.19567 | 0.055009 | 0.79723 |  |  | insufficient_history
66278 | Elliott Energy Storage | FALSE | <1.5h | CS | 10 | 21 | 21 | TRUE | 0.89311 | 0.056775 | 0.56775 | 0.14147 | 0.053532 | 0.076523 | 0.087935 | 0.87935 | 0.85262 | 0.84783 | 0.86294 | 0.083139 | 0.053154 | 0.043255 |  |  | insufficient_history
66279 | Boulevard Energy Storage | FALSE | <1.5h | CS | 10 | 19 | 19 | TRUE | 0.93662 | 0.088994 | 0.88994 | 0.10566 | 0.064931 | 0.046578 | 0.040728 | 0.40728 | 0.85117 | 0.82637 | 0.84838 | 0.78817 | 0.028579 | 0.01119 |  |  | insufficient_history
66280 | Pala Gomez Creek BESS | FALSE | <1.5h | CS | 10 | 21 | 21 | TRUE | 0.88255 | 0.020733 | 0.20733 | 0.028651 | 0.0075891 | 0.033549 | 0.021062 | 0.21062 | 0.87328 | 0.87291 | 0.87836 | 0.043806 | 0.016783 | 0.022223 |  |  | insufficient_history
66281 | Melrose BESS | FALSE | <1.5h | CS | 20 | 22 | 22 | TRUE | 0.88188 | 0.11503 | 0.57515 | 0.11504 | 0.095775 | 0.07375 | 0.019269 | 0.096345 | 0.81925 | 0.81454 | 0.81907 | 0.42279 | 0.026121 | 0.030054 |  |  | insufficient_history
66285 | Condor Energy Storage LLC | FALSE | 2.5-4.5h | CS | 200 | 18 | 18 | TRUE | 0.97814 | 2.7563 | 1.3781 | 2.7828 | 2.8276 | 2.6613 | -0.044816 | -0.022408 | 0.89138 | 0.88913 | 0.89926 | 0.49526 | 0.026535 | 0.69563 |  |  | insufficient_history
66286 | Peregrine Energy Storage LLC | FALSE | 1.5-2.5h | CS | 200 | 7 |  | FALSE | [9 empty] | 0.87277 | [6 empty] | insufficient_history
66325 | Hemmingway BESS | FALSE | 2.5-4.5h | CS | 116 | 10 | 10 | TRUE | 0.95398 | 0.53138 | 0.45809 | 1.5575 | 0.93286 |  | 0.62469 | 0.53853 | 0.87806 | 0.85958 | 0.87711 | 0.54057 | 0.052901 | 0.1732 |  |  | insufficient_history
66326 | Black Mesa BESS | FALSE | 2.5-4.5h | CS | 40 | 10 | 10 | TRUE | 0.91966 | 0.058119 | 0.1453 | -0.21191 | -0.15633 |  | -0.055582 | -0.13895 | 0.90799 | 0.90588 | 0.9091 | 0.37429 | 0.0095442 | 0.026568 |  |  | insufficient_history
66327 | Elmore BESS | FALSE | 2.5-4.5h | CS | 4 | 11 | 11 | TRUE | 0.90519 | 0.0012134 | 0.030336 | 0.0057323 | 0.001683 | 0.0020783 | 0.0040493 | 0.10123 | 0.90499 | 0.90331 | 0.90928 | 0.0052707 | 0.022333 | 0.0055566 |  |  | insufficient_history
66328 | Filer BESS | FALSE | 1.5-2.5h | CS | 2 | 10 | 10 | TRUE | 0.90353 | 0.0014833 | 0.074166 | -0.0014573 | -0.027241 | -0.01533 | 0.025784 | 1.2892 | 0.9023 | 0.89765 | 0.90858 | 0.020022 | 0.03487 | 0.003669 |  |  | insufficient_history
66329 | Melba BESS | FALSE | 2.5-4.5h | CS | 2 | 5 |  | FALSE | [9 empty] | 0.90792 | [6 empty] | insufficient_history
66330 | Weiser BESS | FALSE | 2.5-4.5h | CS | 3 | 10 | 10 | TRUE | 0.89154 | -0.0091887 | -0.30629 | 0.0018375 | -0.0046757 | -0.0075639 | 0.0065132 | 0.21711 | 0.91419 | 0.91658 | 0.91944 | 0.16644 | 0.02586 | 0.0072701 |  |  | insufficient_history
66333 | Superstition Energy Storage | FALSE | 2.5-4.5h | CS | 90 | 18 | 18 | TRUE | 0.94841 | 1.0705 | 1.1895 | 1.0835 | 0.97212 | 0.91099 | 0.11142 | 0.1238 | 0.87861 | 0.87463 | 0.88486 | 0.84106 | 0.01041 | 0.11634 |  |  | insufficient_history
66334 | Sierra Estrella Energy Storage | FALSE | 2.5-4.5h | CS | 250 | 20 | 20 | TRUE | 0.88331 | -0.39757 | -0.15903 | 0.36651 | -0.35877 | -0.51958 | 0.72527 | 0.29011 | 0.8918 | 0.89401 | 0.89321 | 0.5622 | 0.0040663 | 0.082695 |  |  | insufficient_history
66336 | St. Gall Energy Storage I | FALSE | 1.5-2.5h | CS | 102.6 | 22 | 22 | TRUE | 0.9049 | 0.40386 | 0.39363 | 0.42143 | 0.42897 | 0.54859 | -0.0075361 | -0.0073452 | 0.86063 | 0.85787 | 0.85195 | 0.32185 | 0.021641 | 0.13109 |  |  | insufficient_history
66337 | Tidwell Prairie Storage 1 | FALSE | 1.5-2.5h | CS | 200 | 3 |  | FALSE | [9 empty] | 0.83765 | [6 empty] | insufficient_history
66338 | Callisto I Energy Center | FALSE | <1.5h | CS | 223.4 | 17 | 17 | TRUE | 0.84971 | -0.11922 | -0.053365 | -0.14108 | -0.13293 | -0.5989 | -0.0081497 | -0.003648 | 0.85676 | 0.85797 | 0.85919 | 0.053874 | 0.013143 | 0.129 |  |  | insufficient_history
66357 | Yellow Pine Solar | TRUE | 2.5-4.5h | CS | 65 | 30 | 30 | TRUE | 0.85444 | -0.20447 | -0.31458 | -0.089752 | -0.18158 | -0.093344 | 0.091832 | 0.14128 | 0.87092 | 0.87179 | 0.87301 | 0.07787 | 0.015345 | 0.13298 | 0.58251 | 51.05 | ok
66394 | Goleta Energy Storage, LLC | FALSE | 2.5-4.5h | CS | 60 | 23 | 23 | TRUE | 0.92039 | 0.39124 | 0.65207 | 0.39765 | 0.37714 | 0.4557 | 0.020509 | 0.034182 | 0.86451 | 0.8592 | 0.86847 | 0.7995 | 0.0093132 | 0.042754 |  |  | insufficient_history
66408 | Buena Vista Energy Center | TRUE | 2.5-4.5h | CS | 50 | 31 | 31 | TRUE | 0.89416 | -0.0025049 | -0.0050099 | -0.018664 | -0.24353 | -0.017462 | 0.22486 | 0.44973 | 0.88924 | 0.90176 | 0.92324 | 4.1075e-05 | 0.030935 | 0.072578 | 1.6735 | 105.3878 | ok
66420 | Five Wells Solar Center - Hybrid | TRUE | <1.5h | CS | 262.5 | 10 | 10 | TRUE | 0.92487 | 1.1464 | 0.43673 | 0.96042 | 0.88246 |  | 0.077957 | 0.029698 | 0.8501 | 0.84886 | 0.85136 | 0.69559 | 0.022919 | 0.26813 |  |  | insufficient_history
66423 | Stanton Battery Energy Storage | FALSE | 2.5-4.5h | CS | 68.8 | 26 | 26 | TRUE | 0.91993 | 0.27653 | 0.40193 | 0.24832 | 0.227 | 0.23261 | 0.021311 | 0.030975 | 0.89807 | 0.89792 | 0.89673 | 0.10208 | 0.016319 | 0.16741 | 1.7643 | 82.8427 | ok
66461 | Beaumont BESS | FALSE | 2.5-4.5h | CS | 116.6 | 17 | 17 | TRUE | 0.94544 | 1.0173 | 0.87244 | 1.0299 | 1.0605 | 1.0805 | -0.030556 | -0.026206 | 0.88132 | 0.87938 | 0.88339 | 0.50905 | 0.021449 | 0.25795 |  |  | insufficient_history
66462 | Placerita ESS | FALSE | 2.5-4.5h | CS | 88 | 14 | 14 | TRUE | 0.95421 | 0.81611 | 0.92739 | 0.56414 | 1.1187 | 1.2709 | -0.55452 | -0.63014 | 0.88894 | 0.88905 | 0.90481 | 0.14135 | 0.057677 | 0.58066 |  |  | insufficient_history
66488 | Davis Solar | TRUE | 1.5-2.5h | CS | 2 | 13 | 13 | TRUE | 0.9022 | 0.0029007 | 0.14504 | 0.0036845 | 0.0007535 |  | 0.002931 | 0.14655 | 0.87346 | 0.81887 | 0.87719 | 0.74697 | 0.063577 | 0.00050903 |  |  | insufficient_history
66494 | Menifee Power Bank | FALSE | 2.5-4.5h | CS | 680 | 19 | 19 | TRUE | 0.88288 | 1.0812 | 0.159 | 1.0037 | 1.2585 | -0.13799 | -0.25472 | -0.037459 | 0.87366 | 0.87266 | 0.87316 | 0.12073 | 0.0097974 | 0.70769 |  |  | insufficient_history
66499 | Federalsburg Energy Storage 1 LLC | TRUE | 1.5-2.5h | CT | 1.2 | 13 | 13 | TRUE | 0.84362 | 0.00045144 | 0.03762 | -0.00069819 | 0.00022195 | 0.0007449 | -0.00092014 | -0.076678 | 0.82105 | 0.82409 | 0.8 | 0.032293 | 0.19981 | 0.00074512 |  |  | ok
66500 | Valley Center 85 | FALSE | 1.5-2.5h | CS | 85 | 36 | 36 | TRUE | 0.80616 | 0.22091 | 0.2599 | 0.32469 | 0.17308 | 0.35916 | 0.15161 | 0.17837 | 0.78598 | 0.78686 | 0.77813 | 0.023129 | 0.039211 | 0.24622 | 4.5171 | 52.7818 | ok
66502 | Valley Center 54 | FALSE | 2.5-4.5h | CS | 54 | 36 | 36 | TRUE | 0.91079 | 0.71948 | 1.3324 | 0.56796 | 0.72196 | 0.59841 | -0.15399 | -0.28517 | 0.8086 | 0.80261 | 0.80392 | 0.37658 | 0.038248 | 0.15876 | 9.4843 | 35.6125 | ok
66505 | EnerSmart Chula Vista Sub Station | FALSE | 1.5-2.5h | CS | 6 | 13 | 13 | TRUE | 0.81776 | 0.0031409 | 0.052348 | 0.0045023 | 0.004196 | 0.010099 | 0.00030636 | 0.005106 | 0.81116 | 0.82255 | 0.80515 | 0.046246 | 0.023223 | 0.0043007 |  |  | insufficient_history
66533 | BCE Los Alamitos 1 | TRUE | 1.5-2.5h | CS | 10 | 12 | 12 | TRUE | 0.90488 | 0.01688 | 0.1688 | 0.0065918 | 0.0075035 | 0.010374 | -0.0009117 | -0.009117 | 0.88468 | 0.88445 | 0.88521 | 0.35853 | 0.010876 | 0.0071401 |  |  | insufficient_history
66540 | Shamrock Wind | TRUE | <1.5h | CS | 100 | 12 | 12 | TRUE | 0.84821 | -0.20354 | -0.20354 | 0.28257 | -0.070636 | -0.5445 | 0.35321 | 0.35321 | 0.86073 | 0.86178 | 0.85992 | 0.017339 | 0.043485 | 0.48455 |  |  | insufficient_history
66574 | San Juan Solar I | TRUE | >4.5h | CS | 100 | 15 | 15 | TRUE | 0.97164 | 1.7547 | 1.7547 | 2.2782 | 1.0188 | 5.624 | 1.2594 | 1.2594 | 0.86922 | 0.86253 | 0.89096 | 0.16204 | 0.12643 | 1.1067 |  |  | insufficient_history
66575 | Sunlight Storage II | FALSE | 2.5-4.5h | CS | 230 | 21 | 21 | TRUE | 0.99278 | 6.3765 | 2.7724 | 5.5726 | 6.3491 | 8.9563 | -0.77643 | -0.33758 | 0.83573 | 0.83553 | 0.85629 | 0.14421 | 0.11374 | 3.5636 |  |  | insufficient_history
66598 | Baldy Mesa Solar & Storage | TRUE | 2.5-4.5h | CS | 75 | 15 | 15 | TRUE | 0.85963 | -0.27831 | -0.37107 | -0.30587 | -0.21674 | -0.40658 | -0.089125 | -0.11883 | 0.90212 | 0.90964 | 0.92446 | 0.073738 | 0.061678 | 0.27357 |  |  | insufficient_history
66599 | Dark Sky Energy Center | FALSE | <1.5h | CS | 7.3 | 4 |  | FALSE | [9 empty] | 0.8189 | [6 empty] | insufficient_history
66606 | Cross Town Energy Storage | FALSE | 1.5-2.5h | CS | 175 | 2 |  | FALSE | [9 empty] | 0.79937 | [6 empty] | insufficient_history
66616 | Wolf Tank Storage | FALSE | <1.5h | CS | 150 | 30 | 30 | TRUE | 0.92115 | 1.3787 | 0.91911 | 1.4541 | 1.1274 | 1.194 | 0.32668 | 0.21779 | 0.73634 | 0.70893 | 0.73899 | 0.9433 | 0.020492 | 0.06388 | -3.4166 | -18.2074 | ok
66617 | Cald BESS | FALSE | 2.5-4.5h | CT | 100 | 16 | 16 | TRUE | 0.92358 | 0.84213 | 0.84213 | 1.2157 | 1.0807 | 0.99231 | 0.135 | 0.135 | 0.87952 | 0.84151 | 0.87956 | 0.056591 | 0.060205 | 0.91895 |  |  | insufficient_history
66619 | Lakeview Battery Storage Facility | FALSE | 2.5-4.5h | CS | 1.2 | 7 |  | FALSE | [9 empty] | 0.84789 | [6 empty] | insufficient_history
66620 | Resurgence Solar II | TRUE | >4.5h | CS | 40 | 28 | 28 | TRUE | 0.95123 | 0.40281 | 1.007 | 0.26711 | 0.27325 | 0.44681 | -0.0061374 | -0.015344 | 0.87812 | 0.85444 | 0.88076 | 0.26958 | 0.033295 | 0.13003 | -7.5137 | -308.0192 | ok
66627 | Sonoran Solar Energy | TRUE | 2.5-4.5h | CS | 260 | 31 | 31 | TRUE | 0.8886 | 0.21388 | 0.08226 | 1.406 | 0.24297 | 0.49794 | 1.163 | 0.44731 | 0.8857 | 0.88323 | 0.88145 | 0.10385 | 0.0084355 | 0.11667 | -3.9295 | -116.3642 | ok
66636 | McFarland A Solar and Storage | TRUE | 2.5-4.5h | CS | 100 | 25 | 25 | TRUE | 0.94037 | 0.22544 | 0.22544 | 0.2153 | 0.225 | 0.20239 | -0.0096953 | -0.0096953 | 0.92353 | 0.91486 | 0.92659 | 0.89013 | 0.0058609 | 0.016515 | -1.8823 | -272.2894 | ok
66637 | McFarland B Solar and Storage | TRUE | 2.5-4.5h | CS | 150 | 13 | 13 | TRUE | 0.97108 | 0.71701 | 0.478 | 0.7395 | 0.70369 | 0.20489 | 0.035816 | 0.023877 | 0.92036 | 0.86661 | 0.92026 | 0.98035 | 0.015043 | 0.030608 |  |  | insufficient_history
66648 | Blackwell?s Corner Storage Facility | FALSE | >4.5h | CS | 2 | 10 | 10 | TRUE | 0.78002 | -0.00035205 | -0.017603 | -0.0003543 | -0.00035659 |  | 2.2843e-06 | 0.00011422 | 0.78446 | 0.79042 | 0.78475 | 0.4245 | 0.0092996 | 0.00014493 |  |  | insufficient_history
66650 | Bear Canyon | FALSE | 2.5-4.5h | CS | 13 | 17 | 17 | FALSE | 1.0153 | 0.24485 | 1.8835 | 0.25471 | 0.24341 | 0.26941 | 0.011303 | 0.086944 | 0.88338 | 0.88124 | 0.88703 | 0.85676 | 0.016233 | 0.02585 |  |  | insufficient_history
66659 | Acid BESS | FALSE | <1.5h | CS | 97 | 10 | 10 | TRUE | 0.90493 | 0.10023 | 0.10333 | 0.095926 | 0.099824 |  | -0.0038983 | -0.0040189 | 0.88153 | 0.87878 | 0.88036 | 0.53623 | 0.011787 | 0.032954 |  |  | insufficient_history
66660 | Lead BESS 1 | FALSE | <1.5h | CS | 99.4 | 5 |  | FALSE | [9 empty] | 0.93925 | [6 empty] | insufficient_history
66661 | Electrolyte BESS | FALSE | <1.5h | CS | 99.4 | 8 |  | FALSE | [9 empty] | 0.82751 | [6 empty] | insufficient_history
66662 | Lead BESS 2 | FALSE | <1.5h | CS | 32 | 5 |  | FALSE | [9 empty] | 0.94135 | [6 empty] | insufficient_history
66666 | Tumbleweed Energy Storage | FALSE | 2.5-4.5h | CS | 125 | 18 | 18 | TRUE | 0.86526 | 0.23455 | 0.18764 | 0.22982 | 0.10544 | 0.23779 | 0.12438 | 0.099506 | 0.85471 | 0.84993 | 0.85525 | 0.76688 | 0.0050226 | 0.03233 |  |  | insufficient_history
66669 | West Ford Flat | FALSE | 2.5-4.5h | CS | 25 | 17 | 17 | TRUE | 0.91217 | 0.17838 | 0.71353 | 0.16665 | 0.11737 | 0.043681 | 0.049278 | 0.19711 | 0.86014 | 0.85214 | 0.85331 | 0.90619 | 0.0088222 | 0.014819 |  |  | insufficient_history
66688 | Bright Arrow Solar, LLC | TRUE | <1.5h | CS | 103.6 | 11 | 11 | FALSE | 1.0822 | 1.59 | 1.5348 | 1.5314 | 1.6647 | 1.2537 | -0.13331 | -0.12868 | 0.83511 | 0.83309 | 0.84979 | 0.30741 | 0.14233 | 0.79553 |  |  | insufficient_history
66690 | Brazos Bend BESS, LLC | FALSE | <1.5h | CS | 100 | 16 | 16 | FALSE | 1.0148 | 1.2695 | 1.2695 | 1.2253 | 1.4175 | 1.2951 | -0.19218 | -0.19218 | 0.76661 | 0.76087 | 0.77004 | 0.69247 | 0.06084 | 0.22611 |  |  | insufficient_history
66694 | Atrisco Energy Storage | TRUE | 2.5-4.5h | CS | 300 | 11 | 11 | TRUE | 0.89201 | -4.9028 | -1.6343 | -7.0408 | -5.5718 | -23.4431 | -1.469 | -0.48967 | 0.98246 | 0.90001 | 0.89951 | 0.48356 | 0.11172 | 1.6889 |  |  | insufficient_history
66699 | Lockhart Solar PV II | TRUE | <1.5h | CS | 59.7 | 4 |  | FALSE | [9 empty] | 0.79219 | [6 empty] | insufficient_history
66716 | Saint Energy Storage II LLC | FALSE | 2.5-4.5h | CS | 100 | 26 | 26 | TRUE | 0.91542 | 0.98823 | 0.98823 | 0.90089 | 0.5902 | 0.9072 | 0.3107 | 0.3107 | 0.83993 | 0.83431 | 0.84823 | 0.29626 | 0.036852 | 0.3109 | -4.2588 | -64.8839 | ok
66726 | Inland Empire Energy Storage | FALSE | 2.5-4.5h | CS | 70 | 14 | 14 | TRUE | 0.87064 | -0.2094 | -0.29914 | -0.14485 | -0.20835 | -0.30649 | 0.063504 | 0.09072 | 0.88912 | 0.89537 | 0.88817 | 0.88598 | 0.0042027 | 0.021685 |  |  | insufficient_history
66727 | Georgia Ballard BESS | FALSE | 1.5-2.5h | CS | 5 | 23 | 23 | FALSE | 1.1576 | 0.090391 | 1.8078 | 0.0625 | 0.05724 | 0.089658 | 0.0052602 | 0.1052 | 0.76841 | 0.74778 | 0.77632 | 0.29323 | 0.1544 | 0.030623 |  |  | ok
66728 | Springfield BESS | FALSE | 1.5-2.5h | CS | 5 | 23 | 23 | FALSE | 1.3209 | 0.11749 | 2.3499 | 0.08767 | 0.081781 | 0.10991 | 0.0058883 | 0.11777 | 0.74311 | 0.71756 | 0.74719 | 0.48056 | 0.14038 | 0.026657 |  |  | ok
66757 | Bottleneck Energy Storage | FALSE | 2.5-4.5h | CS | 80 | 14 | 14 | TRUE | 0.84287 | -0.064669 | -0.080837 | -0.082156 | -0.1895 | -0.21262 | 0.10735 | 0.13419 | 0.84901 | 0.85058 | 0.84544 | 0.042824 | 0.016443 | 0.088259 |  |  | insufficient_history
66758 | Justin Court Energy Storage | FALSE | <1.5h | CS | 20 | 23 | 23 | TRUE | 0.89892 | 0.046356 | 0.23178 | 0.13998 | 0.087949 | 0.058562 | 0.052033 | 0.26017 | 0.88975 | 0.88904 | 0.89032 | 0.10645 | 0.0082311 | 0.029307 |  |  | insufficient_history
66764 | SCH - (2A) 156 Barhydt Rd Glenville | TRUE | 2.5-4.5h | CS | 2.5 | 15 | 15 | TRUE | 0.7374 | -0.00097707 | -0.039083 | 0.0048123 | 0.0096627 | -0.00067026 | -0.0048504 | -0.19402 | 0.78213 | 0.75225 | 0.83529 | 0.040221 | 0.084162 | 0.0013238 |  |  | insufficient_history
66765 | SCH County - (2B) 4982 Rynex Corners Rd | TRUE | 2.5-4.5h | CS | 2.5 | 16 | 16 | TRUE | 0.99954 | 0.010667 | 0.42667 | 0.0022038 | 0.01364 |  | -0.011436 | -0.45746 | 0.87728 | 0.81679 | 0.87149 | 0.62325 | 0.062762 | 0.0022165 |  |  | insufficient_history
66767 | Source Power Company - Richland | TRUE | 2.5-4.5h | CS | 2.5 | 24 | 24 | TRUE | 0.9498 | 0.00124 | 0.049598 | 0.0017722 | 0.0012508 | 0.0015005 | 0.00052139 | 0.020856 | 0.9379 | 0.9074 | 0.93131 | 0.43455 | 0.019558 | 0.00030156 | -0.044743 | -0.66082 | ok
66772 | Estrella Solar & Storage | TRUE | 2.5-4.5h | CS | 28 | 22 | 22 | TRUE | 0.89305 | 0.010826 | 0.038665 | 0.034798 | 0.010674 | -0.045498 | 0.024124 | 0.086158 | 0.89044 | 0.88887 | 0.89342 | 0.28785 | 0.0049834 | 0.0038078 |  |  | insufficient_history
66773 | Raceway Solar & Storage | TRUE | 2.5-4.5h | CS | 80 | 20 | 20 | TRUE | 0.89259 | -0.058378 | -0.072973 | -0.11266 | -0.054154 | -0.19136 | -0.058502 | -0.073128 | 0.89604 | 0.90151 | 0.89764 | 0.38093 | 0.0055969 | 0.017541 |  |  | insufficient_history
66782 | Hamilton BESS | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.9648 | 0.027851 | 0.28132 | 0.027139 | 0.028739 | 0.032891 | -0.0015998 | -0.01616 | 0.84943 | 0.84161 | 0.86618 | 0.71486 | 0.022001 | 0.0037501 | -9.2844 | -141.6554 | ok
66783 | Weil Tract BESS | FALSE | <1.5h | CS | 9.9 | 20 | 20 | TRUE | 0.92669 | 0.017479 | 0.17656 | 0.017762 | 0.014777 | 0.014662 | 0.0029857 | 0.030159 | 0.81392 | 0.80174 | 0.83138 | 0.92824 | 0.012208 | 0.0011455 |  |  | insufficient_history
66784 | Pauline BESS | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.91844 | 0.015581 | 0.15738 | 0.017731 | 0.01431 | 0.010382 | 0.0034209 | 0.034554 | 0.82809 | 0.81984 | 0.84321 | 0.61296 | 0.0243 | 0.0026397 | -13.4803 | -169.0662 | ok
66788 | Mineral Wells East BESS | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.94587 | 0.026423 | 0.2669 | 0.026782 | 0.02696 | 0.025442 | -0.00017824 | -0.0018004 | 0.80543 | 0.79254 | 0.82854 | 0.89479 | 0.016586 | 0.0019317 | -12.536 | -119.9429 | ok
66789 | Lufkin South BESS | FALSE | <1.5h | CS | 9.9 | 23 | 23 | TRUE | 0.82512 | 0.004585 | 0.046313 | 0.016674 | 0.01526 | 0.0040835 | 0.0014141 | 0.014283 | 0.80944 | 0.80007 | 0.82635 | 0.18259 | 0.02366 | 0.0021169 |  |  | insufficient_history
66790 | Judkins BESS | FALSE | <1.5h | CS | 9.9 | 24 | 24 | FALSE | 1.0313 | 0.030389 | 0.30696 | 0.017254 | 0.022088 | 0.031061 | -0.0048336 | -0.048825 | 0.90232 | 0.89447 | 0.90418 | 0.81544 | 0.018139 | 0.0030823 |  |  | ok
66791 | Garden City East BESS | FALSE | <1.5h | CS | 9.9 | 23 | 23 | TRUE | 0.92632 | 0.010839 | 0.10948 | 0.011895 | 0.011232 | 0.011104 | 0.00066294 | 0.0066964 | 0.88425 | 0.85988 | 0.88701 | 0.28603 | 0.018975 | 0.0037368 |  |  | insufficient_history
66792 | Falfurrias BESS | FALSE | <1.5h | CS | 9.9 | 18 | 18 | TRUE | 0.968 | 0.024148 | 0.24392 | 0.02441 | 0.023795 | 0.024242 | 0.00061503 | 0.0062124 | 0.80711 | 0.80168 | 0.81497 | 0.78656 | 0.029232 | 0.0031448 |  |  | insufficient_history
66794 | Diboll BESS | FALSE | <1.5h | CS | 9.9 | 24 | 24 | TRUE | 0.82266 | 0.0065412 | 0.066072 | 0.010452 | 0.0061427 | 0.002648 | 0.0043098 | 0.043533 | 0.78496 | 0.78368 | 0.7799 | 0.15356 | 0.03379 | 0.0032742 | -30.457 | -280.7755 | ok
66795 | CISCO BESS | FALSE | <1.5h | CS | 9.9 | 17 | 17 | TRUE | 0.97453 | 0.032316 | 0.32643 | 0.035022 | 0.032975 | 0.030193 | 0.0020468 | 0.020675 | 0.83499 | 0.83336 | 0.83851 | 0.47463 | 0.048401 | 0.0087787 |  |  | insufficient_history
66799 | Bishop Ranch - BR 1-Y | TRUE | 1.5-2.5h | CS | 0.7 | 10 | 10 | TRUE | 0.92678 | 0.0012322 | 0.17602 | 0.0034103 | 0.0025896 |  | 0.00082074 | 0.11725 | 0.84762 | 0.84462 | 0.83974 | 0.16426 | 0.090582 | 0.00098265 |  |  | insufficient_history
66801 | Fence Post Solar Hybrid Project, LLC | TRUE | 1.5-2.5h | CS | 72 | 16 | 16 | TRUE | 0.84929 | -0.065726 | -0.091286 | -0.071465 | -0.0040401 | -0.092828 | -0.067425 | -0.093646 | 0.86771 | 0.86834 | 0.86951 | 0.16007 | 0.017543 | 0.040238 |  |  | insufficient_history
66804 | Borden County BESS | FALSE | 1.5-2.5h | CT | 150 | 17 | 17 | TRUE | 0.84592 | 0.57543 | 0.38362 | 0.56917 | 0.56147 | 0.52405 | 0.0077051 | 0.0051367 | 0.81751 | 0.81637 | 0.81514 | 0.15608 | 0.027186 | 0.34548 |  |  | insufficient_history
66807 | SEPV Cuyama Hybrid | TRUE | 2.5-4.5h | CS | 3 | 24 | 24 | TRUE | 0.95478 | 0.0055936 | 0.18645 | 0.00098532 | 0.00087168 | 0.0051958 | 0.00011364 | 0.003788 | 0.94334 | 0.94183 | 0.94577 | 0.22599 | 0.0061529 | 0.002207 | 1.2316 | 134.3966 | ok
66814 | Sky Ranch Solar | TRUE | 2.5-4.5h | CS | 50 | 21 | 21 | TRUE | 0.8828 | 0.20826 | 0.41652 | 0.19671 | 0.21869 | 0.17838 | -0.021973 | -0.043945 | 0.86177 | 0.86146 | 0.86269 | 0.20184 | 0.013068 | 0.095009 |  |  | insufficient_history
66871 | GulfStar Power, LLC | TRUE | 1.5-2.5h | CS | 300 | 6 |  | FALSE | [9 empty] | 0.79094 | [6 empty] | insufficient_history
66872 | Estonian Solar Project, LLC | TRUE | 1.5-2.5h | CS | 100 | 11 | 11 | TRUE | 0.92713 | 0.61689 | 0.61689 | 0.59998 | 0.58811 |  | 0.011875 | 0.011875 | 0.84718 | 0.83968 | 0.83988 | 0.88171 | 0.014758 | 0.075318 |  |  | insufficient_history
66885 | Baldy Mesa 2_Silver Peak Hybrid | TRUE | 2.5-4.5h | CS | 25 | 11 | 11 | TRUE | 0.89896 | 0.011027 | 0.044109 | -0.037801 | -0.22244 |  | 0.18464 | 0.73857 | 0.89571 | 0.83046 | 0.92151 | 0.00010514 | 0.18266 | 0.35845 |  |  | insufficient_history
66905 | Ables Springs Solar & Storage | TRUE | 1.5-2.5h | CS | 100 | 12 | 12 | TRUE | 0.76825 | -0.049502 | -0.049502 | 0.51503 | 0.043479 | -0.047586 | 0.47155 | 0.47155 | 0.78119 | 0.78374 | 0.78799 | 0.0038047 | 0.096063 | 0.2533 |  |  | insufficient_history
66925 | SR McNeal | TRUE | <1.5h | BL | 20 | 23 | 23 | TRUE | 0.92885 | 0.060269 | 0.30134 | 0.064697 | 0.065889 | 0.060952 | -0.0011924 | -0.0059621 | 0.91073 | 0.90846 | 0.91164 | 0.82291 | 0.0030281 | 0.0061009 |  |  | insufficient_history
66926 | SMT Mercedes LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.9194 | 0.021353 | 0.21353 | 0.018702 | 0.027196 | 0.022809 | -0.0084933 | -0.084933 | 0.84282 | 0.82315 | 0.8507 | 0.76771 | 0.018691 | 0.0025042 | -4.1984 | -38.3643 | ok
66927 | SMT Mission LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.94817 | 0.027631 | 0.27631 | 0.027398 | 0.028788 | 0.027302 | -0.0013899 | -0.013899 | 0.81377 | 0.77621 | 0.81334 | 0.93279 | 0.017445 | 0.0015812 | 1.3719 | -7.7209 | ok
66928 | SMT Santa Rosa LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.9436 | 0.025259 | 0.25259 | 0.023588 | 0.026056 | 0.023787 | -0.0024679 | -0.024679 | 0.81025 | 0.77342 | 0.8006 | 0.93174 | 0.018193 | 0.0014576 | 0.99471 | 2.314 | ok
66929 | SMT Alamo LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.93529 | 0.023306 | 0.23306 | 0.023112 | 0.027805 | 0.021093 | -0.0046924 | -0.046924 | 0.83087 | 0.80812 | 0.83333 | 0.71645 | 0.028304 | 0.0031259 | -0.75336 | -3.5886 | ok
66930 | SMT Bay City LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.94559 | 0.026993 | 0.26993 | 0.036852 | 0.027617 | 0.027355 | 0.0092351 | 0.092351 | 0.8327 | 0.81133 | 0.83975 | 0.85601 | 0.018696 | 0.0023604 | 1.1007 | 2.0734 | ok
66931 | SMT Elsa LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.94217 | 0.027081 | 0.27081 | 0.028612 | 0.028871 | 0.02645 | -0.00025932 | -0.0025932 | 0.83019 | 0.8027 | 0.83008 | 0.96594 | 0.0096422 | 0.0010843 | -0.52483 | -8.1783 | ok
66932 | SMT Los Fresnos LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.97296 | 0.027173 | 0.27173 | 0.023943 | 0.026972 | 0.0274 | -0.0030289 | -0.030289 | 0.81578 | 0.78186 | 0.81202 | 0.91042 | 0.021721 | 0.0018172 | 3.6254 | 3.2176 | ok
66933 | SMT Harlingen II LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.93709 | 0.027638 | 0.27638 | 0.027176 | 0.028332 | 0.027037 | -0.0011566 | -0.011566 | 0.82177 | 0.79642 | 0.81204 | 0.907 | 0.01623 | 0.0018868 | 0.97327 | -5.4992 | ok
66934 | SMT Rio Grande I LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.9345 | 0.025258 | 0.25258 | 0.023666 | 0.026713 | 0.024753 | -0.0030473 | -0.030473 | 0.82162 | 0.7945 | 0.81245 | 0.89526 | 0.017705 | 0.0018418 | -0.47421 | -5.7138 | ok
66935 | SMT Rio Grande II LLC | FALSE | <1.5h | CS | 10 | 24 | 24 | TRUE | 0.9302 | 0.02446 | 0.2446 | 0.024704 | 0.025363 | 0.024181 | -0.00065901 | -0.0065901 | 0.81863 | 0.78793 | 0.81257 | 0.88605 | 0.019727 | 0.0018701 | -2.0629 | -23.0395 | ok
66946 | Lockhart ESS, LLC | FALSE | 2.5-4.5h | CS | 45 | 18 | 18 | TRUE | 0.90952 | 0.32703 | 0.72673 | 0.28856 | 0.19083 | 0.28934 | 0.097731 | 0.21718 | 0.87397 | 0.87343 | 0.87456 | 0.17787 | 0.024904 | 0.17577 |  |  | insufficient_history
66949 | Sagebrush Solar 2 ESS 40 | FALSE | 2.5-4.5h | CS | 40 | 16 | 16 | TRUE | 0.80962 | -0.081248 | -0.20312 | -0.054194 | 0.064859 | -0.17178 | -0.11905 | -0.29763 | 0.82041 | 0.82268 | 0.8226 | 0.021263 | 0.034388 | 0.14732 |  |  | insufficient_history
66950 | Sagebrush Solar 2 ESS 59 | FALSE | 2.5-4.5h | CS | 59 | 16 | 16 | FALSE | 1.0923 | 2.2568 | 3.8251 | 1.3829 | 2.0602 | 1.9923 | -0.67737 | -1.1481 | 0.83764 | 0.83666 | 0.81669 | 0.26524 | 0.1297 | 1.0039 |  |  | insufficient_history
66951 | Scarlet II Hybrid | TRUE | 2.5-4.5h | CS | 150 | 12 | 12 | TRUE | 0.88298 | 0.66941 | 0.44627 | 0.59154 | 0.74915 | 0.66338 | -0.15761 | -0.10507 | 0.84415 | 0.78552 | 0.84775 | 0.49789 | 0.031337 | 0.21258 |  |  | insufficient_history
66966 | Acton-Boxborough Schools BESS | FALSE | 1.5-2.5h | CS | 2.1 | 24 | 24 | TRUE | 0.85079 | 0.0037599 | 0.17904 | 0.0036104 | 0.0036265 | -0.0017887 | -1.6102e-05 | -0.00076676 | 0.80518 | 0.80049 | 0.81814 | 0.44082 | 0.028326 | 0.00090283 | 8.261 | 153.8496 | ok
67019 | Copperhead Solar, LLC | TRUE | <1.5h | CS | 100 | 16 | 16 | FALSE | 1.1024 | 0.74848 | 0.74848 | 0.69957 | 0.84208 | 0.74903 | -0.14251 | -0.14251 | 0.84172 | 0.83318 | 0.84349 | 0.80508 | 0.041016 | 0.09843 |  |  | insufficient_history
67036 | Davistown-Mercer | FALSE | 1.5-2.5h | CS | 2.5 | 13 | 13 | TRUE | 0.87008 | 0.0072393 | 0.28957 | 0.0040762 | 0.0032488 | 0.012553 | 0.00082743 | 0.033097 | 0.82222 | 0.80422 | 0.8284 | 0.25244 | 0.069604 | 0.0037561 |  |  | insufficient_history
67037 | Medoc | FALSE | 1.5-2.5h | CS | 2.5 | 13 | 13 | TRUE | 0.88561 | 0.010548 | 0.42192 | 0.018097 | 0.0088704 | 0.015029 | 0.0092264 | 0.36905 | 0.82129 | 0.78764 | 0.82828 | 0.68881 | 0.040837 | 0.0021377 |  |  | insufficient_history
67039 | Northern Orchard Solar PV, LLC | TRUE | 2.5-4.5h | CS | 92 | 6 |  | FALSE | [9 empty] | 0.9483 | [6 empty] | insufficient_history
67040 | Archie Horne | FALSE | 1.5-2.5h | CS | 10 | 13 | 13 | TRUE | 0.87959 | 0.038116 | 0.38116 | 0.044788 | 0.038862 | 0.039577 | 0.0059262 | 0.059262 | 0.71222 | 0.70122 | 0.71631 | 0.57768 | 0.088617 | 0.0098264 |  |  | insufficient_history
67041 | McLauchin | FALSE | 1.5-2.5h | CS | 15 | 13 | 13 | TRUE | 0.78017 | 0.015015 | 0.1001 | 0.020674 | 0.0078608 | 0.02673 | 0.012813 | 0.08542 | 0.73532 | 0.73534 | 0.74757 | 0.077617 | 0.10651 | 0.015606 |  |  | insufficient_history
67042 | Butler | FALSE | 1.5-2.5h | CS | 10 | 13 | 13 | TRUE | 0.83723 | 0.027067 | 0.27067 | 0.029844 | 0.026483 | 0.030014 | 0.0033616 | 0.033616 | 0.71461 | 0.70263 | 0.70796 | 0.51491 | 0.079025 | 0.0079212 |  |  | insufficient_history
67043 | Double Creek | FALSE | 1.5-2.5h | CS | 5 | 13 | 13 | TRUE | 0.85318 | 0.016769 | 0.33538 | 0.01561 | 0.015087 | 0.0186 | 0.00052362 | 0.010472 | 0.71687 | 0.6966 | 0.70968 | 0.77898 | 0.049459 | 0.0026932 |  |  | insufficient_history
67044 | Fairfield Harbor | FALSE | 1.5-2.5h | CS | 5 | 13 | 13 | TRUE | 0.88707 | 0.017748 | 0.35496 | 0.019062 | 0.017715 | 0.018372 | 0.0013472 | 0.026944 | 0.73307 | 0.71586 | 0.73684 | 0.72503 | 0.061581 | 0.0032954 |  |  | insufficient_history
67083 | Longbow BESS, LLC | FALSE | 1.5-2.5h | CS | 174 | 12 | 12 | TRUE | 0.85775 | 0.45886 | 0.26371 | 0.32731 | 0.51484 | 0.44982 | -0.18753 | -0.10778 | 0.82964 | 0.6415 | 0.83246 | 0.90637 | 0.0072603 | 0.046636 |  |  | insufficient_history
67091 | Yellow Pine II | TRUE | 2.5-4.5h | CS | 85 | 19 | 19 | TRUE | 0.89506 | 0.14709 | 0.17304 | 0.38597 | 0.16681 | 0.093873 | 0.21916 | 0.25783 | 0.8862 | 0.88608 | 0.8876 | 0.03284 | 0.015262 | 0.1936 |  |  | insufficient_history
67092 | Paulsell | TRUE | 2.5-4.5h | CS | 15 | 18 | 18 | TRUE | 0.91618 | 0.10363 | 0.69088 | 0.073681 | 0.036967 | 0.10675 | 0.036714 | 0.24476 | 0.86799 | 0.85461 | 0.87108 | 0.6771 | 0.018949 | 0.017892 |  |  | insufficient_history
67093 | Mojave 16/17/18 BESS | FALSE | <1.5h | CS | 77 | 22 | 22 | TRUE | 0.96233 | 0.26386 | 0.34267 | 0.28549 | 0.2422 | 0.25268 | 0.043297 | 0.05623 | 0.87318 | 0.87206 | 0.87552 | 0.31035 | 0.036727 | 0.087951 |  |  | insufficient_history
67122 | BRIGHT Battery | FALSE | 1.5-2.5h | CS | 1 | 24 | 24 | TRUE | 0.81408 | -0.0024064 | -0.24064 | -0.0032021 | -0.0021503 | -0.0045926 | -0.0010518 | -0.10518 | 0.84485 | 0.86429 | 0.90161 | 0.076424 | 0.051093 | 0.0017835 | -13.9563 | 11.9836 | ok
67162 | Groton BESS 2 | FALSE | 2.5-4.5h | CS | 2 | 19 | 19 | TRUE | 0.84758 | 0.014706 | 0.7353 | 0.015407 | 0.024755 | 0.021959 | -0.0093476 | -0.46738 | 0.78043 | 0.74783 | 0.77778 | 0.89708 | 0.02426 | 0.0012081 |  |  | insufficient_history
67170 | Amazon SAN3 Solar Project | TRUE | 2.5-4.5h | CS | 2.4 | 18 | 18 | TRUE | 0.8399 | -0.0049746 | -0.20728 | -0.00067969 | -0.0046513 | -0.0026458 | 0.0039716 | 0.16549 | 0.86845 | 0.8381 | 0.87053 | 0.46071 | 0.015068 | 0.0013455 |  |  | insufficient_history
67175 | Rodeo Ranch Energy Storage | FALSE | 1.5-2.5h | CS | 300 | 23 | 23 | TRUE | 0.83772 | 0.55946 | 0.18649 | 0.9925 | 0.71729 | 0.58812 | 0.27522 | 0.091739 | 0.81664 | 0.81511 | 0.81775 | 0.24682 | 0.013565 | 0.21327 |  |  | insufficient_history
67183 | Franklin Battery Storage | FALSE | 2.5-4.5h | CS | 60 | 14 | 14 | TRUE | 0.90515 | 0.16582 | 0.27636 | 0.46115 | 0.23915 | 0.20999 | 0.222 | 0.36999 | 0.88909 | 0.88736 | 0.88967 | 0.18962 | 0.014883 | 0.098955 |  |  | insufficient_history
67185 | Groton BESS 1 | FALSE | 2.5-4.5h | CS | 2 | 18 | 18 | TRUE | 0.86999 | 0.0082207 | 0.41104 | 0.0065047 | -0.0055884 | -0.0051787 | 0.012093 | 0.60466 | 0.84218 | 0.82364 | 0.84227 | 0.65298 | 0.018213 | 0.0014982 |  |  | insufficient_history
67186 | Holden BESS 1 | FALSE | 2.5-4.5h | CS | 5 | 17 | 17 | TRUE | 0.88289 | 0.0070787 | 0.14157 | 0.0069621 | 0.0035639 | 0.0056284 | 0.0033982 | 0.067964 | 0.87082 | 0.85564 | 0.87478 | 0.93814 | 0.0051075 | 0.00046934 |  |  | insufficient_history
67187 | Paxton BESS 1 | FALSE | 2.5-4.5h | CS | 3 | 13 | 13 | TRUE | 0.90261 | 0.016254 | 0.5418 | 0.02068 | 0.016827 | 0.017899 | 0.0038524 | 0.12841 | 0.8577 | 0.85437 | 0.85771 | 0.65818 | 0.014661 | 0.0035318 |  |  | insufficient_history
67236 | Anemoi Energy Storage | FALSE | 1.5-2.5h | CS | 200 | 19 | 19 | TRUE | 0.83064 | 0.79594 | 0.39797 | 0.72385 | 0.44465 | 0.24854 | 0.2792 | 0.1396 | 0.78667 | 0.7805 | 0.788 | 0.65538 | 0.017071 | 0.13999 |  |  | insufficient_history
67237 | Ebony Energy Storage | FALSE | 1.5-2.5h | CS | 207.9 | 19 | 19 | TRUE | 0.7669 | -0.68163 | -0.32787 | -0.76923 | -1.0243 | -1.0506 | 0.25505 | 0.12268 | 0.80018 | 0.80266 | 0.79957 | 0.29956 | 0.022583 | 0.2528 |  |  | insufficient_history
67275 | White Plains_RFP-Gedney Way Landfill | TRUE | 2.5-4.5h | CS | 1.3 | 12 | 12 | TRUE | 0.76887 | -0.0002753 | -0.021177 | -0.00021667 | -0.00041154 | -0.00023168 | 0.00019487 | 0.01499 | 0.86641 | 0.71082 | 0.8759 | 0.089488 | 0.12181 | 0.0002777 |  |  | ok
67278 | Bishop Ranch - BR 2600 | TRUE | 1.5-2.5h | CS | 1.1 | 2 |  | FALSE | [9 empty] | 0.67857 | [6 empty] | insufficient_history
67281 | FFP - NY Urbanski | TRUE | 2.5-4.5h | CS | 4 | 5 |  | FALSE | [9 empty] | 0.56885 | [6 empty] | insufficient_history
67282 | FFP - NY Varano | TRUE | 1.5-2.5h | CS | 5 | 6 |  | FALSE | [9 empty] | 0.62752 | [6 empty] | insufficient_history
67284 | Ganado Solar | TRUE | 1.5-2.5h | CS | 70.5 | 22 | 22 | TRUE | 0.83054 | 0.17767 | 0.25202 | 0.37542 | 0.16821 | 0.14005 | 0.20721 | 0.29392 | 0.80889 | 0.78471 | 0.8053 | 0.58328 | 0.023895 | 0.033581 |  |  | insufficient_history
67285 | Sun Streams 3 | TRUE | 2.5-4.5h | CS | 215 | 19 | 19 | TRUE | 0.8991 | 1.3039 | 0.60648 | 2.5786 | 1.3388 | 0.3555 | 1.2399 | 0.57667 | 0.86713 | 0.85891 | 0.85882 | 0.81546 | 0.010195 | 0.15044 |  |  | insufficient_history
67291 | Sun Streams 4 | TRUE | 2.5-4.5h | CS | 300 | 10 | 10 | TRUE | 0.83528 | -2.4773 | -0.82576 | 0.57961 | -1.1215 |  | 1.7011 | 0.56702 | 0.87832 | 0.88079 | 0.87506 | 0.22795 | 0.040812 | 1.6119 |  |  | insufficient_history
67296 | CVEC Round 4 Brewster Captn Golf Course | TRUE | 1.5-2.5h | CS | 0.4 | 33 | 33 | TRUE | 0.85246 | 0.00016045 | 0.040113 | -2.6974e-05 | 0.00012322 | 0.0006869 | -0.0001502 | -0.037549 | 0.832 | 0.85338 | 1 | 0.016332 | 0.10971 | 0.00022365 |  |  | ok
67299 | Pome BESS | FALSE | 2.5-4.5h | CS | 100 | 3 |  | FALSE | [9 empty] | 0.75286 | [6 empty] | insufficient_history
67300 | Rattlesnake Ridge Battery Storage | FALSE | 2.5-4.5h | CS | 11.8 | 19 | 19 | TRUE | 0.87957 | 0.087571 | 0.74213 | 0.094277 | 0.077154 | 0.06794 | 0.017123 | 0.14511 | 0.82611 | 0.82995 | 0.87511 | 0.12737 | 0.083937 | 0.055592 |  |  | insufficient_history
67301 | Parkway Battery Storage | FALSE | 2.5-4.5h | CS | 7.8 | 20 | 20 | TRUE | 0.87973 | -0.00069449 | -0.0089037 | 0.023615 | -0.0010577 | 0.047582 | 0.024673 | 0.31632 | 0.88711 | 0.88239 | 0.8905 | 0.0035878 | 0.013153 | 0.0027279 |  |  | insufficient_history
67302 | Frederick Battery Storage | FALSE | 2.5-4.5h | CS | 7.8 | 14 | 14 | TRUE | 0.88253 | 0.013412 | 0.17196 | 0.0053579 | 0.009007 | 0.047665 | -0.003649 | -0.046783 | 0.8765 | 0.82586 | 0.87987 | 0.25751 | 0.01928 | 0.0065746 |  |  | insufficient_history
67303 | Mead Battery Storage | FALSE | 2.5-4.5h | CS | 7.8 | 18 | 18 | TRUE | 0.95589 | 0.084987 | 1.0896 | 0.073513 | 0.057361 | 0.088839 | 0.016152 | 0.20708 | 0.87765 | 0.83089 | 0.88347 | 0.81563 | 0.014578 | 0.010102 |  |  | insufficient_history
67304 | Davis Battery Storage | FALSE | 2.5-4.5h | CS | 11.8 | 16 | 16 | TRUE | 0.98656 | 0.18298 | 1.5506 | 0.18343 | 0.18119 | 0.18363 | 0.0022484 | 0.019054 | 0.87784 | 0.86829 | 0.88687 | 0.96496 | 0.0080489 | 0.009319 |  |  | insufficient_history
67305 | Bromley Battery Storage | FALSE | 2.5-4.5h | CS | 11.8 | 18 | 18 | TRUE | 0.93195 | 0.083384 | 0.70664 | 0.042183 | 0.056532 | 0.078299 | -0.014349 | -0.1216 | 0.88323 | 0.87707 | 0.89069 | 0.78756 | 0.010241 | 0.010827 |  |  | insufficient_history
67306 | Keenesburg Battery Storage | FALSE | 2.5-4.5h | CS | 11.8 | 19 | 19 | TRUE | 0.92637 | 0.080256 | 0.68013 | 0.068008 | 0.11845 | 0.070762 | -0.050444 | -0.42749 | 0.88199 | 0.87424 | 0.88651 | 0.61124 | 0.014941 | 0.015523 |  |  | insufficient_history
67307 | Platte Valley Battery Storage | FALSE | 2.5-4.5h | CS | 7.8 | 17 | 17 | TRUE | 0.87847 | -0.013141 | -0.16848 | -0.013453 | -0.0089434 | -0.025103 | -0.0045098 | -0.057818 | 0.89003 | 0.89422 | 0.8905 | 0.52035 | 0.0073367 | 0.0032576 |  |  | insufficient_history
67321 | Yuma Solar + Storage | TRUE | 2.5-4.5h | CS | 70 | 10 | 10 | TRUE | 0.97884 | 0.79839 | 1.1406 | 0.77048 | 0.78963 |  | -0.019146 | -0.027352 | 0.90341 | 0.89949 | 0.90028 | 0.16672 | 0.076069 | 0.63107 |  |  | insufficient_history
67323 | High Mesa CO | TRUE | 1.5-2.5h | CS | 11.2 | 9 |  | FALSE | [9 empty] | 0.86464 | [6 empty] | insufficient_history
67328 | Pluto Energy Storage | FALSE | 2.5-4.5h | CS | 75 | 6 |  | FALSE | [9 empty] | 0.7766 | [6 empty] | insufficient_history
67454 | Scatter Wash 1 | FALSE | 2.5-4.5h | CS | 170 | 8 |  | FALSE | [9 empty] | 0.88122 | [6 empty] | insufficient_history
67455 | Scatter Wash 2 | FALSE | 2.5-4.5h | CS | 85 | 8 |  | FALSE | [9 empty] | 0.88542 | [6 empty] | insufficient_history
67474 | Harquahala 2 | TRUE | 2.5-4.5h | CS | 300 | 9 |  | FALSE | [9 empty] | 0.89549 | [6 empty] | insufficient_history
67489 | Cavalry Solar Hybrid | TRUE | 2.5-4.5h | CS | 45 | 20 | 20 | TRUE | 0.89248 | -0.052344 | -0.11632 | 0.027768 | -0.09294 | -0.34417 | 0.12071 | 0.26824 | 0.89832 | 0.90451 | 0.91024 | 0.014033 | 0.026598 | 0.10342 |  |  | insufficient_history
67493 | Pavlov | FALSE | <1.5h | CS | 9.9 | 17 | 17 | TRUE | 0.93865 | 0.023968 | 0.2421 | 0.024144 | 0.026512 | 0.026476 | -0.002368 | -0.02392 | 0.82132 | 0.80435 | 0.8323 | 0.97835 | 0.010152 | 0.00092054 |  |  | insufficient_history
67494 | Mainland | FALSE | <1.5h | CS | 9.9 | 20 | 20 | TRUE | 0.94286 | 0.026433 | 0.267 | 0.026566 | 0.022703 | 0.024289 | 0.0038629 | 0.039019 | 0.79387 | 0.76826 | 0.82524 | 0.93971 | 0.017616 | 0.0015781 |  |  | insufficient_history
67495 | Russek | FALSE | <1.5h | CS | 9.9 | 16 | 16 | TRUE | 0.90479 | 0.0070621 | 0.071334 | 0.0074924 | 0.017447 | 0.018595 | -0.0099551 | -0.10056 | 0.87042 | 0.8504 | 0.87626 | 0.65852 | 0.037269 | 0.0013592 |  |  | insufficient_history
67496 | Sandlake | FALSE | <1.5h | CS | 9.9 | 17 | 17 | TRUE | 0.90067 | 0.0025951 | 0.026213 | 0.002878 | 0.0046874 | 0.0026657 | -0.0018094 | -0.018277 | 0.89092 | 0.89055 | 0.89756 | 0.11316 | 0.010204 | 0.0018758 |  |  | insufficient_history
67498 | McFarland C | FALSE | 2.5-4.5h | CS | 185 | 7 |  | FALSE | [9 empty] | 0.90235 | [6 empty] | insufficient_history
67503 | Serrano | TRUE | 2.5-4.5h | CS | 213.8 | 9 |  | FALSE | [9 empty] | 0.92667 | [6 empty] | insufficient_history
67545 | Marshall Solar Plus LLC | TRUE | >4.5h | CS | 5 | 12 | 12 | TRUE | 0.97272 | 0.1409 | 2.8179 | 0.082197 | 0.063341 | 0.12701 | 0.018856 | 0.37712 | 0.81192 | 0.70073 | 0.82305 | 0.96192 | 0.020423 | 0.0088645 |  |  | insufficient_history
67549 | Kuna BESS | FALSE | 2.5-4.5h | CT | 150 | 7 |  | FALSE | [9 empty] | 0.87285 | [6 empty] | insufficient_history
67573 | Happy Valley Battery Storage | FALSE | 2.5-4.5h | CS | 82 | 6 |  | FALSE | [9 empty] | 0.86638 | [6 empty] | insufficient_history
67577 | Monument Valley | TRUE | 1.5-2.5h | CS | 1 | 24 | 24 | FALSE | 1.0035 | 0.0042165 | 0.42165 | 0.0027499 | 0.002682 | 0.0039445 | 6.7866e-05 | 0.0067866 | 0.99181 | 0.98769 | 0.99336 | 0.80887 | 0.0020247 | 0.00043697 |  |  | ok
67578 | Sandwich | TRUE | 1.5-2.5h | CS | 2 | 24 | 24 | TRUE | 0.99441 | -0.00050183 | -0.025092 | 0.0036789 | 0.00027046 | -4.5748e-05 | 0.0034085 | 0.17042 | 0.99469 | 0.99587 | 1 | 0.0062153 | 0.0044993 | 0.0013529 | -1.7109 | -70.5245 | ok
67579 | AES ES Alamitos 2 LLC | FALSE | 2.5-4.5h | CS | 82 | 12 | 12 | TRUE | 0.88869 | 0.058032 | 0.07077 | -0.070344 | 0.04812 | 0.050489 | -0.11846 | -0.14447 | 0.88456 | 0.87504 | 0.88254 | 0.41143 | 0.005627 | 0.021949 |  |  | insufficient_history
67598 | Desert Willow Energy Storage | FALSE | 1.5-2.5h | CS | 150 | 8 |  | FALSE | [9 empty] | 0.81009 | [6 empty] | insufficient_history
67680 | Kola Energy Center | FALSE | >4.5h | CS | 400 | 6 |  | FALSE | [9 empty] | 0.82942 | [6 empty] | insufficient_history
67695 | Holtville | TRUE | 2.5-4.5h | CS | 30 | 16 | 16 | TRUE | 0.91447 | 0.15548 | 0.51826 | 0.14982 | 0.069718 | 0.16125 | 0.080099 | 0.267 | 0.86667 | 0.87209 | 0.85896 | 0.038121 | 0.092337 | 0.20873 |  |  | insufficient_history
67698 | Coffee Creek BESS | FALSE | 1.5-2.5h | CS | 17 | 13 | 13 | TRUE | 0.89668 | 0.01022 | 0.060119 | 0.073865 | 0.050396 | 0.00023699 | 0.023469 | 0.13805 | 0.88809 | 0.88567 | 0.88824 | 0.055948 | 0.02784 | 0.012658 |  |  | insufficient_history
67710 | TAG | TRUE | 2.5-4.5h | OT | 57.8 | 5 |  | FALSE | [9 empty] | 0.89073 | [6 empty] | insufficient_history
67711 | Seaside BESS | FALSE | 2.5-4.5h | CS | 200 | 6 |  | FALSE | [9 empty] | 0.88981 | [6 empty] | insufficient_history
67712 | Constable BESS | FALSE | 2.5-4.5h | CS | 75 | 13 | 13 | TRUE | 0.87608 | -0.079184 | -0.10558 | 0.18958 | -0.013485 | -0.058873 | 0.20306 | 0.27075 | 0.88441 | 0.88552 | 0.88825 | 0.10809 | 0.01269 | 0.068582 |  |  | insufficient_history
67721 | Al Pastor Battery Storage Plant | FALSE | <1.5h | CS | 100.3 | 14 | 14 | TRUE | 0.90948 | 1.015 | 1.0119 | 0.98801 | 0.99519 | 0.96425 | -0.0071809 | -0.0071594 | 0.76675 | 0.76477 | 0.76131 | 0.75861 | 0.034402 | 0.16528 |  |  | insufficient_history
67734 | Silver State South Storage | FALSE | 2.5-4.5h | CT | 200 | 9 |  | FALSE | [9 empty] | 0.84944 | [6 empty] | insufficient_history
67736 | Silver Peak | FALSE | 2.5-4.5h | CS | 279 | 7 |  | FALSE | [9 empty] | 0.90445 | [6 empty] | insufficient_history
67737 | SMT Ironman Battery Storage Plant | FALSE | <1.5h | CS | 304 | 7 |  | FALSE | [9 empty] | 0.83494 | [6 empty] | insufficient_history
67738 | Citadel Battery Storage Plant | FALSE | <1.5h | CS | 204 | 13 | 13 | TRUE | 0.78721 | 0.69386 | 0.34013 | 0.8407 | 0.90179 | 0.68673 | -0.06109 | -0.029946 | 0.74249 | 0.73385 | 0.73228 | 0.73198 | 0.020384 | 0.12659 |  |  | insufficient_history
67739 | Wigeon Whistle Battery Storage Plant | FALSE | <1.5h | CS | 120 | 13 | 13 | TRUE | 0.80276 | 0.62084 | 0.51737 | 0.95314 | 0.92729 | 0.60326 | 0.025852 | 0.021543 | 0.73573 | 0.73133 | 0.72482 | 0.4547 | 0.042727 | 0.20499 |  |  | insufficient_history
67740 | Anole Energy Storage | FALSE | 1.5-2.5h | CS | 240 | 6 |  | FALSE | [9 empty] | 0.77531 | [6 empty] | insufficient_history
67743 | Bishop Ranch BR 1-X | TRUE | 1.5-2.5h | CS | 0.5 | 14 | 14 | TRUE | 0.97328 | 0.0034743 | 0.69486 | 0.0051232 | 0.0040617 | 0.0040366 | 0.0010614 | 0.21229 | 0.81858 | 0.81511 | 0.79474 | 0.43457 | 0.072254 | 0.001144 |  |  | ok
67745 | White Plains RFP Shapham Place | TRUE | <1.5h | CS | 5 | 3 |  | FALSE | [9 empty] | 0.68512 | [6 empty] | insufficient_history
67752 | Fort Duncan BESS | FALSE | 1.5-2.5h | CS | 102.6 | 7 |  | FALSE | [9 empty] | 0.81848 | [6 empty] | insufficient_history
67758 | Slocum Energy Storage | FALSE | 2.5-4.5h | CS | 14 | 11 | 11 | TRUE | 0.86765 | 0.042273 | 0.30195 | 0.052772 | 0.023783 |  | 0.028989 | 0.20707 | 0.84279 | 0.84146 | 0.85128 | 0.033165 | 0.085173 | 0.07608 |  |  | insufficient_history
67762 | Stampede Solar Hybrid | TRUE | 1.5-2.5h | CS | 72.2 | 15 | 15 | TRUE | 0.81474 | -0.084502 | -0.11704 | 0.1256 | -0.069472 | 0.04615 | 0.19507 | 0.27018 | 0.83963 | 0.8387 | 0.83555 | 0.077261 | 0.035188 | 0.080994 |  |  | insufficient_history
67764 | Rosamond South 1 | TRUE | 2.5-4.5h | CS | 117 | 5 |  | FALSE | [9 empty] | 0.8857 | [6 empty] | insufficient_history
67828 | Mordor ES1 | FALSE | 2.5-4.5h | CS | 25 | 8 |  | FALSE | [9 empty] | 0.86759 | [6 empty] | insufficient_history
67829 | Mordor ES2 | FALSE | 2.5-4.5h | CS | 20 | 8 |  | FALSE | [9 empty] | 0.89127 | [6 empty] | insufficient_history
67843 | Farmersville West | TRUE | 1.5-2.5h | CS | 9.9 | 12 | 12 | TRUE | 0.87609 | -0.018561 | -0.18749 | -0.1074 | -0.12292 | -0.02694 | 0.015527 | 0.15684 | 0.9122 | 0.90039 | 0.91361 | 0.3807 | 0.042889 | 0.0074862 |  |  | insufficient_history
67845 | Junction BESS | FALSE | 1.5-2.5h | CS | 9.9 | 12 | 12 | TRUE | 0.80887 | 0.012724 | 0.12853 | 0.07702 | 0.06768 | 0.014572 | 0.0093404 | 0.094348 | 0.80648 | 0.78036 | 0.81185 | 0.22582 | 0.05434 | 0.0074504 |  |  | insufficient_history
67850 | Arrowleaf Solar and Storage | TRUE | 2.5-4.5h | CS | 35 | 1 |  | FALSE | [9 empty] | 0.87309 | [6 empty] | insufficient_history
67851 | Montague Energy Storage | FALSE | <1.5h | CS | 20 | 14 | 14 | TRUE | 0.87725 | 0.12633 | 0.63165 | 0.1051 | 0.12481 | 0.20017 | -0.019705 | -0.098527 | 0.85704 | 0.80231 | 0.86544 | 0.98292 | 0.018597 | 0.0048079 |  |  | insufficient_history
67855 | Westwing | FALSE | 2.5-4.5h | CS | 200 | 15 | 15 | TRUE | 0.94033 | 1.3779 | 0.68894 | 0.90777 | 1.193 | 1.4461 | -0.28521 | -0.14261 | 0.87214 | 0.8631 | 0.87458 | 0.55593 | 0.025589 | 0.34155 |  |  | insufficient_history
67860 | GFTX BESS | FALSE | 1.5-2.5h | CS | 125 | 19 | 19 | TRUE | 0.95164 | 1.3419 | 1.0735 | 1.4065 | 1.4121 | 1.5748 | -0.0055715 | -0.0044572 | 0.83262 | 0.76733 | 0.82078 | 0.37352 | 0.051055 | 0.42149 |  |  | insufficient_history
67861 | Connolly BESS | FALSE | 1.5-2.5h | CS | 125 | 17 | 17 | TRUE | 0.83155 | -0.059416 | -0.047533 | -0.081017 | -0.15685 | -0.27236 | 0.07583 | 0.060664 | 0.84103 | 0.83961 | 0.84922 | 0.02412 | 0.020329 | 0.097582 |  |  | insufficient_history
67869 | Sundial (Troutdale) BESS | FALSE | 2.5-4.5h | CT | 200 | 13 | 13 | TRUE | 0.88486 | 0.18044 | 0.090218 | 0.14444 | 0.6327 | 0.76062 | -0.48826 | -0.24413 | 0.87962 | 0.87996 | 0.88049 | 0.0077096 | 0.025909 | 0.61721 |  |  | insufficient_history
67880 | Arthur Kill Energy, LLC | FALSE | 2.5-4.5h | CS | 5 | 5 |  | FALSE | [9 empty] | 0.49545 | [6 empty] | insufficient_history
67882 | Empire Clean Energy, LLC | FALSE | 2.5-4.5h | CS | 10 | 7 |  | FALSE | [9 empty] | 0.63218 | [6 empty] | insufficient_history
67883 | Gabby Giffords Clean Energy, LLC | FALSE | 2.5-4.5h | CS | 8 | 7 |  | FALSE | [9 empty] | 0.48779 | [6 empty] | insufficient_history
67886 | Gunther | FALSE | 2.5-4.5h | CS | 3 | 15 | 15 | TRUE | 0.78267 | 0.01248 | 0.41601 | 0.012453 | 0.01125 | 0.012902 | 0.0012029 | 0.040097 | 0.71456 | 0.45855 | 0.66102 | 0.80966 | 0.089036 | 0.0016783 |  |  | ok
67893 | Dunns Bridge II Solar | TRUE | 2.5-4.5h | CS | 56.3 | 12 | 12 | TRUE | 0.8097 | -0.89369 | -1.5874 | 0.98361 | -0.61973 | -0.57141 | 1.6033 | 2.8479 | 0.86454 | 0.8764 | 0.88209 | 0.222 | 0.057596 | 0.52906 |  |  | insufficient_history
67898 | Escape Solar Plant | TRUE | 2.5-4.5h | CS | 100 | 1 |  | FALSE | [9 empty] | 0.87772 | [6 empty] | insufficient_history
67899 | PNY BESS LLC | FALSE | <1.5h | CS | 6.2 | 24 | 24 | TRUE | 0.94369 | 0.020433 | 0.32956 | 0.018262 | 0.0093221 | 0.011675 | 0.0089398 | 0.14419 | 0.92527 | 0.92476 | 0.92493 | 0.12355 | 0.012719 | 0.011603 | 3.292 | 184.801 | ok
67905 | Roadrunner Reserve Phase 1 | FALSE | 2.5-4.5h | CS | 200 | 6 |  | FALSE | [9 empty] | 0.87107 | [6 empty] | insufficient_history
67931 | Daggett 1 | FALSE | 2.5-4.5h | CS | 113.5 | 4 |  | FALSE | [9 empty] | 0.82163 | [6 empty] | insufficient_history
67948 | Hampton Substation Energy Storage | FALSE | >4.5h | CS | 1.8 | 24 | 24 | TRUE | 0.91104 | 0.00019053 | 0.010585 | 0.0011438 | 0.00041123 | 0.0016369 | 0.00073255 | 0.040697 | 0.90675 | 0.90683 | 0.90608 | 0.014841 | 0.012481 | 0.00033097 | 2.0481 | 286.8802 | ok
67963 | Tynan | FALSE | <1.5h | CS | 9.9 | 9 |  | FALSE | [9 empty] | 0.89663 | [6 empty] | insufficient_history
67968 | Burksol Energy Storage | FALSE | 1.5-2.5h | CS | 100 | 9 |  | FALSE | [9 empty] | 0.85704 | [6 empty] | insufficient_history
67973 | Sierra Pinta BESS | FALSE | <1.5h | BL | 113 | 2 |  | FALSE | [9 empty] | 0.83771 | [6 empty] | insufficient_history
68012 | Caballero | FALSE | 2.5-4.5h | CS | 99.7 | 9 |  | FALSE | [9 empty] | 0.85118 | [6 empty] | insufficient_history
68023 | BCE Seal Beach | TRUE | 2.5-4.5h | CS | 16.7 | 2 |  | FALSE | [9 empty] | 0.9197 | [6 empty] | insufficient_history
68058 | Prairie Center Energy LLC | FALSE | >4.5h | CS | 35.4 | 13 | 13 | TRUE | 0.90552 | 0.063336 | 0.17892 | -0.50352 | -0.032987 | 0.060857 | -0.47053 | -1.3292 | 0.91504 | 0.85826 | 0.89522 | 0.18114 | 0.085415 | 0.040603 |  |  | insufficient_history
68064 | CA- US Foods- Livermore | TRUE | 1.5-2.5h | CS | 1.2 | 17 | 17 | FALSE | 3.8117 | 0.24138 | 20.1152 | 0.37248 | 0.32654 | 0.28819 | 0.045939 | 3.8282 | 0.73246 | 0.73863 | 0.7541 | 0.72887 | 0.19232 | 0.038012 |  |  | insufficient_history
68069 | Old Frontier Solar III | TRUE | <1.5h | CT | 2 | 20 | 20 | TRUE | 0.9135 | -0.00049603 | -0.024802 | -0.00019328 | -0.0010339 | -0.00052539 | 0.00084058 | 0.042029 | 0.92822 | 0.92832 | 0.92262 | 0.08245 | 0.015678 | 0.00039003 | 8.1236 | 54.6238 | ok
68146 | Angelo Storage | FALSE | 1.5-2.5h | CS | 100 | 11 | 11 | TRUE | 0.93176 | 0.68411 | 0.68411 | 0.69117 | 0.56223 |  | 0.12894 | 0.12894 | 0.8427 | 0.83934 | 0.8368 | 0.38337 | 0.052923 | 0.28921 |  |  | insufficient_history
68147 | Coffeen Solar BESS | TRUE | 2.5-4.5h | CS | 2 | 13 | 13 | TRUE | 0.67817 | 6.9958e-05 | 0.0034979 | -0.018732 | -0.011805 | -0.00035448 | -0.0069269 | -0.34634 | 0.68012 | 0.68904 | 0.68644 | 0.00094893 | 0.071325 | 0.00068442 |  |  | insufficient_history
68148 | Baldwin Solar BESS | TRUE | 2.5-4.5h | CS | 2 | 11 | 11 | TRUE | 0.57822 | -0.012652 | -0.63262 | -0.03859 | -0.01405 |  | -0.02454 | -1.227 | 0.65609 | 0.70479 | 0.71111 | 0.12487 | 0.24166 | 0.011165 |  |  | insufficient_history
68189 | Great Kiskadee Storage | FALSE | 1.5-2.5h | CS | 100 | 11 | 11 | TRUE | 0.8998 | 0.50877 | 0.50877 | 0.42677 | 0.41076 |  | 0.016006 | 0.016006 | 0.79242 | 0.78602 | 0.78886 | 0.56119 | 0.050444 | 0.14996 |  |  | insufficient_history
68266 | North Juvenile Detention Center Solar | TRUE | 1.5-2.5h | CS | 0.3 | 21 | 21 | TRUE | 0.79297 | 0.00073143 | 0.24381 | 0.00079345 | 0.002256 | 0.0012996 | -0.0014626 | -0.48753 | 0.75714 | 0.74098 | 0.77778 | 0.15243 | 0.11461 | 0.00039568 | 17.401 | 178.1071 | ok
68322 | Atlas VII | FALSE | 2.5-4.5h | CS | 300 | 2 |  | FALSE | [9 empty] | 0.85219 | [6 empty] | insufficient_history
68324 | Atlas IX | FALSE | 2.5-4.5h | CS | 150 | 2 |  | FALSE | [9 empty] | 0.90609 | [6 empty] | insufficient_history
68423 | St Gall Energy Storage II | FALSE | 1.5-2.5h | CS | 100 | 4 |  | FALSE | [9 empty] | 0.89221 | [6 empty] | insufficient_history
68424 | Tibbits Energy Storage | FALSE | 2.5-4.5h | CS | 104.9 | 7 |  | FALSE | [9 empty] | 0.85309 | [6 empty] | insufficient_history
68475 | Kearsarge Riverpark I LLC | FALSE | 1.5-2.5h | CS | 5 | 8 |  | FALSE | [9 empty] | 0.80728 | [6 empty] | insufficient_history
68476 | Kearsarge Riverpark II LLC | FALSE | 1.5-2.5h | CS | 5 | 8 |  | FALSE | [9 empty] | 0.81626 | [6 empty] | insufficient_history
68493 | Central Heating Plant | FALSE | <1.5h | CS | 3.3 | 23 | 23 | TRUE | 0.85618 | 0.031648 | 0.95902 | 0.020403 | 0.030618 | 0.030359 | -0.010215 | -0.30955 | 0.75138 | 0.7215 | 0.72727 | 0.55798 | 0.058753 | 0.0061467 | -4.0549 | -84.9089 | ok
68496 | Lower Rio Energy Storage | FALSE | 1.5-2.5h | CS | 60 | 5 |  | FALSE | [9 empty] | 0.80681 | [6 empty] | insufficient_history
68522 | Bishop Ranch - BR 8-O | TRUE | 1.5-2.5h | CS | 0.5 | 1 |  | FALSE | [9 empty] | 1 | [6 empty] | insufficient_history
68524 | Bishop Ranch - BR 15-AA | TRUE | 1.5-2.5h | CS | 0.5 | 5 |  | FALSE | [9 empty] | 0.82 | [6 empty] | insufficient_history
68547 | Tipton 1 - (CA) | TRUE | 2.5-4.5h | CS | 1 | 10 | 10 | TRUE | 0.92136 | 0.0023341 | 0.23341 | 0.0018471 | 0.0021312 |  | -0.00028407 | -0.028407 | 0.90539 | 0.7586 | 0.89869 | 0.16303 | 0.017418 | 0.0018698 |  |  | insufficient_history
68548 | Tipton 2 - (CA) | TRUE | 2.5-4.5h | CS | 0.7 | 8 |  | FALSE | [9 empty] | 0.85068 | [6 empty] | insufficient_history
68576 | Breckinridge Energy Storage | FALSE | 2.5-4.5h | CS | 65 | 8 |  | FALSE | [9 empty] | 0.85242 | [6 empty] | insufficient_history
68577 | Woodward Energy Storage | FALSE | 2.5-4.5h | CS | 40 | 8 |  | FALSE | [9 empty] | 0.8435 | [6 empty] | insufficient_history
68596 | Dominguez Energy Storage | FALSE | 2.5-4.5h | CS | 200 | 1 |  | FALSE | [9 empty] | 0.92146 | [6 empty] | insufficient_history
68605 | Mauna Loa Macadamia Nut | TRUE | 2.5-4.5h | CS | 0.5 | 22 | 22 | TRUE | 0.86596 | -1.3078e-05 | -0.0026155 | -0.000164 | 0.00049224 | 0.0010903 | -0.00065624 | -0.13125 | 0.87107 | 0.87 | 0.87939 | 0.00019804 | 0.02493 | 0.00020778 | 4.7219 | 211.87 | ok
68613 | Guajillo Energy Storage | FALSE | <1.5h | CS | 228.7 | 3 |  | FALSE | [9 empty] | 0.89568 | [6 empty] | insufficient_history
68617 | Sky Ranch BESS II | FALSE | 2.5-4.5h | CT | 100 | 2 |  | FALSE | [9 empty] | 0.88873 | [6 empty] | insufficient_history
68679 | Partridge Solar | TRUE | <1.5h | CS | 3 | 24 | 24 | FALSE | 1.0279 | 0.0039967 | 0.13322 | 0.003662 | 0.0036053 | 0.003924 | 5.6724e-05 | 0.0018908 | 0.95954 | 0.94563 | 0.96327 | 0.37767 | 0.031021 | 0.0010938 |  |  | ok
68680 | Saddleback Solar | TRUE | <1.5h | CS | 2.5 | 24 | 24 | TRUE | 0.99288 | 0.001716 | 0.06864 | 6.3431e-05 | -0.0012138 | 0.0013437 | 0.0012772 | 0.051089 | 0.96893 | 0.95898 | 0.96713 | 0.54247 | 0.0094996 | 0.00033599 |  |  | ok
68683 | Crockett BESS | FALSE | 1.5-2.5h | CS | 10 | 9 |  | FALSE | [9 empty] | 0.61826 | [6 empty] | insufficient_history
68684 | Century BESS | FALSE | 1.5-2.5h | CS | 10 | 12 | 12 | TRUE | 0.82852 | -0.0055303 | -0.055303 | 0.028353 | -0.011941 | 0.0042003 | 0.040294 | 0.40294 | 0.83866 | 0.83865 | 0.83247 | 0.0049744 | 0.055918 | 0.024734 |  |  | insufficient_history
68685 | Liggett Switch | FALSE | <1.5h | CS | 10 | 12 | 12 | TRUE | 0.88787 | 0.032395 | 0.32395 | 0.036988 | 0.034581 | 0.024408 | 0.0024064 | 0.024064 | 0.80764 | 0.80408 | 0.80593 | 0.55245 | 0.03463 | 0.0092205 |  |  | insufficient_history
68686 | Citrus City BESS | FALSE | 1.5-2.5h | CS | 9.9 | 6 |  | FALSE | [9 empty] | 0.77002 | [6 empty] | insufficient_history
68687 | Rio Grande City BESS 2 | FALSE | 1.5-2.5h | CS | 9.9 | 6 |  | FALSE | [9 empty] | 0.7747 | [6 empty] | insufficient_history
68742 | Skyline Solar | TRUE | <1.5h | CS | 3 | 24 | 24 | TRUE | 0.99604 | 0.0016893 | 0.056309 | 0.0017493 | 0.00090675 | 0.0016686 | 0.00084252 | 0.028084 | 0.96916 | 0.95961 | 0.96276 | 0.58913 | 0.008437 | 0.00030077 |  |  | ok
68743 | Adams Grove Solar | TRUE | <1.5h | CS | 3.3 | 24 | 24 | FALSE | 1.0104 | 0.0083547 | 0.25317 | 0.015121 | 0.011803 | 0.0093615 | 0.0033177 | 0.10054 | 0.95378 | 0.94352 | 0.95732 | 0.76396 | 0.010907 | 0.0009901 |  |  | ok
68773 | Apollo | TRUE | 1.5-2.5h | CS | 1.3 | 19 | 19 | TRUE | 0.9261 | 0.0009087 | 0.0699 | 0.00077163 | -0.0048318 | 0.0030006 | 0.0056034 | 0.43103 | 0.92832 | 0.92075 | 0.93182 | 0.074964 | 0.026661 | 0.00077419 |  |  | insufficient_history
68801 | Kingman Energy Storage | FALSE | 2.5-4.5h | CS | 50 | 2 |  | FALSE | [9 empty] | 0.73118 | [6 empty] | insufficient_history
68802 | Minco II Energy Storage | FALSE | <1.5h | CS | 65 | 8 |  | FALSE | [9 empty] | 0.86068 | [6 empty] | insufficient_history
68809 | Hidden Lakes Reliability Project | FALSE | 1.5-2.5h | CS | 220 | 1 |  | FALSE | [9 empty] | 0.59607 | [6 empty] | insufficient_history
68816 | Google Bayhill Solar PV and Microgrid | TRUE | 1.5-2.5h | CS | 2.6 | 18 | 18 | TRUE | 0.67247 | 0.00017174 | 0.0066054 | -0.0061221 | -0.0001865 | 0.010019 | -0.0059356 | -0.22829 | 0.73393 | 0.68529 | 0.73495 | 0.0010258 | 0.13238 | 0.0013399 |  |  | insufficient_history
68842 | Chillingham Storage | FALSE | <1.5h | CS | 150 | 6 |  | FALSE | [9 empty] | 0.81658 | [6 empty] | insufficient_history
68868 | Shallow Basket | TRUE | 2.5-4.5h | CS | 50 | 5 |  | FALSE | [9 empty] | 0.90373 | [6 empty] | insufficient_history
68874 | Inertia Energy Storage | FALSE | 2.5-4.5h | CS | 13 | 8 |  | FALSE | [9 empty] | 0.79769 | [6 empty] | insufficient_history
68875 | Wakefield MA BESS 1 | FALSE | 2.5-4.5h | CS | 5 | 7 |  | FALSE | [9 empty] | 0.88736 | [6 empty] | insufficient_history
68878 | Longhorn Storage | FALSE | <1.5h | CS | 165 | 9 |  | FALSE | [9 empty] | 0.86496 | [6 empty] | insufficient_history
68879 | Bocanova Energy Storage | FALSE | 1.5-2.5h | CS | 150 | 5 |  | FALSE | [9 empty] | 0.79185 | [6 empty] | insufficient_history
68891 | Visalia - (CA) | TRUE | 2.5-4.5h | CS | 1 | 6 |  | FALSE | [9 empty] | 0.88901 | [6 empty] | insufficient_history
68895 | Libra Storage | FALSE | <1.5h | CS | 236.3 | 8 |  | FALSE | [9 empty] | 0.70107 | [6 empty] | insufficient_history
68896 | Sun Valley Storage | FALSE | <1.5h | CS | 123.3 | 8 |  | FALSE | [9 empty] | 0.80026 | [6 empty] | insufficient_history
68906 | Pine Forest Solar I | TRUE | <1.5h | CS | 200 | 1 |  | FALSE | [9 empty] | 0.97233 | [6 empty] | insufficient_history
68912 | Padua 1 | FALSE | 2.5-4.5h | CS | 50 | 6 |  | FALSE | [9 empty] | 0.7416 | [6 empty] | insufficient_history
68997 | Thermo Fisher Pleasanton | TRUE | 2.5-4.5h | CS | 0.7 | 7 |  | FALSE | [9 empty] | 0.91285 | [6 empty] | insufficient_history
69023 | Knightdale Battery | FALSE | 1.5-2.5h | CS | 100 | 2 |  | FALSE | [9 empty] | 0.73705 | [6 empty] | insufficient_history
69026 | Tanzanite Storage | FALSE | <1.5h | CS | 283.2 | 2 |  | FALSE | [9 empty] | 0.84301 | [6 empty] | insufficient_history
69045 | Sealy BESS | FALSE | 1.5-2.5h | CS | 200 | 5 |  | FALSE | [9 empty] | 0.94784 | [6 empty] | insufficient_history
69122 | Jackson Fuller Energy Storage | FALSE | <1.5h | CS | 100 | 4 |  | FALSE | [9 empty] | 0.8887 | [6 empty] | insufficient_history
69128 | Chesapeake Beach BESS | FALSE | 1.5-2.5h | CS | 1.1 | 11 | 11 | TRUE | 0.86819 | 0.0057582 | 0.52348 | 0.0059533 | 0.0057993 | 0.0080548 | 0.00015405 | 0.014005 | 0.81461 | 0.73675 | 0.82353 | 0.9868 | 0.010427 | 0.00022197 |  |  | insufficient_history
69171 | Allen 1 Battery Energy Storage System | FALSE | 2.5-4.5h | CS | 50 | 2 |  | FALSE | [9 empty] | 0.88505 | [6 empty] | insufficient_history
69187 | Big Bend 1 Solar and Battery Storage | TRUE | 1.5-2.5h | CS | 12.6 | 1 |  | FALSE | [9 empty] | 0.6 | [6 empty] | insufficient_history
69190 | GreenStruxure BBU004, LLC | TRUE | 1.5-2.5h | CS | 0.2 | 12 | 12 | TRUE | 0.79007 | -0.00026526 | -0.13263 | -0.001637 | -0.00025077 | -0.0005584 | -0.0013863 | -0.69314 | 0.83871 | 0.85492 | 0.83333 | 0.11366 | 0.081924 | 0.00023425 |  |  | insufficient_history
69191 | GreenStruxure REP009, LLC | TRUE | 1.5-2.5h | CS | 0.2 | 12 | 12 | FALSE | 1.0366 | 0.0020407 | 1.0203 | 0.0029369 | 0.0026685 | 0.00043243 | 0.00026833 | 0.13416 | 0.84762 | 0.84421 | 0.85417 | 0.50663 | 0.097043 | 0.00063681 |  |  | insufficient_history
69210 | Salem Henningsen | TRUE | 1.5-2.5h | CS | 1 | 12 | 12 | TRUE | 1 | 4.9103e-18 | 4.9103e-16 | -6.0192e-17 | -4.6391e-17 | -2.8792e-17 | -1.3801e-17 | -1.3801e-15 | 1 | 1 | 1 |  | 7.442e-16 | 5.837e-18 |  |  | insufficient_history
69244 | Cross Trails Energy Storage Project | FALSE | 1.5-2.5h | CS | 58.3 | 8 |  | FALSE | [9 empty] | 0.80537 | [6 empty] | insufficient_history
69250 | Suwannee | FALSE | <1.5h | CS | 5 | 7 |  | FALSE | [9 empty] | 0.58404 | [6 empty] | insufficient_history
69288 | Palm Springs DAC PV | TRUE | 1.5-2.5h | CS | 0.3 | 10 | 10 | TRUE | 0.91347 | 0.00099439 | 0.33146 | 0.0012613 | 0.0011192 |  | 0.00014212 | 0.047374 | 0.83529 | 0.8241 | 0.83333 | 0.45627 | 0.053228 | 0.00038379 |  |  | insufficient_history
69298 | PP Jaguar BESS LLC | FALSE | 1.5-2.5h | CS | 300 | 1 |  | FALSE | [9 empty] | 0.87599 | [6 empty] | insufficient_history
69300 | Regis Continental | FALSE | <1.5h | CS | 9.9 | 3 |  | FALSE | [9 empty] | 0.85423 | [6 empty] | insufficient_history
69301 | Regis Gregory | FALSE | <1.5h | CS | 9.9 | 6 |  | FALSE | [9 empty] | 0.64933 | [6 empty] | insufficient_history
69302 | Regis Palacios | FALSE | <1.5h | CS | 9.9 | 6 |  | FALSE | [9 empty] | 0.71738 | [6 empty] | insufficient_history
69331 | Regis Carrizo Springs | FALSE | <1.5h | CS | 9.9 | 5 |  | FALSE | [9 empty] | 0.65647 | [6 empty] | insufficient_history
69333 | Regis Goodwin LLC | FALSE | <1.5h | CS | 9.9 | 4 |  | FALSE | [9 empty] | 0.60955 | [6 empty] | insufficient_history
69334 | Johnson City BESS | FALSE | 1.5-2.5h | CS | 2.3 | 9 |  | FALSE | [9 empty] | 0.3602 | [6 empty] | insufficient_history
69344 | Regis Hearn | FALSE | <1.5h | CS | 9.9 | 4 |  | FALSE | [9 empty] | 0.51796 | [6 empty] | insufficient_history
69345 | Regis Mason | FALSE | <1.5h | CS | 9.9 | 6 |  | FALSE | [9 empty] | 0.74551 | [6 empty] | insufficient_history
69346 | Regis Monte Cristo LLC | FALSE | <1.5h | CS | 9.9 | 7 |  | FALSE | [9 empty] | 0.78787 | [6 empty] | insufficient_history
69347 | Regis Muenster | FALSE | <1.5h | CS | 9.9 | 6 |  | FALSE | [9 empty] | 0.81427 | [6 empty] | insufficient_history
69348 | Regis Pirate | FALSE | <1.5h | CS | 9.9 | 9 |  | FALSE | [9 empty] | 0.6582 | [6 empty] | insufficient_history
69349 | Regis Falfurrias | FALSE | <1.5h | CS | 9.9 | 8 |  | FALSE | [9 empty] | 0.64373 | [6 empty] | insufficient_history
69350 | Matta Power Station | FALSE | 1.5-2.5h | CS | 10 | 12 | 12 | TRUE | 0.97351 | 0.047571 | 0.47571 | 0.05113 | 0.032418 | 0.06289 | 0.018712 | 0.18712 | 0.8932 | 0.89246 | 0.89199 | 0.14447 | 0.074588 | 0.036608 |  |  | insufficient_history
69353 | Sunset Ridge Energy Center, LLC | FALSE | 1.5-2.5h | CS | 9.9 | 12 | 12 | TRUE | 0.86283 | 0.013998 | 0.1414 | 0.0048124 | 0.025605 | 0.020321 | -0.020792 | -0.21002 | 0.83694 | 0.76122 | 0.78646 | 0.65504 | 0.092057 | 0.0032124 |  |  | insufficient_history
69365 | SMT Dallas BESS | FALSE | <1.5h | CS | 10 | 3 |  | FALSE | [9 empty] | 0.85822 | [6 empty] | insufficient_history
69366 | SME Mission II BESS | FALSE | <1.5h | CS | 10 | 12 | 12 | TRUE | 0.88026 | 0.015743 | 0.15743 | 0.019755 | 0.025334 | 0.016179 | -0.0055793 | -0.055793 | 0.80983 | 0.80195 | 0.8278 | 0.28151 | 0.073425 | 0.0079534 |  |  | insufficient_history
69407 | Dogfish BESS | FALSE | <1.5h | CS | 75 | 7 |  | FALSE | [9 empty] | 0.72962 | [6 empty] | insufficient_history
69411 | Snyder BESS | FALSE | 1.5-2.5h | CS | 10 | 12 | 12 | TRUE | 0.89207 | 0.021575 | 0.21575 | -0.004502 | -0.024741 | 0.0086811 | 0.020239 | 0.20239 | 0.85063 | 0.85255 | 0.85095 | 0.03336 | 0.096548 | 0.036726 |  |  | insufficient_history
69413 | Sweetwater BESS | FALSE | 1.5-2.5h | CS | 10 | 12 | 12 | TRUE | 0.92267 | 0.04044 | 0.4044 | 0.019475 | 0.018198 | 0.030572 | 0.0012772 | 0.012772 | 0.86348 | 0.86092 | 0.86344 | 0.60067 | 0.020982 | 0.010427 |  |  | insufficient_history
69414 | Blevins Solar & Storage | TRUE | 1.5-2.5h | CS | 180 | 1 |  | FALSE | [9 empty] | 0.74021 | [6 empty] | insufficient_history
69415 | Westover BESS | FALSE | 1.5-2.5h | CS | 10 | 12 | 12 | TRUE | 0.91568 | 0.035524 | 0.35524 | 0.021004 | 0.019536 | 0.031856 | 0.0014688 | 0.014688 | 0.86801 | 0.86493 | 0.86382 | 0.54787 | 0.019216 | 0.010205 |  |  | insufficient_history
69454 | Crosby Clean Energy Center (BESS) | FALSE | 1.5-2.5h | OT | 12 | 9 |  | FALSE | [9 empty] | 0.92144 | [6 empty] | insufficient_history
69456 | Maverick Clean Energy Center (BESS) | FALSE | 1.5-2.5h | OT | 12 | 8 |  | FALSE | [9 empty] | 0.86849 | [6 empty] | insufficient_history
69459 | Spencer Clean Energy Center (BESS) | FALSE | 1.5-2.5h | OT | 12 | 5 |  | FALSE | [9 empty] | 0.81719 | [6 empty] | insufficient_history
69460 | Winmil Clean Energy Center (BESS) | FALSE | 1.5-2.5h | OT | 12 | 12 | 12 | FALSE | 1.0108 | 0.067076 | 0.55896 | 0.081885 | 0.068064 | 0.071643 | 0.013821 | 0.11517 | 0.9095 | 0.90244 | 0.90521 | 0.73242 | 0.02477 | 0.012821 |  |  | insufficient_history
69576 | Non-PLD US-El Paso - BSSAT004 | FALSE | <1.5h | CS | 9.9 | 8 |  | FALSE | [9 empty] | 0.81808 | [6 empty] | insufficient_history
69727 | Martinsville BESS | TRUE | <1.5h | CS | 10.1 | 3 |  | FALSE | [9 empty] | 0.27863 | [6 empty] | insufficient_history
69803 | 55 Drive BESS | FALSE | <1.5h | CT | 4.6 | 4 |  | FALSE | [9 empty] | 0.84521 | [6 empty] | insufficient_history

## hazards
signature | axis | k | eta | loglik | k_lo | k_hi | n_events | n_units | loglik_calendar_density | aic | shape | best_axis
FULL_OUTAGE | age_years | 1.2192 | 6.7106 | -793.5759 | 1.0987 | 1.3529 | 273 | 825 | -793.5759 | 1591.1518 | wear-out (k>1) | age_years
FULL_OUTAGE | cum_efc_x100 | 0.25144 | 11.7853 | -872.514 | 0.21087 | 0.29981 | 273 | 825 | -2708.5574 | 5421.1148 | infant mortality (k<1) | age_years
PARTIAL_AVAILABILITY | age_years | 1.0679 | 6.6362 | -814.4152 | 0.96005 | 1.1878 | 281 | 825 | -814.4152 | 1632.8303 | random (k~1) | age_years
PARTIAL_AVAILABILITY | cum_efc_x100 | 0.65241 | 19.4104 | -1108.2768 | 0.5945 | 0.71597 | 281 | 825 | -875.3016 | 1754.6032 | infant mortality (k<1) | age_years
THERMAL_AUX | age_years | 0.31608 | 232.5911 | -300.6478 | 0.27659 | 0.36119 | 100 | 825 | -300.6478 | 605.2956 | infant mortality (k<1) | age_years
THERMAL_AUX | cum_efc_x100 | 0.38923 | 239.7204 | -454.0342 | 0.32588 | 0.46488 | 100 | 825 | -385.3128 | 774.6256 | infant mortality (k<1) | age_years
UNATTRIBUTED | age_years | 0.42895 | 3.2479 | -853.8789 | 0.3891 | 0.47288 | 416 | 825 | -853.8789 | 1711.7577 | infant mortality (k<1) | age_years
UNATTRIBUTED | cum_efc_x100 | 0.46666 | 7.7853 | -1358.3711 | 0.42412 | 0.51347 | 416 | 825 | -1092.8421 | 2189.6842 | infant mortality (k<1) | age_years

## rate_model_dispersion
signature | plant_years | events | var_mean_ratio | poisson_pearson_disp | nb_alpha | phi | lr_nb_vs_poisson | model_used
FULL_OUTAGE | 2192 | 284 | 1.1048 | 0.97407 | 3.7824e-06 | inf | -0.00020649 | poisson (alpha~0)
PARTIAL_AVAILABILITY | 2192 | 287 | 0.93362 | 0.84607 | 7.6814e-06 | inf | -0.00086351 | poisson (alpha~0)
THERMAL_AUX | 2192 | 102 | 1.1789 | 0.41412 | 1.0415 | 0.96019 |  | negative binomial
UNATTRIBUTED | 2192 | 453 | 1.2572 | 0.45993 | 0.00011872 | inf |  | poisson (alpha~0)

## rate_FULL_OUTAGE
term | coef | se | rate_ratio | p
Intercept | -21.0382 | 3107.5043 | 7.2985e-10 | 0.9946
C(dur_band)[T.2.5-4.5h] | -0.66153 | 0.17594 | 0.51606 | 0.00016987
C(dur_band)[T.<1.5h] | 0.09012 | 0.16186 | 1.0943 | 0.57769
C(dur_band)[T.>4.5h] | -0.59404 | 0.28307 | 0.55209 | 0.035857
C(chem_g)[T.other] | 0.671 | 0.28217 | 1.9562 | 0.017406
C(enclosure_g)[T.CS] | -0.42471 | 0.22959 | 0.65396 | 0.064329
C(enclosure_g)[T.CT] | -0.53342 | 0.29658 | 0.5866 | 0.07209
C(enclosure_g)[T.other] | -0.76649 | 0.63211 | 0.46464 | 0.22529
C(ba_g)[T.CISO] | 16.9474 | 3107.5043 | 22918367.5226 | 0.99565
C(ba_g)[T.CPLE] | 16.1003 | 3107.5043 | 9824038.8259 | 0.99587
C(ba_g)[T.ERCO] | 16.2042 | 3107.5043 | 10899228.4604 | 0.99584
C(ba_g)[T.ISNE] | 16.4292 | 3107.5043 | 13648904.0024 | 0.99578
C(ba_g)[T.MISO] | 16.9292 | 3107.5043 | 22502811.9121 | 0.99565
C(ba_g)[T.NYIS] | 17.7053 | 3107.5043 | 48899812.9617 | 0.99545
C(ba_g)[T.PJM] | 16.8394 | 3107.5043 | 20571787.9414 | 0.99568
C(ba_g)[T.other] | 16.4903 | 3107.5043 | 14509229.2772 | 0.99577
C(climate_region)[T.coastal] | 0.51733 | 0.22845 | 1.6775 | 0.023543
C(climate_region)[T.industrial] | -0.04309 | 0.45933 | 0.95783 | 0.92526
C(climate_region)[T.inland] | 0.33365 | 0.22771 | 1.396 | 0.14287
C(vintage_g)[T.2022-23] | -0.3137 | 0.19163 | 0.73074 | 0.10163
C(vintage_g)[T.2024+] | 0.31003 | 0.26789 | 1.3635 | 0.24715
C(vintage_g)[T.<=2019] | 0.0032891 | 0.18455 | 1.0033 | 0.98578
log_age | 0.37083 | 0.17511 | 1.4489 | 0.034198
log_cefc | -0.33071 | 0.077244 | 0.71841 | 1.857e-05
arb | -0.45126 | 0.17488 | 0.63683 | 0.0098707
freq | -0.47361 | 0.18053 | 0.62275 | 0.0087046
hybrid | 0.60945 | 0.1528 | 1.8394 | 6.6471e-05

## rate_PARTIAL_AVAILABILITY
term | coef | se | rate_ratio | p
Intercept | -4.9065 |  | 0.0073982
C(dur_band)[T.2.5-4.5h] | 0.21709 |  | 1.2425
C(dur_band)[T.<1.5h] | -0.44785 |  | 0.639
C(dur_band)[T.>4.5h] | 0.061706 |  | 1.0636
C(chem_g)[T.other] | -0.95783 |  | 0.38372
C(enclosure_g)[T.CS] | 0.46188 |  | 1.5871
C(enclosure_g)[T.CT] | 0.49763 |  | 1.6448
C(enclosure_g)[T.other] | 0.24563 |  | 1.2784
C(ba_g)[T.CISO] | -0.70194 |  | 0.49562
C(ba_g)[T.CPLE] | -1.5371 |  | 0.21501
C(ba_g)[T.ERCO] | -0.754 |  | 0.47048
C(ba_g)[T.ISNE] | -1.1988 |  | 0.30155
C(ba_g)[T.MISO] | -0.70538 |  | 0.49392
C(ba_g)[T.NYIS] | -1.6802 |  | 0.18634
C(ba_g)[T.PJM] | -1.4762 |  | 0.2285
C(ba_g)[T.other] | -0.45775 |  | 0.63271
C(climate_region)[T.coastal] | 0.25429 |  | 1.2895
C(climate_region)[T.industrial] | 0.61056 |  | 1.8415
C(climate_region)[T.inland] | 0.22487 |  | 1.2522
C(vintage_g)[T.2022-23] | 0.12255 |  | 1.1304
C(vintage_g)[T.2024+] | -0.3957 |  | 0.67321
C(vintage_g)[T.<=2019] | -0.11788 |  | 0.8888
log_age | -0.17264 |  | 0.84144
log_cefc | 0.48457 |  | 1.6235
arb | 0.022871 |  | 1.0231
freq | 0.18673 |  | 1.2053
hybrid | 0.10053 |  | 1.1058

## rate_THERMAL_AUX
term | coef | se | rate_ratio | p
Intercept | -18.7635 | 3913.317 | 7.098e-09 | 0.99617
C(dur_band)[T.2.5-4.5h] | 0.42149 | 0.37401 | 1.5242 | 0.25976
C(dur_band)[T.<1.5h] | -0.28284 | 0.32836 | 0.75364 | 0.38902
C(dur_band)[T.>4.5h] | 0.7112 | 0.84314 | 2.0364 | 0.39894
C(chem_g)[T.other] | -0.74226 | 1.0737 | 0.47604 | 0.48937
C(enclosure_g)[T.CS] | 0.23154 | 0.54142 | 1.2605 | 0.6689
C(enclosure_g)[T.CT] | -19.1228 | 8234.049 | 4.9553e-09 | 0.99815
C(enclosure_g)[T.other] | -17.1197 | 8698.8668 | 3.6727e-08 | 0.99843
C(ba_g)[T.CISO] | 15.7122 | 3913.317 | 6663757.7318 | 0.9968
C(ba_g)[T.CPLE] | -3.4814 | 14246.6835 | 0.030765 | 0.99981
C(ba_g)[T.ERCO] | 16.0186 | 3913.317 | 9052634.1221 | 0.99673
C(ba_g)[T.ISNE] | 15.3823 | 3913.317 | 4791007.3558 | 0.99686
C(ba_g)[T.MISO] | 16.5086 | 3913.317 | 14777545.7033 | 0.99663
C(ba_g)[T.NYIS] | -3.5818 | 13312.7436 | 0.027825 | 0.99979
C(ba_g)[T.PJM] | 15.8214 | 3913.317 | 7432495.9036 | 0.99677
C(ba_g)[T.other] | 16.42 | 3913.317 | 13524110.8409 | 0.99665
C(climate_region)[T.coastal] | -0.23492 | 0.33368 | 0.79063 | 0.48141
C(climate_region)[T.industrial] | 2.0212 | 0.79416 | 7.5476 | 0.010925
C(climate_region)[T.inland] | 0.083269 | 0.32356 | 1.0868 | 0.79691
C(vintage_g)[T.2022-23] | -0.61369 | 0.30025 | 0.54135 | 0.040962
C(vintage_g)[T.2024+] | -2.605 | 0.45498 | 0.073902 | 1.0309e-08
C(vintage_g)[T.<=2019] | -0.97223 | 0.38954 | 0.37824 | 0.012566
log_age | -1.3438 | 0.33022 | 0.26085 | 4.7121e-05
log_cefc | 0.23656 | 0.19203 | 1.2669 | 0.218
arb | -0.8131 | 0.32501 | 0.44348 | 0.012357
freq | 0.28427 | 0.25902 | 1.3288 | 0.27243
hybrid | -23.1309 | 7892.019 | 9.0032e-11 | 0.99766

## rate_UNATTRIBUTED
term | coef | se | rate_ratio | p
Intercept | -2.6547 | 0.65181 | 0.070323 | 4.6466e-05
C(dur_band)[T.2.5-4.5h] | -0.013521 | 0.16679 | 0.98657 | 0.93539
C(dur_band)[T.<1.5h] | -0.11502 | 0.13862 | 0.89135 | 0.40669
C(dur_band)[T.>4.5h] | -0.35024 | 0.33377 | 0.70452 | 0.29402
C(chem_g)[T.other] | 0.18443 | 0.28755 | 1.2025 | 0.52127
C(enclosure_g)[T.CS] | -0.74284 | 0.17381 | 0.47576 | 1.9212e-05
C(enclosure_g)[T.CT] | -0.89956 | 0.37546 | 0.40675 | 0.016581
C(enclosure_g)[T.other] | -2.0698 | 1.0267 | 0.12621 | 0.0438
C(ba_g)[T.CISO] | 0.063368 | 0.59549 | 1.0654 | 0.91525
C(ba_g)[T.CPLE] | 0.28778 | 0.6431 | 1.3335 | 0.65452
C(ba_g)[T.ERCO] | 0.26384 | 0.59916 | 1.3019 | 0.65969
C(ba_g)[T.ISNE] | 0.23402 | 0.61776 | 1.2637 | 0.70481
C(ba_g)[T.MISO] | 0.51345 | 0.66411 | 1.671 | 0.43944
C(ba_g)[T.NYIS] | -0.21627 | 0.67811 | 0.80551 | 0.74978
C(ba_g)[T.PJM] | -0.64234 | 0.65168 | 0.52606 | 0.3243
C(ba_g)[T.other] | -0.16864 | 0.605 | 0.84482 | 0.78044
C(climate_region)[T.coastal] | 0.042951 | 0.14351 | 1.0439 | 0.76472
C(climate_region)[T.industrial] | 0.26761 | 0.5287 | 1.3068 | 0.61274
C(climate_region)[T.inland] | -0.059696 | 0.13072 | 0.94205 | 0.64791
C(vintage_g)[T.2022-23] | 0.28877 | 0.17349 | 1.3348 | 0.096013
C(vintage_g)[T.2024+] | 0.4279 | 0.20617 | 1.534 | 0.037943
C(vintage_g)[T.<=2019] | 0.3253 | 0.19058 | 1.3844 | 0.087841
log_age | -0.43795 | 0.14395 | 0.64536 | 0.0023472
log_cefc | 0.14231 | 0.074268 | 1.1529 | 0.055349
arb | 0.10953 | 0.13285 | 1.1157 | 0.4097
freq | 0.17334 | 0.11344 | 1.1893 | 0.12652
hybrid | -23.9834 | 7589.373 | 3.8382e-11 | 0.99748

## backtest
signature | n | share_new_sites | event_rate | AUC | calibration_slope | pearson_chi2_df | brier | brier_fleet_mean | beats_baseline | pass
FULL_OUTAGE | 1899 | 0.40232 | 0.12112 | 0.63149 | 0.64596 | 3.8799 | 0.10606 | 0.10669 | TRUE | FALSE
PARTIAL_AVAILABILITY | 1899 | 0.40232 | 0.12322 | 0.60517 | 0.48474 | 11.2558 | 0.10907 | 0.10627 | FALSE | FALSE
THERMAL_AUX | 1899 | 0.40232 | 0.043707 | 0.73829 | 0.82552 | 3.9299 | 0.037994 | 0.041939 | TRUE | FALSE
UNATTRIBUTED | 1899 | 0.40232 | 0.16904 | 0.61069 | 0.4118 | 6.239 | 0.14468 | 0.1439 | FALSE | FALSE

## risk_by_signature
plant_id | K_own | E_own | dur_band | chem | enclosure | ba | cod_year | hybrid | nameplate_mw | e_rated_mwh | Arbitrage | Frequency Regulation | climate_region | ba_g | chem_g | enclosure_g | vintage_g | arb | freq | lam_pool | pool_level | Z | lam_hat | typical_monthly_discharge_mwh | signature | phi | P12 | L_bar_months | delta_bar | EAL_MWh | hazard_axis | hazard_shape
141 | 0 | 52 | 2.5-4.5h | LIB | CS | SRP | 2021 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 1432 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 821.0995 | age_years | wear-out (k>1)
260 | 0 | 55 | 2.5-4.5h | LIB | BL | CISO | 2021.9333 | 1 | 750 | 3000 | Y | N | coastal | CISO | LIB | BL | 2022-23 | 1 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 0 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
389 | 0 | 84 | <1.5h | LIB | BL | IID | 2016 | 0 | 30 | 20 | N | Y | arid | other | LIB | BL | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 379.5 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 391.4498 | age_years | wear-out (k>1)
645 | 2 | 33 | 1.5-2.5h | LIB | CS | TEC | 2017 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 5 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 9.9721 | age_years | wear-out (k>1)
1016 | 0 | 48 | <1.5h | LIB | CS | CPLE | 2019 | 1 | 0.5 | 0.5 | N | N | inland | CPLE | LIB | CS | <=2019 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 20.5 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 18.2448 | age_years | wear-out (k>1)
1482 | 0 | 33 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 585 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 667.8887 | age_years | wear-out (k>1)
1507 | 1 | 84 | <1.5h | LIB | CS | ISNE | 2016 | 0 | 16.7 | 10.9 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.013158 | ba_g+dur_band+vintage_g | 0 | 0.013158 | 288 | FULL_OUTAGE | inf | 0.14606 | 6.1162 | 1 | 278.126 | age_years | wear-out (k>1)
1615 | 3 | 36 | >4.5h | LIB | BL | ISNE | 2019 | 0 | 6 | 48 | N | N | coastal | ISNE | LIB | BL | <=2019 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 1 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 0.88963 | age_years | wear-out (k>1)
1682 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 3 | 6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 27.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 26.1368 | age_years | wear-out (k>1)
2324 | 0 | 23 | <1.5h | LIB | CS | NEVP | 2023 | 0 | 220 | 220 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 13845.5 | FULL_OUTAGE | inf | 0.20148 | 6.1162 | 1 | 19053.4068 | age_years | wear-out (k>1)
2830 | 1 | 84 | <1.5h | LIB | CS | PJM | 2015 | 1 | 4 | 1.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 91.5 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 64.0134 | age_years | wear-out (k>1)
6304 | 1 | 36 | <1.5h | LIB | CT |  | 2015 | 1 | 1.2 | 1 | N | N | coastal | other | LIB | CT | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 4 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 4.126 | age_years | wear-out (k>1)
6377 | 0 | 36 | <1.5h | LIB | CS | PJM | 2017 | 1 | 1 | 1 | Y | N | coastal | PJM | LIB | CS | <=2019 | 1 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 3 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 2.0988 | age_years | wear-out (k>1)
8063 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 269.1 | 263 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 2501.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 163.6328 | age_years | wear-out (k>1)
10156 | 0 | 34 | <1.5h | LIB | CS | CISO | 2023 | 0 | 16 | 16 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 13.5 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 12.2703 | age_years | wear-out (k>1)
10444 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 69 | 69 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 4203 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 4935.6243 | age_years | wear-out (k>1)
10493 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 613.5 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 700.4269 | age_years | wear-out (k>1)
50064 | 2 | 24 | <1.5h | LIB | CS | CISO | 2022 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 12 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 10.9069 | age_years | wear-out (k>1)
50300 | 0 | 84 | <1.5h | LIB | BL | CISO | 2019.5 | 0 | 40 | 40 | N | Y | inland | CISO | LIB | BL | <=2019 | 0 | 1 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 1235.5 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 1099.5805 | age_years | wear-out (k>1)
54134 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 0 | 20 | 20 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 729.5 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 202.8075 | age_years | wear-out (k>1)
54296 | 2 | 76 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.3 | 0.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 1 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 1.9703 | age_years | wear-out (k>1)
54639 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 14 | 14 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 751.5 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 557.13 | age_years | wear-out (k>1)
55370 | 0 | 36 | <1.5h | LIB | CT | PJM | 2016 | 0 | 10.4 | 10.4 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 0 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
56961 | 0 | 84 | <1.5h | LIB | BL | ERCO | 2012 | 0 | 36 | 13.6 | N | N | arid | ERCO | LIB | BL | <=2019 | 0 | 0 | 0.0097087 | ba_g+dur_band+vintage_g | 0 | 0.0097087 | 227.5 | FULL_OUTAGE | inf | 0.10997 | 6.1162 | 1 | 162.1089 | age_years | wear-out (k>1)
56981 | 0 | 84 | <1.5h | LIB | CS | ERCO | 2018 | 1 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.0097087 | ba_g+dur_band+vintage_g | 0 | 0.0097087 | 43.5 | FULL_OUTAGE | inf | 0.10997 | 6.1162 | 1 | 30.9966 | age_years | wear-out (k>1)
56984 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2018 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.0097087 | ba_g+dur_band+vintage_g | 0 | 0.0097087 | 68 | FULL_OUTAGE | inf | 0.10997 | 6.1162 | 1 | 48.4545 | age_years | wear-out (k>1)
57206 | 0 | 36 | 1.5-2.5h | LIB | CS |  | 2022 | 0 | 46.5 | 93 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0057143 | ba_g+dur_band+vintage_g | 0 | 0.0057143 | 268.5 | FULL_OUTAGE | inf | 0.066273 | 6.1162 | 1 | 112.6079 | age_years | wear-out (k>1)
57242 | 0 | 30 | 2.5-4.5h | LIB | CS |  | 2022 | 1 | 39 | 156 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3159 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 23.1853 | age_years | wear-out (k>1)
57325 | 1 | 84 | <1.5h | LIB | CS | PJM | 2014 | 1 | 20 | 8.3 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 446 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 312.0215 | age_years | wear-out (k>1)
57447 | 0 | 78 | <1.5h | LIB | CS | PJM | 2011 | 0 | 16 | 16 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 628.5 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 439.6984 | age_years | wear-out (k>1)
57560 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 19 | 76 | Y | N | arid | AZPS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1891 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 13.8789 | age_years | wear-out (k>1)
57561 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1278.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 9.3835 | age_years | wear-out (k>1)
57562 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1289 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 9.4605 | age_years | wear-out (k>1)
57563 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 16 | 48 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1141 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 8.3743 | age_years | wear-out (k>1)
57583 | 0 | 84 | <1.5h | NIB | BL |  | 2003 | 0 | 40 | 11 | N | Y | inland | other | other | BL | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 17 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 17.5353 | age_years | wear-out (k>1)
57584 | 1 | 78 | 1.5-2.5h | LIB | CS | CISO | 2015 | 0 | 2.5 | 5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 13.5 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 26.5993 | age_years | wear-out (k>1)
57996 | 0 | 36 | <1.5h | LIB | CS |  | 2012 | 0 | 11 | 4.4 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 106.5 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 109.8535 | age_years | wear-out (k>1)
57997 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 35 | 105 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2396 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 17.5853 | age_years | wear-out (k>1)
58236 | 2 | 62 | 1.5-2.5h | LIB | CS | MISO | 2020 | 1 | 0.3 | 0.6 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
58256 | 0 | 41 | >4.5h | NAB | CS | PNM | 2012 | 1 | 1.8 | 8.3 | N | N | inland | other | other | CS | <=2019 | 0 | 0 | 0.025862 | dur_band+climate_region | 0 | 0.025862 |  | FULL_OUTAGE | inf | 0.26681 | 6.1162 | 1 |  | age_years | wear-out (k>1)
58383 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 14 | 42 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1015.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 7.4532 | age_years | wear-out (k>1)
58405 | 0 | 36 | <1.5h | LIB | CS |  | 2012 | 1 | 3 | 3 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 0.5 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 0.51574 | age_years | wear-out (k>1)
58462 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 230 | 920 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 23132.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 11914.3521 | age_years | wear-out (k>1)
58585 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2017 | 1 | 0.5 | 1 | N | N | industrial | CISO | LIB | CS | <=2019 | 0 | 0 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 2 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 3.9406 | age_years | wear-out (k>1)
58639 | 0 | 48 | <1.5h | LIB | CS |  | 2015 | 1 | 6 | 4.6 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 |  | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 |  | age_years | wear-out (k>1)
59020 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 32 | 96 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2334.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 17.1339 | age_years | wear-out (k>1)
59118 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 16.4 | 32.8 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 548.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 76.244 | age_years | wear-out (k>1)
59150 | 0 | 36 | <1.5h | LIB | CS | CISO | 2021 | 1 | 75 | 75 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 7373 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 16234.0999 | age_years | wear-out (k>1)
59256 | 1 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 2 | 14 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 |  | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 |  | age_years | wear-out (k>1)
59257 | 0 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 4 | 28 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 |  | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 |  | age_years | wear-out (k>1)
59444 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 10 | 30 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 840.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 6.1688 | age_years | wear-out (k>1)
59871 | 0 | 13 | <1.5h | LIB | CS | CISO | 2024 | 1 | 150 | 150 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 12527 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 14710.5796 | age_years | wear-out (k>1)
59939 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021.4861 | 1 | 72 | 288 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 6176.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 3181.1951 | age_years | wear-out (k>1)
59949 | 0 | 70 | <1.5h | LIB | BL | PJM | 2015 | 0 | 11 | 5 | N | N | inland | PJM | LIB | BL | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 |  | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 |  | age_years | wear-out (k>1)
59957 | 0 | 84 | <1.5h | LIB | CT | PJM | 2014.75 | 1 | 36 | 13.5 | Y | Y | inland | PJM | LIB | CT | <=2019 | 1 | 1 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 0 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
59959 | 0 | 34 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 |  | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 |  | age_years | wear-out (k>1)
59960 | 0 | 30 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 |  | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 |  | age_years | wear-out (k>1)
59993 | 1 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 10 | 40 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 13 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 3.9755 | age_years | wear-out (k>1)
60014 | 0 | 48 | 1.5-2.5h | LIB | CS | FPL | 2021 | 1 | 409 | 900 | N | Y | coastal | other | LIB | CS | 2020-21 | 0 | 1 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 6521 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 10635.6592 | age_years | wear-out (k>1)
60016 | 1 | 74 | <1.5h | LIB | CS | BPAT | 2015.5 | 0 | 2 | 1 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 0 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60061 | 0 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 4 | 16 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 110.5 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 33.792 | age_years | wear-out (k>1)
60092 | 0 | 57 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 12058.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 88.5026 | age_years | wear-out (k>1)
60093 | 0 | 36 | >4.5h | LIB | CS | CISO | 2021 | 1 | 63 | 301.2 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 7022 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 51.5375 | age_years | wear-out (k>1)
60094 | 0 | 51 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 11924 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 87.5154 | age_years | wear-out (k>1)
60095 | 0 | 36 | <1.5h | LIB | CS | CISO | 2022 | 1 | 47 | 47 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 4070 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 3699.2578 | age_years | wear-out (k>1)
60123 | 1 | 76 | 2.5-4.5h | LIB | CS | ERCO | 2019 | 1 | 9.9 | 42 | N | Y | arid | ERCO | LIB | CS | <=2019 | 0 | 1 | 0.0028726 | dur_band+climate_region | 0 | 0.0028726 | 29.5 | FULL_OUTAGE | inf | 0.033884 | 6.1162 | 1 | 6.2197 | age_years | wear-out (k>1)
60231 | 1 | 36 | <1.5h | LIB | CS | CISO | 2016 | 1 | 2 | 2 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.013793 | dur_band+climate_region | 0 | 0.013793 | 25 | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 | 25.3084 | age_years | wear-out (k>1)
60233 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 88 | 352 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 8494.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 4375.0768 | age_years | wear-out (k>1)
60249 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2020 | 0 | 1 | 2 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 0 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60297 | 3 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 10 | 4.1 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 75.5 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 52.8198 | age_years | wear-out (k>1)
60299 | 1 | 24 | <1.5h | LIB | CS | PJM | 2016 | 1 | 7 | 7 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 |  | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 |  | age_years | wear-out (k>1)
60316 | 0 | 24 | <1.5h | LIB | CS | PJM | 2022 | 1 | 40 | 48 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0 | 0.0092593 | 308 | FULL_OUTAGE | inf | 0.10516 | 6.1162 | 1 | 209.3099 | age_years | wear-out (k>1)
60390 | 0 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 31.5 | 12.5 | N | Y | inland | PJM | LIB | CT | <=2019 | 0 | 1 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 0 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60441 | 0 | 67 | <1.5h | LIB | BL | PGE | 2013 | 1 | 5 | 5 | N | N | inland | other | LIB | BL | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 |  | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 |  | age_years | wear-out (k>1)
60444 | 1 | 36 | 1.5-2.5h | LIB | CT | PSEI | 2016 | 0 | 2 | 4.4 | Y | Y | inland | other | LIB | CT | <=2019 | 1 | 1 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 0 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60467 | 0 | 14 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 41 | 164 | Y | N | arid | AZPS | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3200.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 23.4899 | age_years | wear-out (k>1)
60491 | 1 | 64 | <1.5h | LIB | CT | LDWP | 2019 | 1 | 1.5 | 1.5 | N | Y | arid | other | LIB | CT | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 0 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60506 | 3 | 48 | <1.5h | NAB | BL | ERCO | 2010 | 1 | 4 | 4 | N | N | arid | ERCO | other | BL | <=2019 | 0 | 0 | 0.0097087 | ba_g+dur_band+vintage_g | 0 | 0.0097087 |  | FULL_OUTAGE | inf | 0.10997 | 6.1162 | 1 |  | age_years | wear-out (k>1)
60518 | 1 | 72 | 1.5-2.5h | LIB | CS | ISNE | 2015 | 1 | 2 | 3.4 | N | Y | inland | ISNE | LIB | CS | <=2019 | 0 | 1 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 0 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60546 | 0 | 36 | 2.5-4.5h | LIB | CS |  | 2017 | 1 | 13 | 52 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 1150.5 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 351.8342 | age_years | wear-out (k>1)
60562 | 0 | 71 | 2.5-4.5h | LIB | OT | ISNE | 2018 | 1 | 1 | 4 | N | Y | inland | ISNE | LIB | other | <=2019 | 0 | 1 | 0.005571 | ba_g+dur_band+vintage_g | 0 | 0.005571 | 52.5 | FULL_OUTAGE | inf | 0.064667 | 6.1162 | 1 | 21.4663 | age_years | wear-out (k>1)
60565 | 3 | 36 | 2.5-4.5h | LIB | CS | CISO | 2013.3333 | 1 | 1.5 | 4.5 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 0 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60566 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2015 | 1 | 1 | 2 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 1082.5 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 2132.8698 | age_years | wear-out (k>1)
60567 | 3 | 36 | 2.5-4.5h | LIB | CS | CISO | 2015 | 1 | 2 | 6 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 0 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60568 | 2 | 36 | 2.5-4.5h | LIB | CS | CISO | 2014 | 1 | 1 | 3 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 0 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60569 | 1 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 7.5 | 30 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 405 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 908.2553 | age_years | wear-out (k>1)
60570 | 2 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 0 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60607 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2017 | 1 | 0.8 | 3.3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.005571 | ba_g+dur_band+vintage_g | 0 | 0.005571 | 3.5 | FULL_OUTAGE | inf | 0.064667 | 6.1162 | 1 | 1.4311 | age_years | wear-out (k>1)
60609 | 2 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2016 | 1 | 0.8 | 3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.005571 | ba_g+dur_band+vintage_g | 0 | 0.005571 | 0 | FULL_OUTAGE | inf | 0.064667 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60641 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 10 | 40 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 758.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 390.664 | age_years | wear-out (k>1)
60649 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 165.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 55.3804 | age_years | wear-out (k>1)
60654 | 0 | 48 | 2.5-4.5h | LIB | CS | WALC | 2021 | 1 | 90 | 360 | Y | Y | arid | other | LIB | CS | 2020-21 | 1 | 1 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 7749.5 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 4443.5128 | age_years | wear-out (k>1)
60656 | 1 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 20 | 7.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 2935 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 2053.3251 | age_years | wear-out (k>1)
60660 | 0 | 33 | <1.5h | LIB | CS | PJM | 2016 | 0 | 6 | 2 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 593 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 414.8626 | age_years | wear-out (k>1)
60661 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2016 | 0 | 20 | 80 | Y | Y | arid | CISO | LIB | CS | <=2019 | 1 | 1 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 1040.5 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 2333.4312 | age_years | wear-out (k>1)
60690 | 0 | 84 | <1.5h | LIB | CS | ERCO | 2017 | 0 | 30 | 12.6 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.0097087 | ba_g+dur_band+vintage_g | 0 | 0.0097087 | 463.5 | FULL_OUTAGE | inf | 0.10997 | 6.1162 | 1 | 330.2746 | age_years | wear-out (k>1)
60698 | 1 | 65 | <1.5h | LIB | CS | CISO | 2020 | 1 | 20 | 9 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 14 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 30.8256 | age_years | wear-out (k>1)
60760 | 0 | 24 | 2.5-4.5h | LIB | BL | CISO | 2016 | 0 | 2 | 8 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 |  | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 |  | age_years | wear-out (k>1)
60815 | 1 | 36 | <1.5h | LIB | CS | ISNE | 2017 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.013158 | ba_g+dur_band+vintage_g | 0 | 0.013158 | 6.5 | FULL_OUTAGE | inf | 0.14606 | 6.1162 | 1 | 6.2771 | age_years | wear-out (k>1)
60906 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.1 | 6.1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 23 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 26.1427 | age_years | wear-out (k>1)
60959 | 2 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2017 | 1 | 2 | 3.9 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 7 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 7.9565 | age_years | wear-out (k>1)
60974 | 4 | 36 | <1.5h | LIB | CS | LDWP | 2017 | 1 | 2 | 1 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 0 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
60996 | 1 | 36 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 2.5 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 74 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 76.3301 | age_years | wear-out (k>1)
61068 | 1 | 72 | >4.5h | LIB | CS |  | 2018 | 1 | 20 | 100 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 1857 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 1652.0405 | age_years | wear-out (k>1)
61098 | 0 | 55 | <1.5h | LIB | CS | NEVP | 2021 | 1 | 25 | 25 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.014019 | ba_g+dur_band+vintage_g | 0 | 0.014019 | 2105 | FULL_OUTAGE | inf | 0.15484 | 6.1162 | 1 | 2165.8197 | age_years | wear-out (k>1)
61107 | 0 | 36 | 2.5-4.5h | FLB | CS | CISO | 2017 | 1 | 2 | 8 | N | Y | coastal | CISO | other | CS | <=2019 | 0 | 1 | 0.030556 | ba_g+dur_band+vintage_g | 0 | 0.030556 | 106 | FULL_OUTAGE | inf | 0.30696 | 6.1162 | 1 | 237.7162 | age_years | wear-out (k>1)
61168 | 0 | 14 | 2.5-4.5h | LIB | CS | LDWP | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 14026 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 7275.1193 | age_years | wear-out (k>1)
61169 | 0 | 6 | 2.5-4.5h | LIB | CS | LDWP | 2025 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 13805 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 7160.4892 | age_years | wear-out (k>1)
61186 | 0 | 32 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 1 | 1.1 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 2 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 1.4827 | age_years | wear-out (k>1)
61197 | 1 | 84 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 10 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 6 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 6.1889 | age_years | wear-out (k>1)
61204 | 0 | 60 | 2.5-4.5h | LIB | BL | CISO | 2021 | 0 | 100 | 400 | Y | N | coastal | CISO | LIB | BL | 2020-21 | 1 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 7946.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 4092.8304 | age_years | wear-out (k>1)
61334 | 4 | 36 | >4.5h | LIB | CT | MISO | 2019 | 1 | 1 | 4.6 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.025862 | dur_band+climate_region | 0 | 0.025862 | 0 | FULL_OUTAGE | inf | 0.26681 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61365 | 1 | 31 | <1.5h | LIB | CS | CISO | 2023 | 0 | 40 | 40 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 3338 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 3033.9368 | age_years | wear-out (k>1)
61366 | 0 | 54 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 2929.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 1508.8337 | age_years | wear-out (k>1)
61431 | 1 | 84 | <1.5h | LIB | CS | LDWP | 2018 | 1 | 20 | 10 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 337 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 347.6116 | age_years | wear-out (k>1)
61439 | 1 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2017 | 1 | 1 | 2.2 | Y | Y | arid | other | LIB | CS | <=2019 | 1 | 1 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 0 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61473 | 1 | 36 | <1.5h | LIB | BL | PJM | 2015 | 1 | 1 | 1 | Y | Y | inland | PJM | LIB | BL | <=2019 | 1 | 1 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 0 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61552 | 1 | 22 | <1.5h | LIB | CS | PJM | 2024 | 1 | 6 | 6 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 455 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 404.9447 | age_years | wear-out (k>1)
61661 | 0 | 84 | <1.5h | LIB | BL | CISO | 2018 | 0 | 40 | 38 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.013793 | dur_band+climate_region | 0 | 0.013793 | 1280.5 | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 | 1296.2964 | age_years | wear-out (k>1)
61667 | 0 | 9 | 1.5-2.5h | LIB | CS | TEC | 2025 | 1 | 40 | 80 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 447 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 683.485 | age_years | wear-out (k>1)
61678 | 0 | 84 | 2.5-4.5h | LIB | CS | SRP | 2018 | 1 | 10 | 40 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 1032 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 315.5958 | age_years | wear-out (k>1)
61721 | 0 | 72 | >4.5h | LIB | CS | CISO | 2019 | 1 | 1 | 6.9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 16.5 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 2.8697 | age_years | wear-out (k>1)
61722 | 0 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.5 | 33.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 455 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 79.1337 | age_years | wear-out (k>1)
61723 | 0 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.8 | 34.8 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 378 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 65.7419 | age_years | wear-out (k>1)
61730 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 1 | 1 | 2 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 19.5 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 22.1644 | age_years | wear-out (k>1)
61737 | 0 | 12 | <1.5h | LIB | CS | PJM | 2021 | 1 | 6.2 | 6.2 | N | Y | coastal | PJM | LIB | CS | 2020-21 | 0 | 1 | 0.013793 | dur_band+climate_region | 0 | 0.013793 |  | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 |  | age_years | wear-out (k>1)
61739 | 1 | 36 | <1.5h | LIB | CS | NYIS | 2017 | 0 | 1 | 1.3 | Y | N | industrial | NYIS | LIB | CS | <=2019 | 1 | 0 | 0.011716 | dur_band | 0 | 0.011716 | 0 | FULL_OUTAGE | inf | 0.13116 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61741 | 2 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2018 | 1 | 1.5 | 3 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61763 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 647.5 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 371.2723 | age_years | wear-out (k>1)
61795 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2020 | 1 | 1 | 2 | Y | N | industrial | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 2.5 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 1.5419 | age_years | wear-out (k>1)
61801 | 1 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 2194.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 711.6227 | age_years | wear-out (k>1)
61803 | 0 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 10 | 40 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 705 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 228.6143 | age_years | wear-out (k>1)
61861 | 1 | 84 | 2.5-4.5h | LIB | BL | SRP | 2019 | 1 | 10 | 40 | N | N | arid | other | LIB | BL | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 0 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61891 | 0 | 83 | <1.5h | LIB | CS | PJM | 2018 | 0 | 19.8 | 19.8 | Y | N | inland | PJM | LIB | CS | <=2019 | 1 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 2740 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 1916.9031 | age_years | wear-out (k>1)
61892 | 1 | 83 | <1.5h | LIB | CS | PJM | 2019 | 0 | 19.8 | 19.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 2919 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 2042.1315 | age_years | wear-out (k>1)
61901 | 1 | 36 | 1.5-2.5h | LIB | CS | TVA | 2017 | 1 | 1 | 2 | Y | N | inland | other | LIB | CS | <=2019 | 1 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 0 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61909 | 0 | 36 | <1.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 1 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 0 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61923 | 1 | 36 | <1.5h | LIB | CS | PJM | 2018 | 0 | 1 | 1 | N | N | coastal | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 127 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 88.8492 | age_years | wear-out (k>1)
61925 | 1 | 84 | <1.5h | LIB | CS | PNM | 2018 | 0 | 1 | 1 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 4.5 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 4.6417 | age_years | wear-out (k>1)
61956 | 0 | 36 | 1.5-2.5h | LIB | CS | SCEG | 2018 | 1 | 4 | 8 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 23 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 45.8715 | age_years | wear-out (k>1)
61990 | 1 | 36 | 1.5-2.5h | LIB | CT | MISO | 2017 | 1 | 0.3 | 0.5 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
61995 | 2 | 36 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.5 | 0.9 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 0 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62027 | 1 | 36 | 1.5-2.5h | OTH | CS | PJM | 2016 | 1 | 1 | 2 | Y | Y | coastal | PJM | other | CS | <=2019 | 1 | 1 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 0 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62147 | 1 | 36 | <1.5h | LIB | CS | NYIS | 2019 | 0 | 20 | 8.4 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 2179 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 1939.2844 | age_years | wear-out (k>1)
62175 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 200 | 800 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 17609 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 3308.1947 | age_years | wear-out (k>1)
62219 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 1 | 3 | 3 | N | N | inland | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.013158 | ba_g+dur_band+vintage_g | 0 | 0.013158 | 19.5 | FULL_OUTAGE | inf | 0.14606 | 6.1162 | 1 | 18.8314 | age_years | wear-out (k>1)
62235 | 0 | 13 | 2.5-4.5h | LIB | CS | SCEG | 2024 | 1 | 66 | 198 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1632.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 846.7583 | age_years | wear-out (k>1)
62248 | 0 | 25 | >4.5h | LIB | CS | NEVP | 2023 | 1 | 75 | 375 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 8731 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 64.0806 | age_years | wear-out (k>1)
62257 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 0 | 2 | 4.2 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 26.5 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 30.1209 | age_years | wear-out (k>1)
62373 | 0 | 84 | 2.5-4.5h | LIB | CS | WACM | 2018 | 0 | 4 | 16 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 0 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62381 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0.005571 | ba_g+dur_band+vintage_g | 0 | 0.005571 | 94 | FULL_OUTAGE | inf | 0.064667 | 6.1162 | 1 | 38.4349 | age_years | wear-out (k>1)
62382 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0.005571 | ba_g+dur_band+vintage_g | 0 | 0.005571 | 92 | FULL_OUTAGE | inf | 0.064667 | 6.1162 | 1 | 37.6172 | age_years | wear-out (k>1)
62383 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0.005571 | ba_g+dur_band+vintage_g | 0 | 0.005571 | 105.5 | FULL_OUTAGE | inf | 0.064667 | 6.1162 | 1 | 43.1371 | age_years | wear-out (k>1)
62441 | 0 | 24 | <1.5h | LIB | CS | CISO | 2020 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 48.5 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 106.7888 | age_years | wear-out (k>1)
62444 | 0 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 18 | 12.1 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 1974 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 1381.0098 | age_years | wear-out (k>1)
62490 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 558 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 319.9536 | age_years | wear-out (k>1)
62494 | 0 | 2 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 1 | 252 | 1008 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 8863.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 4597.392 | age_years | wear-out (k>1)
62497 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 9 | 36 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 0 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62499 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 6 | 24 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 0 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62541 | 1 | 34 | 1.5-2.5h | LIB | CS | FPC | 2023 | 1 | 17.3 | 36 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0057143 | ba_g+dur_band+vintage_g | 0 | 0.0057143 | 160 | FULL_OUTAGE | inf | 0.066273 | 6.1162 | 1 | 67.1034 | age_years | wear-out (k>1)
62561 | 1 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 63.3 | 108.6 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 0 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62562 | 1 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 63.3 | 81 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 0 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62564 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 182.5 | 730 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 0 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62569 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 4 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62585 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 0 | 3 | 3 | N | N | coastal | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.013158 | ba_g+dur_band+vintage_g | 0 | 0.013158 | 16.5 | FULL_OUTAGE | inf | 0.14606 | 6.1162 | 1 | 15.9343 | age_years | wear-out (k>1)
62604 | 1 | 41 | 1.5-2.5h | LIB | BL | ISNE | 2022 | 0 | 25 | 38 | N | N | coastal | ISNE | LIB | BL | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 64.5 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 73.639 | age_years | wear-out (k>1)
62609 | 1 | 76 | <1.5h | LIB | CS | ERCO | 2019 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | <=2019 | 1 | 1 | 0.0097087 | ba_g+dur_band+vintage_g | 0 | 0.0097087 | 156.5 | FULL_OUTAGE | inf | 0.10997 | 6.1162 | 1 | 111.5167 | age_years | wear-out (k>1)
62644 | 0 | 80 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 5 | 10 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 42.5 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 48.3071 | age_years | wear-out (k>1)
62652 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.3 | 6.6 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 98.5 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 111.9589 | age_years | wear-out (k>1)
62682 | 2 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 0 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62683 | 3 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 0 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62695 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 19 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 18.0582 | age_years | wear-out (k>1)
62714 | 0 | 36 | <1.5h | LIB | CS |  | 2019 | 0 | 1 | 0.9 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 11 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 11.3464 | age_years | wear-out (k>1)
62733 | 3 | 36 | >4.5h | LIB | BL | NYIS | 2018 | 0 | 5 | 40 | Y | N | coastal | NYIS | LIB | BL | <=2019 | 1 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 25 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 22.2407 | age_years | wear-out (k>1)
62734 | 2 | 36 | >4.5h | LIB | BL | NYIS | 2019 | 0 | 5 | 40 | N | N | coastal | NYIS | LIB | BL | <=2019 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 0 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62745 | 0 | 45 | 2.5-4.5h | LIB | CS | BPAT | 2022 | 1 | 30 | 120 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1836 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 13.4752 | age_years | wear-out (k>1)
62753 | 1 | 72 | <1.5h | LIB | CS | ERCO | 2020 | 1 | 9.9 | 10 | Y | Y | inland | ERCO | LIB | CS | 2020-21 | 1 | 1 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 14 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 4.6847 | age_years | wear-out (k>1)
62754 | 1 | 20 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 2 | 4 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 0 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62801 | 0 | 24 | <1.5h | LIB | CS | CISO | 2021 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 908 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 1999.2625 | age_years | wear-out (k>1)
62835 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 1.5 | 3 | N | Y | coastal | ISNE | LIB | CS | <=2019 | 0 | 1 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 6 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 6.8198 | age_years | wear-out (k>1)
62839 | 0 | 36 | >4.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 10 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 0 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62844 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 150 | 300 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 6721.5 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 7801.5851 | age_years | wear-out (k>1)
62856 | 1 | 83 | <1.5h | LIB | CS | PJM | 2018 | 1 | 20 | 20 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0095321 | ba_g+dur_band+vintage_g | 0 | 0.0095321 | 0 | FULL_OUTAGE | inf | 0.10809 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
62862 | 3 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 74 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 65.8591 | age_years | wear-out (k>1)
62874 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 2 | 6 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 83.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 43.0065 | age_years | wear-out (k>1)
62875 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 3 | 12 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 86 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 44.2941 | age_years | wear-out (k>1)
62889 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 20 | 80 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 1815.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 935.07 | age_years | wear-out (k>1)
62907 | 1 | 36 | <1.5h | LIB | CS | ISNE | 2019 | 0 | 1.9 | 1.9 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.013158 | ba_g+dur_band+vintage_g | 0 | 0.013158 | 155 | FULL_OUTAGE | inf | 0.14606 | 6.1162 | 1 | 149.6859 | age_years | wear-out (k>1)
62908 | 0 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 0 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 9.5 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 11.72 | age_years | wear-out (k>1)
62937 | 0 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 4 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 4.9347 | age_years | wear-out (k>1)
62964 | 0 | 16 | <1.5h | LIB | CS | AZPS | 2023 | 0 | 50 | 50 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.0087159 | dur_band+climate_region | 0 | 0.0087159 | 4547.5 | FULL_OUTAGE | inf | 0.099307 | 6.1162 | 1 | 2909.0141 | age_years | wear-out (k>1)
62968 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 4 | Y | N | coastal | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 53 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 60.5096 | age_years | wear-out (k>1)
62969 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 74.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 70.8071 | age_years | wear-out (k>1)
62970 | 1 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 64.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 61.3028 | age_years | wear-out (k>1)
62971 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 2.9 | 6 | Y | N | inland | ISNE | other | CT | 2022-23 | 1 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 62.5 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 71.3556 | age_years | wear-out (k>1)
62972 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2021 | 1 | 2 | 4.2 | Y | N | inland | ISNE | other | CT | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 57 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 54.1745 | age_years | wear-out (k>1)
62973 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 1.6 | 3.2 | Y | N | coastal | ISNE | other | CT | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 36.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 34.6907 | age_years | wear-out (k>1)
62974 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 3.8 | 7.9 | Y | Y | inland | ISNE | other | CT | 2022-23 | 1 | 1 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 154 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 175.8203 | age_years | wear-out (k>1)
62975 | 1 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 3.9 | 7.9 | Y | Y | inland | ISNE | other | CT | 2020-21 | 1 | 1 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 114 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 108.3491 | age_years | wear-out (k>1)
62976 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2020 | 1 | 2 | 4 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 16 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 15.2069 | age_years | wear-out (k>1)
62977 | 0 | 12 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 51.5 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 58.797 | age_years | wear-out (k>1)
62978 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3 | 6 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 65 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 61.778 | age_years | wear-out (k>1)
62981 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2018 | 0 | 2 | 4.2 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 35.5 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 43.7958 | age_years | wear-out (k>1)
62999 | 2 | 36 | <1.5h | LIB | CT | NYIS | 2020 | 1 | 3 | 4.4 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 0 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63000 | 3 | 36 | 1.5-2.5h | LIB | CT | NYIS | 2020 | 1 | 4 | 8.8 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63011 | 1 | 36 | >4.5h | LIB | CT | ISNE | 2020 | 1 | 1.5 | 7.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.025862 | dur_band+climate_region | 0 | 0.025862 | 100.5 | FULL_OUTAGE | inf | 0.26681 | 6.1162 | 1 | 190.7621 | age_years | wear-out (k>1)
63022 | 0 | 36 | 1.5-2.5h | LIB | CS | WACM | 2018 | 0 | 4.2 | 8.5 | N | N | industrial | other | LIB | CS | <=2019 | 0 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 238 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 474.6701 | age_years | wear-out (k>1)
63044 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 4.3 | 14 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 196 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 149.8468 | age_years | wear-out (k>1)
63064 | 1 | 64 | <1.5h | LIB | CS | CPLW | 2020 | 0 | 8.8 | 8.8 | Y | Y | inland | other | LIB | CS | 2020-21 | 1 | 1 | 0.014019 | ba_g+dur_band+vintage_g | 0 | 0.014019 | 31 | FULL_OUTAGE | inf | 0.15484 | 6.1162 | 1 | 31.8957 | age_years | wear-out (k>1)
63090 | 0 | 36 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 3 | 6 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 9 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 11.1031 | age_years | wear-out (k>1)
63172 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 14374.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 105.5007 | age_years | wear-out (k>1)
63186 | 2 | 36 | <1.5h | LIB | CS | JEA | 2019 | 1 | 5 | 3.8 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.014054 | ba_g+dur_band+vintage_g | 0 | 0.014054 | 0 | FULL_OUTAGE | inf | 0.15519 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63214 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3 | 6.6 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 0 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63238 | 1 | 24 | <1.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 20 | Y | N | inland | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 0 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63255 | 0 | 57 | <1.5h | LIB | BL | ERCO | 2021 | 1 | 40 | 40 | Y | Y | arid | ERCO | LIB | BL | 2020-21 | 1 | 1 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 125 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 41.8281 | age_years | wear-out (k>1)
63264 | 1 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 32 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 8.8963 | age_years | wear-out (k>1)
63280 | 0 | 36 | >4.5h | LIB | CT |  | 2021 | 1 | 14 | 70 | N | Y | coastal | other | LIB | CT | 2020-21 | 0 | 1 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 1353 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 1203.6676 | age_years | wear-out (k>1)
63324 | 3 | 36 | <1.5h | LIB | BL | MISO | 2019 | 1 | 5 | 5 | N | N | inland | MISO | LIB | BL | <=2019 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 64.5 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 57.4042 | age_years | wear-out (k>1)
63337 | 0 | 36 | <1.5h | LIB | CT | NYIS | 2022 | 1 | 3 | 3 | N | N | inland | NYIS | LIB | CT | 2022-23 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 55 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 48.9494 | age_years | wear-out (k>1)
63338 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 63 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 46.7055 | age_years | wear-out (k>1)
63339 | 1 | 17 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.04 | ba_g+dur_band+vintage_g | 0 | 0.04 | 4.5 | FULL_OUTAGE | inf | 0.38122 | 6.1162 | 1 | 13.211 | age_years | wear-out (k>1)
63340 | 0 | 33 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.025806 | ba_g+dur_band+vintage_g | 0 | 0.025806 | 49 | FULL_OUTAGE | inf | 0.26632 | 6.1162 | 1 | 92.8084 | age_years | wear-out (k>1)
63341 | 1 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.025806 | ba_g+dur_band+vintage_g | 0 | 0.025806 | 52.5 | FULL_OUTAGE | inf | 0.26632 | 6.1162 | 1 | 99.4375 | age_years | wear-out (k>1)
63352 | 0 | 21 | <1.5h | LIB | CS | NEVP | 2024 | 1 | 380 | 380 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0087159 | dur_band+climate_region | 0 | 0.0087159 | 38646 | FULL_OUTAGE | inf | 0.099307 | 6.1162 | 1 | 24721.6619 | age_years | wear-out (k>1)
63398 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 1.6 | 3.8 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 104 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 118.2104 | age_years | wear-out (k>1)
63415 | 1 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 1.6 | 6.6 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 0 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63420 | 1 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 0.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 5 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 11.0092 | age_years | wear-out (k>1)
63421 | 4 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.2 | 0.2 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 0 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63422 | 3 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.3 | 0.3 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 0 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63458 | 1 | 24 | 1.5-2.5h | FLB | CS | SWPP | 2020 | 0 | 10 | 20 | Y | N | inland | other | other | CS | 2020-21 | 1 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 376.5 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 614.0662 | age_years | wear-out (k>1)
63468 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 15 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 4.1701 | age_years | wear-out (k>1)
63469 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.5 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 42.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 40.3933 | age_years | wear-out (k>1)
63470 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.9 | 5.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 50 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 47.5215 | age_years | wear-out (k>1)
63472 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 2.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 22.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 21.3847 | age_years | wear-out (k>1)
63473 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.8 | 3.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 52 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 49.4224 | age_years | wear-out (k>1)
63474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 65 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 61.778 | age_years | wear-out (k>1)
63475 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.3 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 63 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 59.8771 | age_years | wear-out (k>1)
63486 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.5 | 0.8 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 18 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 35.4657 | age_years | wear-out (k>1)
63510 | 3 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.5 | 0.5 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 0.5 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 1.1009 | age_years | wear-out (k>1)
63522 | 0 | 43 | 1.5-2.5h | LIB | OT | SOCO | 2022 | 1 | 40 | 80 | N | N | inland | other | LIB | other | 2022-23 | 0 | 0 | 0.0057143 | ba_g+dur_band+vintage_g | 0 | 0.0057143 | 1540.5 | FULL_OUTAGE | inf | 0.066273 | 6.1162 | 1 | 646.0801 | age_years | wear-out (k>1)
63535 | 0 | 36 | 2.5-4.5h | LIB | BL | SOCO | 2020 | 1 | 1 | 4 | Y | N | inland | other | LIB | BL | 2020-21 | 1 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 93 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 53.3256 | age_years | wear-out (k>1)
63585 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 3 | 12 | Y | N | coastal | NYIS | LIB | CS | 2020-21 | 1 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 98 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 221.3122 | age_years | wear-out (k>1)
63609 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 91 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 15.8267 | age_years | wear-out (k>1)
63610 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.2 | 6.3 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 73 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 12.6962 | age_years | wear-out (k>1)
63611 | 0 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 2.5 | 15 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 218 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 37.9146 | age_years | wear-out (k>1)
63612 | 0 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 1 | 6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 35 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 6.0872 | age_years | wear-out (k>1)
63613 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 2 | 13 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 66 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 11.4787 | age_years | wear-out (k>1)
63614 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1 | 5 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 59 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 10.2613 | age_years | wear-out (k>1)
63615 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 8.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 182 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 31.6535 | age_years | wear-out (k>1)
63616 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 4.9 | 32.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 326 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 56.698 | age_years | wear-out (k>1)
63617 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.3 | 7.2 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.0023697 | ba_g+dur_band+vintage_g | 0 | 0.0023697 | 146 | FULL_OUTAGE | inf | 0.028036 | 6.1162 | 1 | 25.3924 | age_years | wear-out (k>1)
63685 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 100 | 400 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 9551.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1794.4359 | age_years | wear-out (k>1)
63721 | 0 | 49 | 1.5-2.5h | LIB | CS | SOCO | 2021 | 1 | 40 | 80 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 2340.5 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 3817.3225 | age_years | wear-out (k>1)
63722 | 2 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2021 | 1 | 1 | 2 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 37.5 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 61.162 | age_years | wear-out (k>1)
63723 | 0 | 6 | 2.5-4.5h | LIB | CS | HECO | 2025 | 1 | 52 | 208 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 4320.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 2240.9919 | age_years | wear-out (k>1)
63727 | 1 | 47 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 140.3 | 561 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 15233 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2861.8167 | age_years | wear-out (k>1)
63728 | 0 | 38 | 1.5-2.5h | LIB | CS | PNM | 2022 | 1 | 12.5 | 25 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0057143 | ba_g+dur_band+vintage_g | 0 | 0.0057143 | 540.5 | FULL_OUTAGE | inf | 0.066273 | 6.1162 | 1 | 226.6837 | age_years | wear-out (k>1)
63731 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 125 | 500 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6763.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 49.6403 | age_years | wear-out (k>1)
63735 | 1 | 23 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 11 | 44 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 1053.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 542.6033 | age_years | wear-out (k>1)
63737 | 1 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 125 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 3352 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 1121.6622 | age_years | wear-out (k>1)
63757 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 6598 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 431.6007 | age_years | wear-out (k>1)
63763 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 5.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 30.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 28.9881 | age_years | wear-out (k>1)
63774 | 1 | 9 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 0.7 | 2.1 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 5 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 11.2914 | age_years | wear-out (k>1)
63775 | 1 | 36 | 1.5-2.5h | LIB | BL | SOCO | 2020 | 0 | 0.2 | 0.4 | N | N | inland | other | LIB | BL | 2020-21 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 0 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
63776 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6764.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 49.6476 | age_years | wear-out (k>1)
63804 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2 | 3.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 17.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 16.6325 | age_years | wear-out (k>1)
63805 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 44 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 41.8189 | age_years | wear-out (k>1)
63834 | 1 | 66 | 2.5-4.5h | LIB | BL | CISO | 2020 | 0 | 250 | 1000 | N | N | coastal | CISO | LIB | BL | 2020-21 | 0 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 12078.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 6221.0095 | age_years | wear-out (k>1)
63843 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021.75 | 1 | 80 | 320 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 7844 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1473.6487 | age_years | wear-out (k>1)
63848 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 225 | 900 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 26478.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 4974.5036 | age_years | wear-out (k>1)
63849 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 135 | 540 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 16258.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 3054.4769 | age_years | wear-out (k>1)
63859 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 1 | 147 | 147 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 13900.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 16323.4942 | age_years | wear-out (k>1)
63891 | 0 | 57 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 9420.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 4852.0114 | age_years | wear-out (k>1)
63892 | 0 | 52 | <1.5h | LIB | CS | ERCO | 2021 | 1 | 55.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 1015.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 339.8115 | age_years | wear-out (k>1)
63900 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 1 | 30 | 120 | N | Y | coastal | other | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3080 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 22.6055 | age_years | wear-out (k>1)
63905 | 0 | 43 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 91.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 2243 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 146.7233 | age_years | wear-out (k>1)
63913 | 0 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 5017.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 36.8256 | age_years | wear-out (k>1)
63930 | 0 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 60 | 242 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 5428.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 2795.9391 | age_years | wear-out (k>1)
63933 | 0 | 20 | 1.5-2.5h | LIB | CS | NEVP | 2024 | 1 | 100 | 150 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 10988.5 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 16801.9582 | age_years | wear-out (k>1)
63943 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 60 | 240 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 6549 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1230.3576 | age_years | wear-out (k>1)
63995 | 1 | 23 | <1.5h | LIB | CS | FPC | 2021 | 0 | 11 | 10.1 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.014019 | ba_g+dur_band+vintage_g | 0 | 0.014019 | 5 | FULL_OUTAGE | inf | 0.15484 | 6.1162 | 1 | 5.1445 | age_years | wear-out (k>1)
63996 | 0 | 24 | 2.5-4.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 14.3 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 39 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 0.28624 | age_years | wear-out (k>1)
63998 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 5.5 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 11 | FULL_OUTAGE | inf | 0.20148 | 6.1162 | 1 | 15.1376 | age_years | wear-out (k>1)
63999 | 1 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 8.3 | 11.7 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 18 | FULL_OUTAGE | inf | 0.20148 | 6.1162 | 1 | 24.7706 | age_years | wear-out (k>1)
64000 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.2 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 48 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 45.6207 | age_years | wear-out (k>1)
64050 | 2 | 35 | <1.5h | LIB | CS | CPLE | 2023 | 1 | 2 | 2 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 0 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64084 | 1 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64087 | 1 | 22 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64089 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 6631.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 433.7921 | age_years | wear-out (k>1)
64090 | 1 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64092 | 1 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64103 | 0 | 58 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 35 | 140 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 1919.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 988.635 | age_years | wear-out (k>1)
64105 | 1 | 43 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 50 | 200 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 3994.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 750.4449 | age_years | wear-out (k>1)
64128 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 2 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 1.9009 | age_years | wear-out (k>1)
64129 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.1 | 6.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 108.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 103.1217 | age_years | wear-out (k>1)
64140 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 1.4 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 13.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 12.8308 | age_years | wear-out (k>1)
64147 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 50 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 47.5215 | age_years | wear-out (k>1)
64148 | 0 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2345 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 17.211 | age_years | wear-out (k>1)
64164 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 120 | 190 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 4966.5 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 982.5151 | age_years | wear-out (k>1)
64170 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.9 | 1.8 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 14.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 13.7812 | age_years | wear-out (k>1)
64182 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.7 | 9 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 84.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 80.3114 | age_years | wear-out (k>1)
64185 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 1.9 | 3.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 50 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 47.5215 | age_years | wear-out (k>1)
64187 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 2.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 15.5 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 11.8501 | age_years | wear-out (k>1)
64197 | 0 | 28 | <1.5h | LIB | CS | CISO | 2023 | 1 | 137 | 137 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 13407 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 12185.7371 | age_years | wear-out (k>1)
64198 | 0 | 36 | 2.5-4.5h | LIB | CS | BPAT | 2020 | 1 | 1 | 4 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 87.5 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 50.1719 | age_years | wear-out (k>1)
64202 | 0 | 12 |  |  |  | ERCO |  | 1 |  |  |  |  | inland | ERCO | other | other | 2020-21 | 0 | 0 | 0.012047 | fleet | 0 | 0.012047 | 1901.5 | FULL_OUTAGE | inf | 0.1346 | 6.1162 | 1 | 1681.2957 | age_years | wear-out (k>1)
64207 | 1 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 80.5 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 71.6441 | age_years | wear-out (k>1)
64213 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 9.4 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 64 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 73.0682 | age_years | wear-out (k>1)
64222 | 0 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 10 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 5.7339 | age_years | wear-out (k>1)
64223 | 1 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 8.5 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 4.8738 | age_years | wear-out (k>1)
64231 | 0 | 12 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 1 | 1 | 4.4 | N | N | inland | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.011494 | ba_g+dur_band+vintage_g | 0 | 0.011494 | 32.5 | FULL_OUTAGE | inf | 0.12884 | 6.1162 | 1 | 27.4174 | age_years | wear-out (k>1)
64256 | 0 | 17 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 60 | 240 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5987.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 3105.645 | age_years | wear-out (k>1)
64293 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 449.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 150.4138 | age_years | wear-out (k>1)
64294 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 437 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 146.231 | age_years | wear-out (k>1)
64295 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 473 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 158.2775 | age_years | wear-out (k>1)
64296 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 432 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 144.5579 | age_years | wear-out (k>1)
64297 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 486.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 162.795 | age_years | wear-out (k>1)
64298 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 399.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 133.6826 | age_years | wear-out (k>1)
64312 | 0 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 2925 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 978.7775 | age_years | wear-out (k>1)
64314 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 423.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 141.7136 | age_years | wear-out (k>1)
64315 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 458 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 153.2581 | age_years | wear-out (k>1)
64316 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 445 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 29.1092 | age_years | wear-out (k>1)
64317 | 0 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 2799 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 936.6147 | age_years | wear-out (k>1)
64318 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 804 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 52.5928 | age_years | wear-out (k>1)
64319 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 473.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 158.4448 | age_years | wear-out (k>1)
64321 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 407.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 136.3596 | age_years | wear-out (k>1)
64322 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 874.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 57.2044 | age_years | wear-out (k>1)
64374 | 2 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 0 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64375 | 0 | 24 | <1.5h | LIB | CS | MISO | 2021 | 0 | 2.5 | 2.9 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 0 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64395 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2.5 | 5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 39.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 37.542 | age_years | wear-out (k>1)
64400 | 1 | 36 | <1.5h | LIB | CS | HECO | 2021 | 1 | 1.9 | 1.9 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0.014019 | ba_g+dur_band+vintage_g | 0 | 0.014019 | 104 | FULL_OUTAGE | inf | 0.15484 | 6.1162 | 1 | 107.0049 | age_years | wear-out (k>1)
64423 | 2 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 16.5 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 203 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 133.6238 | age_years | wear-out (k>1)
64424 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 17.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 12.5 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 8.2281 | age_years | wear-out (k>1)
64425 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 11.9 | N | N | coastal | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 5.5 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 1.8404 | age_years | wear-out (k>1)
64426 | 1 | 56 | 1.5-2.5h | LIB | CS | TEPC | 2021 | 1 | 30 | 60 | N | Y | arid | other | LIB | CS | 2020-21 | 0 | 1 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 1502 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 2449.7408 | age_years | wear-out (k>1)
64432 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.2 | 4.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 13 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 12.3556 | age_years | wear-out (k>1)
64436 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 8 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 7.6034 | age_years | wear-out (k>1)
64442 | 0 | 10 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 0.7 | 3 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.025806 | ba_g+dur_band+vintage_g | 0 | 0.025806 | 9 | FULL_OUTAGE | inf | 0.26632 | 6.1162 | 1 | 17.0464 | age_years | wear-out (k>1)
64446 | 0 | 36 | <1.5h | LIB | CS | BPAT | 2021 | 1 | 1 | 1.4 | Y | N | coastal | other | LIB | CS | 2020-21 | 1 | 0 | 0.014019 | ba_g+dur_band+vintage_g | 0 | 0.014019 | 14 | FULL_OUTAGE | inf | 0.15484 | 6.1162 | 1 | 14.4045 | age_years | wear-out (k>1)
64450 | 0 | 36 | <1.5h | LIB | CS | PJM | 2021 | 1 | 10 | 10 | N | N | inland | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 42 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 37.3795 | age_years | wear-out (k>1)
64453 | 2 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 3 | 12 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 0 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64481 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 132 | 528 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 13892 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2609.8836 | age_years | wear-out (k>1)
64489 | 0 | 29 | 2.5-4.5h | OTH | CS | CISO | 2023 | 1 | 75 | 300 | N | N | arid | CISO | other | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 6828 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1282.7732 | age_years | wear-out (k>1)
64508 | 1 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 14 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 10.7033 | age_years | wear-out (k>1)
64509 | 1 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 4 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 3.0581 | age_years | wear-out (k>1)
64510 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 5.1 | 10 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 38 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 29.0519 | age_years | wear-out (k>1)
64511 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 2.5 | 5 | Y | N | coastal | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 16.5 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 12.6147 | age_years | wear-out (k>1)
64512 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.5 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 3 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 2.2936 | age_years | wear-out (k>1)
64513 | 1 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 4 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 3.0581 | age_years | wear-out (k>1)
64514 | 0 | 36 | <1.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 2.5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 15 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 13.3498 | age_years | wear-out (k>1)
64516 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 16 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 12.2324 | age_years | wear-out (k>1)
64520 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 15 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 11.4679 | age_years | wear-out (k>1)
64522 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2021 | 1 | 1.3 | 2 | N | N | inland | CPLE | LIB | CS | 2020-21 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 8.5 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 10.4863 | age_years | wear-out (k>1)
64528 | 0 | 55 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 200 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 3780 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 2488.1678 | age_years | wear-out (k>1)
64529 | 0 | 11 | 2.5-4.5h | LIB | CS | TVA | 2025 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 2765 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 1434.1726 | age_years | wear-out (k>1)
64545 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 73 | 108.6 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 1935.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 126.6086 | age_years | wear-out (k>1)
64546 | 0 | 24 | 2.5-4.5h | LIB | BL | FPL | 2019 | 0 | 10 | 40 | N | N | coastal | other | LIB | BL | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0 | 0.0041667 | 218 | FULL_OUTAGE | inf | 0.048771 | 6.1162 | 1 | 66.6665 | age_years | wear-out (k>1)
64564 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 110 | 440 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 9496.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1784.1031 | age_years | wear-out (k>1)
64601 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 12 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 6.1806 | age_years | wear-out (k>1)
64611 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 8.3 | 3.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 845.5 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 1861.6481 | age_years | wear-out (k>1)
64612 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 0 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
64614 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 823.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 154.7106 | age_years | wear-out (k>1)
64617 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 9.5 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 175 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 133.7918 | age_years | wear-out (k>1)
64618 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 9 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 145 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 128.9962 | age_years | wear-out (k>1)
64619 | 0 | 33 | >4.5h | LIB | CS | ISNE | 2023 | 1 | 0.8 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 69 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 61.3844 | age_years | wear-out (k>1)
64620 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 5.1 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 90 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 68.8072 | age_years | wear-out (k>1)
64624 | 0 | 49 | <1.5h | LIB | CS | CISO | 2021 | 1 | 50 | 50 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 5021.5 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 11056.4943 | age_years | wear-out (k>1)
64627 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 17 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 4.7262 | age_years | wear-out (k>1)
64630 | 0 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 20 | 50 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 1453.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 273.0684 | age_years | wear-out (k>1)
64633 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 240 | 960 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 24396 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 7911.0263 | age_years | wear-out (k>1)
64636 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 200 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 8455 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 9928.7899 | age_years | wear-out (k>1)
64640 | 2 | 36 | <1.5h | LIB | CS | CPLW | 2022 | 1 | 4.4 | 4.4 | N | Y | inland | other | LIB | CS | 2022-23 | 0 | 1 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 18.5 | FULL_OUTAGE | inf | 0.20148 | 6.1162 | 1 | 25.4587 | age_years | wear-out (k>1)
64656 | 0 | 18 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 12.5 | 50 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1251 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 648.8788 | age_years | wear-out (k>1)
64664 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 92 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 25.5768 | age_years | wear-out (k>1)
64672 | 0 | 31 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.6 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 1596 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 315.7343 | age_years | wear-out (k>1)
64686 | 0 | 36 | <1.5h | LIB | OT | NYIS | 2022 | 1 | 24.7 | 20 | N | Y | inland | NYIS | LIB | other | 2022-23 | 0 | 1 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 1020 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 907.788 | age_years | wear-out (k>1)
64695 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 3.7 | 15 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 186.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 1.3688 | age_years | wear-out (k>1)
64696 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 4.5 | 20.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 225 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 172.018 | age_years | wear-out (k>1)
64701 | 0 | 40 | 1.5-2.5h | LIB | CS | CISO | 2022 | 0 | 125 | 250 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 7244 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 3029.4518 | age_years | wear-out (k>1)
64712 | 0 | 50 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 100 | 200 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 5802.5 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 3578.7463 | age_years | wear-out (k>1)
64713 | 0 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 10979.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 5654.9715 | age_years | wear-out (k>1)
64719 | 1 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 7.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 28 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 21.4067 | age_years | wear-out (k>1)
64726 | 0 | 35 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 3.6 | 8 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 67 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 76.4932 | age_years | wear-out (k>1)
64727 | 2 | 36 | 2.5-4.5h | LIB | OT | ISNE | 2022 | 1 | 3 | 8 | N | N | coastal | ISNE | LIB | other | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 43.5 | FULL_OUTAGE | inf | 0.21337 | 6.1162 | 1 | 63.8531 | age_years | wear-out (k>1)
64731 | 3 | 36 | 1.5-2.5h | OTH | CS | ISNE | 2021 | 1 | 2.3 | 4.8 | N | N | inland | ISNE | other | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 0.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 0.47522 | age_years | wear-out (k>1)
64743 | 0 | 36 | <1.5h | LIB | CS | CISO | 2022 | 0 | 5 | 5 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 351.5 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 319.4814 | age_years | wear-out (k>1)
64752 | 0 | 24 | >4.5h | LIB | CS | FPC | 2023 | 1 | 2.5 | 18 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 35.5 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 31.5818 | age_years | wear-out (k>1)
64759 | 1 | 24 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 4.5 | 13.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 142.5 | FULL_OUTAGE | inf | 0.21337 | 6.1162 | 1 | 209.1739 | age_years | wear-out (k>1)
64760 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 0 | 3 | 10 | Y | Y | coastal | ISNE | LIB | CS | 2022-23 | 1 | 1 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 87.5 | FULL_OUTAGE | inf | 0.21337 | 6.1162 | 1 | 128.4401 | age_years | wear-out (k>1)
64761 | 0 | 6 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 2 | 11.9 | N | N | coastal | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 42.5 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 37.8092 | age_years | wear-out (k>1)
64763 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | 2020-21 | 1 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 41.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 39.4429 | age_years | wear-out (k>1)
64764 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 1.5 | 3.1 | Y | Y | inland | ISNE | LIB | CS | 2020-21 | 1 | 1 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 35.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 33.7403 | age_years | wear-out (k>1)
64765 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.015487 | ba_g+dur_band+vintage_g | 0 | 0.015487 | 46.5 | FULL_OUTAGE | inf | 0.16959 | 6.1162 | 1 | 52.8537 | age_years | wear-out (k>1)
64766 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 2.2 | 8.8 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 44.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 22.9196 | age_years | wear-out (k>1)
64811 | 0 | 23 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 24.8 | 25 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 565.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 36.9915 | age_years | wear-out (k>1)
64844 | 1 | 13 | 1.5-2.5h | PBB | CS | ISNE | 2024 | 1 | 1.4 | 2.8 | Y | N | inland | ISNE | other | CS | 2024+ | 1 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 23 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 28.3747 | age_years | wear-out (k>1)
64851 | 0 | 23 | <1.5h | LIB | CS | CISO | 2023 | 1 | 131 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 11681 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 10616.9609 | age_years | wear-out (k>1)
64852 | 1 | 29 | <1.5h | LIB | CS | CISO | 2023 | 1 | 149 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 12083.5 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 10982.7966 | age_years | wear-out (k>1)
64864 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 88 | 352 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 8291 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2688.5686 | age_years | wear-out (k>1)
64875 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 23 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 21.8599 | age_years | wear-out (k>1)
64876 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 286 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 79.5106 | age_years | wear-out (k>1)
64877 | 0 | 44 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 11 | 31.5 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 495 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 254.9489 | age_years | wear-out (k>1)
64878 | 0 | 41 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 144 | 272 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 6838.5 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 2859.8711 | age_years | wear-out (k>1)
64879 | 0 | 44 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 120 | 250 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 4492 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 1878.5612 | age_years | wear-out (k>1)
64908 | 0 | 19 | >4.5h | LIB | CS | CISO | 2024 | 1 | 40 | 200 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.025862 | dur_band+climate_region | 0 | 0.025862 | 3315 | FULL_OUTAGE | inf | 0.26681 | 6.1162 | 1 | 6292.3015 | age_years | wear-out (k>1)
64915 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 524.5 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 345.2497 | age_years | wear-out (k>1)
64916 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 444 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 292.261 | age_years | wear-out (k>1)
64917 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 7.5 | 15 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 401.5 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 264.2855 | age_years | wear-out (k>1)
64921 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 20 | 80 | Y | Y | coastal | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 |  | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 |  | age_years | wear-out (k>1)
64928 | 0 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 33 | 70 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 1792.5 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 749.6262 | age_years | wear-out (k>1)
64929 | 0 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 40 | 83.5 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 1178 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 492.6414 | age_years | wear-out (k>1)
64970 | 2 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 20.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 99 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 75.6879 | age_years | wear-out (k>1)
64980 | 0 | 36 | 2.5-4.5h | LIB | BL | ISNE | 2021 | 1 | 0.5 | 2.1 | N | N | coastal | ISNE | LIB | BL | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 3 | FULL_OUTAGE | inf | 0.1175 | 6.1162 | 1 | 2.2936 | age_years | wear-out (k>1)
64993 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 40 | 160 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 1829 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 343.6134 | age_years | wear-out (k>1)
65007 | 0 | 3 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 100 | 400 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 4 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 3.6244 | age_years | wear-out (k>1)
65011 | 0 | 2 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 75 | 300 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 4.5 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 4.0775 | age_years | wear-out (k>1)
65014 | 0 | 18 | 1.5-2.5h | LIB | CS | ISNE | 2024 | 1 | 2.5 | 4.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 4.5 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 5.2231 | age_years | wear-out (k>1)
65015 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 12.8 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 153.5 | FULL_OUTAGE | inf | 0.21337 | 6.1162 | 1 | 225.3207 | age_years | wear-out (k>1)
65018 | 0 | 15 | 2.5-4.5h | LIB | OT | SOCO | 2024 | 0 | 65 | 260 | N | Y | inland | other | LIB | other | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 7460 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 3869.4132 | age_years | wear-out (k>1)
65028 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.8 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 1679 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 332.154 | age_years | wear-out (k>1)
65029 | 3 | 36 | 1.5-2.5h | LIB | BL | MISO | 2021 | 1 | 0.3 | 0.5 | Y | N | inland | MISO | LIB | BL | 2020-21 | 1 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
65035 | 0 | 16 | 2.5-4.5h | LIB | CS | NYIS | 2023 | 0 | 7.5 | 30 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.025806 | ba_g+dur_band+vintage_g | 0 | 0.025806 | 646 | FULL_OUTAGE | inf | 0.26632 | 6.1162 | 1 | 1223.5551 | age_years | wear-out (k>1)
65044 | 0 | 24 | 2.5-4.5h | LIB | CS | PJM | 2023 | 0 | 20 | 80 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 1729 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 1397.1631 | age_years | wear-out (k>1)
65053 | 0 | 34 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 112 | 448 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 13042 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2450.1945 | age_years | wear-out (k>1)
65054 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1 | 5.4 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 33.5 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 29.8026 | age_years | wear-out (k>1)
65055 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.2 | 4.8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 20.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 19.4838 | age_years | wear-out (k>1)
65056 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 36.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 34.6907 | age_years | wear-out (k>1)
65057 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.3 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 23.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 22.3351 | age_years | wear-out (k>1)
65058 | 0 | 30 | <1.5h | LIB | CS | HECO | 2023 | 1 | 36 | 4.6 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 2776.5 | FULL_OUTAGE | inf | 0.20148 | 6.1162 | 1 | 3820.8648 | age_years | wear-out (k>1)
65098 | 1 | 21 | 1.5-2.5h | LIB | CS | SWPP | 2020 | 0 | 1.5 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 17 | FULL_OUTAGE | inf | 0.23407 | 6.1162 | 1 | 27.7268 | age_years | wear-out (k>1)
65114 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1.5 | 8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 81.5 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 72.5047 | age_years | wear-out (k>1)
65140 | 0 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 350 | 1400 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 42235.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 7934.7639 | age_years | wear-out (k>1)
65154 | 0 | 12 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 2 | 4.3 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 16 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 18.267 | age_years | wear-out (k>1)
65174 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 37 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 35.1659 | age_years | wear-out (k>1)
65217 | 1 | 36 | 2.5-4.5h | LIB | OT | NYIS | 2021 | 1 | 4.5 | 17 | N | N | inland | NYIS | LIB | other | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 43.5 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 98.2355 | age_years | wear-out (k>1)
65239 | 0 | 7 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 24.6 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 255 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 226.8553 | age_years | wear-out (k>1)
65240 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 48 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 13.602 | age_years | wear-out (k>1)
65241 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 38 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 10.7683 | age_years | wear-out (k>1)
65242 | 2 | 35 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.5 | 3.8 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 0 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
65243 | 0 | 24 | 2.5-4.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 21.5 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 17.3736 | age_years | wear-out (k>1)
65244 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 25.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 7.2261 | age_years | wear-out (k>1)
65245 | 0 | 24 | <1.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.013793 | dur_band+climate_region | 0 | 0.013793 | 25.5 | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 | 25.8146 | age_years | wear-out (k>1)
65246 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 38.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 10.91 | age_years | wear-out (k>1)
65247 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 34.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 9.7765 | age_years | wear-out (k>1)
65248 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 22.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 6.376 | age_years | wear-out (k>1)
65249 | 1 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 31 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 8.7847 | age_years | wear-out (k>1)
65250 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 48 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 13.602 | age_years | wear-out (k>1)
65259 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 1228.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 80.3609 | age_years | wear-out (k>1)
65271 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 125 | 125 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 1227 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 80.2628 | age_years | wear-out (k>1)
65291 | 0 | 19 | 2.5-4.5h | LIB | CS | TVA | 2024 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 2637.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 1368.0399 | age_years | wear-out (k>1)
65382 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 1 | 2 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 39.5 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 16.519 | age_years | wear-out (k>1)
65396 | 0 | 2 | <1.5h | LIB | CS | CISO | 2025 | 0 | 15 | 15 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 1080.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 1268.8418 | age_years | wear-out (k>1)
65397 | 0 | 14 | <1.5h | LIB | CS | CISO | 2024 | 0 | 30 | 30 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 1606 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 1885.9416 | age_years | wear-out (k>1)
65408 | 1 | 9 | 2.5-4.5h | LIB | CT | CISO | 2021 | 1 | 0.7 | 3 | Y | N | coastal | CISO | LIB | CT | 2020-21 | 1 | 0 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 24 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 12.3612 | age_years | wear-out (k>1)
65409 | 0 | 36 | 1.5-2.5h | LIB | CT | CISO | 2021 | 1 | 0.5 | 0.9 | N | N | coastal | CISO | LIB | CT | 2020-21 | 0 | 0 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 22 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 13.5687 | age_years | wear-out (k>1)
65410 | 0 | 29 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 190 | 380 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 7814 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 1545.8317 | age_years | wear-out (k>1)
65422 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 510 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 264.5309 | age_years | wear-out (k>1)
65429 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 555 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 287.8719 | age_years | wear-out (k>1)
65433 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 426 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 220.9611 | age_years | wear-out (k>1)
65441 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2022 | 1 | 1 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 6.5 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 5.2525 | age_years | wear-out (k>1)
65456 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 112.5 | 450 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 9593 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3110.7754 | age_years | wear-out (k>1)
65457 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 18390 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 5963.4274 | age_years | wear-out (k>1)
65468 | 0 | 12 | 2.5-4.5h | LIB | BL | PJM | 2019 | 1 | 0.6 | 2.1 | Y | Y | coastal | PJM | LIB | BL | <=2019 | 1 | 1 | 0.016591 | dur_band+climate_region | 0 | 0.016591 | 11.5 | FULL_OUTAGE | inf | 0.18053 | 6.1162 | 1 | 14.0036 | age_years | wear-out (k>1)
65469 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 0.8 | 3.1 | N | N | industrial | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 53 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 9.9571 | age_years | wear-out (k>1)
65472 | 0 | 24 | 2.5-4.5h | LIB | CS | NEVP | 2021 | 0 | 10 | 40 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 898.5 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 515.194 | age_years | wear-out (k>1)
65489 | 1 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 10262 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 7575.0157 | age_years | wear-out (k>1)
65490 | 1 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 8758.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 6465.1895 | age_years | wear-out (k>1)
65491 | 1 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 7961.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 5876.8746 | age_years | wear-out (k>1)
65492 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 175 | 175 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 8880 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 6554.8762 | age_years | wear-out (k>1)
65493 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 50 | 50 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 2595 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 1915.5297 | age_years | wear-out (k>1)
65499 | 0 | 36 | 1.5-2.5h | LIB | CS | PJM | 2022 | 0 | 10.5 | 24.6 | Y | Y | inland | PJM | LIB | CS | 2022-23 | 1 | 1 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 1144 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 1411.3337 | age_years | wear-out (k>1)
65530 | 0 | 24 | 1.5-2.5h | LIB | CS | MISO | 2022 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 140 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 172.7157 | age_years | wear-out (k>1)
65531 | 0 | 24 | 1.5-2.5h | LIB | CS | MISO | 2023 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 121.5 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 149.8925 | age_years | wear-out (k>1)
65562 | 0 | 24 | 2.5-4.5h | MAB | BL | CISO | 2024 | 1 | 1.6 | 5.9 | N | N | arid | CISO | other | BL | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 85 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 27.5634 | age_years | wear-out (k>1)
65568 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 1 | 0.6 | 1.1 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 24.5 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 15.1106 | age_years | wear-out (k>1)
65588 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 70 | 140 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 4197 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 583.4018 | age_years | wear-out (k>1)
65589 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 8060.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1120.4456 | age_years | wear-out (k>1)
65591 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 126 | 504 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 10586 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3432.781 | age_years | wear-out (k>1)
65614 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 2.1 | 4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 70 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 29.2741 | age_years | wear-out (k>1)
65633 | 0 | 29 | <1.5h | LIB | CS | MISO | 2023 | 0 | 3.6 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 1 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0.88999 | age_years | wear-out (k>1)
65635 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 587 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 2371.5134 | age_years | wear-out (k>1)
65644 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 7236 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1005.8364 | age_years | wear-out (k>1)
65645 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 8723 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1212.5361 | age_years | wear-out (k>1)
65650 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 1.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 27.5 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 7.6452 | age_years | wear-out (k>1)
65656 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 20 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 1183.5 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 4781.4073 | age_years | wear-out (k>1)
65657 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 65 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 3090 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 3628.6175 | age_years | wear-out (k>1)
65669 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 40 | FULL_OUTAGE | inf | 0.21337 | 6.1162 | 1 | 58.7155 | age_years | wear-out (k>1)
65670 | 1 | 35 | >4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 5 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.012121 | dur_band+climate_region | 0 | 0.012121 | 27.5 | FULL_OUTAGE | inf | 0.13537 | 6.1162 | 1 | 24.4648 | age_years | wear-out (k>1)
65672 | 0 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 169 | 676 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 18683.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 3510.0605 | age_years | wear-out (k>1)
65673 | 0 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 47 | 188 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 5100 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 958.1346 | age_years | wear-out (k>1)
65674 | 0 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 136 | 136 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 9030.5 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 8207.8987 | age_years | wear-out (k>1)
65675 | 0 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 100 | 100 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 2440.5 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 2218.1913 | age_years | wear-out (k>1)
65677 | 0 | 30 | <1.5h | LIB | CS | CISO | 2023 | 1 | 18.8 | 18.8 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.012384 | ba_g+dur_band+vintage_g | 0 | 0.012384 | 548.5 | FULL_OUTAGE | inf | 0.13809 | 6.1162 | 1 | 498.5363 | age_years | wear-out (k>1)
65692 | 0 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 42 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 2304 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 2842.4064 | age_years | wear-out (k>1)
65693 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 5777 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 803.0289 | age_years | wear-out (k>1)
65694 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 802 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 52.4619 | age_years | wear-out (k>1)
65695 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 100 | 100 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 1932 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 126.3796 | age_years | wear-out (k>1)
65696 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 2297 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 150.2557 | age_years | wear-out (k>1)
65698 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 6370 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 885.4585 | age_years | wear-out (k>1)
65699 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 111 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 3123 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 617.8183 | age_years | wear-out (k>1)
65700 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 107 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 3040.5 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 601.4975 | age_years | wear-out (k>1)
65701 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 800 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 52.3311 | age_years | wear-out (k>1)
65711 | 0 | 17 | 2.5-4.5h | LIB | CS | IID | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 14331 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 7433.3192 | age_years | wear-out (k>1)
65733 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 588 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 2375.5534 | age_years | wear-out (k>1)
65734 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 15606.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2931.9859 | age_years | wear-out (k>1)
65735 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 14596.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2742.2377 | age_years | wear-out (k>1)
65743 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 50 | 200 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 4762 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1544.2002 | age_years | wear-out (k>1)
65744 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 136 | 544 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 12977.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 4208.286 | age_years | wear-out (k>1)
65809 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 172.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 11.2839 | age_years | wear-out (k>1)
65810 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 186 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 12.167 | age_years | wear-out (k>1)
65811 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 186 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 12.167 | age_years | wear-out (k>1)
65812 | 0 | 21 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 136 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 100.39 | age_years | wear-out (k>1)
65813 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 182.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 11.938 | age_years | wear-out (k>1)
65814 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 184.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 12.0689 | age_years | wear-out (k>1)
65815 | 0 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 1 | 2.1 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 2 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 2.3214 | age_years | wear-out (k>1)
65829 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 159 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 10.4008 | age_years | wear-out (k>1)
65830 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 157.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 10.3027 | age_years | wear-out (k>1)
65831 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 179.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 11.7418 | age_years | wear-out (k>1)
65832 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 130 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 8.5038 | age_years | wear-out (k>1)
65833 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 177.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 11.611 | age_years | wear-out (k>1)
65834 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 186 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 12.167 | age_years | wear-out (k>1)
65835 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 182.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 11.938 | age_years | wear-out (k>1)
65836 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 10.4 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0045593 | ba_g+dur_band+vintage_g | 0 | 0.0045593 | 191 | FULL_OUTAGE | inf | 0.053242 | 6.1162 | 1 | 63.9133 | age_years | wear-out (k>1)
65837 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 106 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 78.2451 | age_years | wear-out (k>1)
65857 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 22207 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 4172.0188 | age_years | wear-out (k>1)
65860 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 160 | 320 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 8869.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1232.9002 | age_years | wear-out (k>1)
65861 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 10423 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1448.8437 | age_years | wear-out (k>1)
65866 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 593 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 307.582 | age_years | wear-out (k>1)
65888 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 524 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 271.7926 | age_years | wear-out (k>1)
65927 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 547 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 283.7224 | age_years | wear-out (k>1)
65933 | 0 | 32 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 80 | 320 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 6966.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1308.7931 | age_years | wear-out (k>1)
65945 | 1 | 36 | 2.5-4.5h | LIB | CS | PJM | 2022 | 1 | 1.5 | 4.3 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.016591 | dur_band+climate_region | 0 | 0.016591 | 12 | FULL_OUTAGE | inf | 0.18053 | 6.1162 | 1 | 14.6125 | age_years | wear-out (k>1)
65950 | 1 | 32 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 1.8 | 6.4 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 120 | FULL_OUTAGE | inf | 0.21337 | 6.1162 | 1 | 176.1465 | age_years | wear-out (k>1)
65951 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 12 | 12 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0 | 0.0092593 | 2050.5 | FULL_OUTAGE | inf | 0.10516 | 6.1162 | 1 | 1393.4736 | age_years | wear-out (k>1)
65952 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 20 | 20 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0 | 0.0092593 | 3327 | FULL_OUTAGE | inf | 0.10516 | 6.1162 | 1 | 2260.9542 | age_years | wear-out (k>1)
65953 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 7 | 7 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0 | 0.0092593 | 1143.5 | FULL_OUTAGE | inf | 0.10516 | 6.1162 | 1 | 777.0968 | age_years | wear-out (k>1)
65956 | 0 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 88 | 264 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6630.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 48.6641 | age_years | wear-out (k>1)
65962 | 0 | 24 | >4.5h | LIB | CS | CISO | 2024 | 1 | 10 | 47.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 761.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 5.589 | age_years | wear-out (k>1)
65963 | 0 | 30 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 60 | 240 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6495.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 47.6733 | age_years | wear-out (k>1)
65980 | 0 | 31 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 131 | 524 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 13311 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2500.7314 | age_years | wear-out (k>1)
65987 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 325 | 1300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 39866.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 7489.7009 | age_years | wear-out (k>1)
65988 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 8284.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1556.4052 | age_years | wear-out (k>1)
66006 | 0 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 73.2 | 120 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 3429.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 476.7159 | age_years | wear-out (k>1)
66007 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 4593 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 908.6262 | age_years | wear-out (k>1)
66008 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 4727 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 935.1352 | age_years | wear-out (k>1)
66009 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 203 | 400 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 5889 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 1165.0119 | age_years | wear-out (k>1)
66023 | 1 | 14 | <1.5h | LIB | CS | CISO | 2024 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 0 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66050 | 0 | 40 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 127 | 508 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 12855 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2415.0629 | age_years | wear-out (k>1)
66067 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 0 | 185 | 565 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 14604 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 107.1851 | age_years | wear-out (k>1)
66075 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 3.3 | N | N | coastal | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 101 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 95.9935 | age_years | wear-out (k>1)
66076 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 71 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 52.6364 | age_years | wear-out (k>1)
66128 | 0 | 10 | 2.5-4.5h | LIB | CS | TEC | 2025 | 1 | 40 | 103 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 779.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 404.3174 | age_years | wear-out (k>1)
66129 | 0 | 10 | 1.5-2.5h | LIB | CS | TEC | 2024 | 1 | 15 | 30 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 226.5 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 346.3297 | age_years | wear-out (k>1)
66137 | 0 | 21 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 40.4 | 80 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 2080 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 289.1293 | age_years | wear-out (k>1)
66163 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 20 | 80 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1975.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 14.4991 | age_years | wear-out (k>1)
66170 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 368.8 | N | N | arid | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 7464 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 1476.5918 | age_years | wear-out (k>1)
66180 | 1 | 28 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 3.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 0 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66181 | 1 | 29 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 7.8 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 0 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66182 | 1 | 33 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 0 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66208 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 132 | 528 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 15161.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 2848.384 | age_years | wear-out (k>1)
66218 | 3 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2020 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66222 | 4 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2021 | 1 | 4 | 8 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66228 | 4 | 36 | <1.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 2 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 0 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66232 | 2 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66263 | 0 | 19 | 2.5-4.5h | LIB | CS | SRP | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 33877.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 17571.8561 | age_years | wear-out (k>1)
66265 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 828.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 972.9157 | age_years | wear-out (k>1)
66266 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 648.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 761.5399 | age_years | wear-out (k>1)
66270 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 162 | 648 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 12611 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 4089.439 | age_years | wear-out (k>1)
66278 | 0 | 21 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 740.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 869.5765 | age_years | wear-out (k>1)
66279 | 2 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 652 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 765.65 | age_years | wear-out (k>1)
66280 | 1 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 1082.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 1271.1904 | age_years | wear-out (k>1)
66281 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 20 | 20 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 859 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 1008.7322 | age_years | wear-out (k>1)
66285 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 20915 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 6782.2231 | age_years | wear-out (k>1)
66286 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 200 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 10781 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 43555.853 | age_years | wear-out (k>1)
66325 | 0 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 116 | 464 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 4738.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 2457.8036 | age_years | wear-out (k>1)
66326 | 0 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2024 | 0 | 40 | 160 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 3490.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 1810.4808 | age_years | wear-out (k>1)
66327 | 1 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 4 | 16 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 267 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 138.4897 | age_years | wear-out (k>1)
66328 | 1 | 12 | 1.5-2.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 4 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 140 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 214.0669 | age_years | wear-out (k>1)
66329 | 1 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 8 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 0 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66330 | 1 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 3 | 12 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 274.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 142.3799 | age_years | wear-out (k>1)
66333 | 0 | 18 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 90 | 360 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 10478 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 5434.8139 | age_years | wear-out (k>1)
66334 | 0 | 20 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 250 | 1000 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 30035 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 15578.7971 | age_years | wear-out (k>1)
66336 | 0 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 102.6 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 5791.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 805.0445 | age_years | wear-out (k>1)
66337 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 11481 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1595.9105 | age_years | wear-out (k>1)
66338 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 223.4 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 11024.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 8137.864 | age_years | wear-out (k>1)
66357 | 0 | 30 | 2.5-4.5h | LIB | CS | NEVP | 2023 | 1 | 65 | 260 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6979.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 51.2256 | age_years | wear-out (k>1)
66394 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 60 | 160 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 3423.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1110.1573 | age_years | wear-out (k>1)
66408 | 0 | 31 | 2.5-4.5h | LIB | CS | EPE | 2023 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3308 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 24.2789 | age_years | wear-out (k>1)
66420 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 262.5 | 250 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 8277 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 6109.7646 | age_years | wear-out (k>1)
66423 | 0 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 68.8 | 275.2 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 7325.5 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1376.2383 | age_years | wear-out (k>1)
66461 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 116.6 | 400 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 10026 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3251.1867 | age_years | wear-out (k>1)
66462 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 88 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 8473 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2747.5867 | age_years | wear-out (k>1)
66474 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 6.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 0 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66488 | 3 | 27 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66494 | 0 | 19 | 2.5-4.5h | LIB | CS | CISO | 2024.0882 | 0 | 680 | 2720 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 71677 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 23243.0986 | age_years | wear-out (k>1)
66499 | 4 | 36 | 1.5-2.5h | LIB | CT | PJM | 2021 | 1 | 1.2 | 2.4 | N | N | coastal | PJM | LIB | CT | 2020-21 | 0 | 0 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 2 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 2.3214 | age_years | wear-out (k>1)
66500 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 85 | 212 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0084034 | ba_g+dur_band+vintage_g | 0 | 0.0084034 | 4968.5 | FULL_OUTAGE | inf | 0.095923 | 6.1162 | 1 | 3064.369 | age_years | wear-out (k>1)
66502 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 54 | 216 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0070175 | ba_g+dur_band+vintage_g | 0 | 0.0070175 | 3759.5 | FULL_OUTAGE | inf | 0.080762 | 6.1162 | 1 | 1936.3236 | age_years | wear-out (k>1)
66505 | 0 | 15 | 1.5-2.5h | LIB | CS | CISO | 2024 | 0 | 6 | 12 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 212 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 856.4921 | age_years | wear-out (k>1)
66533 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 10 | 20 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 |  | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 |  | age_years | wear-out (k>1)
66540 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 100 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 8494 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 6269.9457 | age_years | wear-out (k>1)
66574 | 0 | 15 | >4.5h | LIB | CS | PNM | 2024 | 1 | 100 | 561.4 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 10717.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 78.6604 | age_years | wear-out (k>1)
66575 | 0 | 21 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 24158 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 7833.8487 | age_years | wear-out (k>1)
66598 | 0 | 15 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 4250.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1378.3332 | age_years | wear-out (k>1)
66599 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 0 | 7.3 | 7.1 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 423.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 497.3202 | age_years | wear-out (k>1)
66606 | 0 | 2 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 175 | 350 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 2393 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 2777.5338 | age_years | wear-out (k>1)
66616 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 5008 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 327.5927 | age_years | wear-out (k>1)
66617 | 0 | 17 | 2.5-4.5h | LIB | CT | CISO | 2024 | 0 | 100 | 400 | N | N | coastal | CISO | LIB | CT | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 12037 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3903.3048 | age_years | wear-out (k>1)
66619 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 1.2 | 4.6 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 104 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 33.7247 | age_years | wear-out (k>1)
66620 | 0 | 29 | >4.5h | LIB | CS | CISO | 2023 | 1 | 40 | 300 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 3569.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 26.1981 | age_years | wear-out (k>1)
66627 | 0 | 31 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 260 | 1040 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 26072.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 191.3575 | age_years | wear-out (k>1)
66636 | 0 | 25 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 9634 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 1809.9351 | age_years | wear-out (k>1)
66637 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 15386 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 4989.3036 | age_years | wear-out (k>1)
66648 | 0 | 10 | >4.5h | LIB | CS | CISO | 2025 | 0 | 2 | 9 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0 | dur_band+climate_region | 0 | 0.0001 | 24 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 0.17615 | age_years | wear-out (k>1)
66650 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 13 | 52 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 1254.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 406.8037 | age_years | wear-out (k>1)
66659 | 0 | 10 | <1.5h | LIB | CS | CISO | 2025 | 0 | 97 | 97 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 2732.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 3208.8017 | age_years | wear-out (k>1)
66660 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 2132 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 2503.6286 | age_years | wear-out (k>1)
66661 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 2374.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 2788.3988 | age_years | wear-out (k>1)
66662 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 32 | 32 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 733 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 860.7691 | age_years | wear-out (k>1)
66666 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 125 | 500 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 12549.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 4069.496 | age_years | wear-out (k>1)
66669 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 2180.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 707.0828 | age_years | wear-out (k>1)
66688 | 1 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 103.6 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 3953.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 2918.3224 | age_years | wear-out (k>1)
66690 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 2817.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 2079.7707 | age_years | wear-out (k>1)
66694 | 1 | 14 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 34752 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 18025.4489 | age_years | wear-out (k>1)
66699 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 59.7 | 59.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 4105.5 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 4821.1291 | age_years | wear-out (k>1)
66716 | 0 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 0 | 100 | 400 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 7273 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 53.3797 | age_years | wear-out (k>1)
66717 | 1 | 22 | 2.5-4.5h | OTH | CS | CPLE | 2023 | 1 | 18 | 72 | N | N | inland | CPLE | other | CS | 2022-23 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66726 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 70 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 7330 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2376.9398 | age_years | wear-out (k>1)
66727 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 149 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 170.1118 | age_years | wear-out (k>1)
66728 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 135 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 154.1282 | age_years | wear-out (k>1)
66757 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 6250 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2026.7222 | age_years | wear-out (k>1)
66758 | 0 | 23 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 18.3 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 3258.5 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 2900.0268 | age_years | wear-out (k>1)
66764 | 0 | 23 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 0 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66765 | 1 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 0 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66767 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 9.5 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.030769 | ba_g+dur_band+vintage_g | 0 | 0.030769 | 25.5 | FULL_OUTAGE | inf | 0.30873 | 6.1162 | 1 | 57.5863 | age_years | wear-out (k>1)
66772 | 0 | 22 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 28 | 112 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 2906 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 545.9489 | age_years | wear-out (k>1)
66773 | 0 | 20 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 7680.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2490.5984 | age_years | wear-out (k>1)
66782 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 174.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 128.8092 | age_years | wear-out (k>1)
66783 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 107.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 79.3524 | age_years | wear-out (k>1)
66784 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 124 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 91.5321 | age_years | wear-out (k>1)
66788 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 134 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 98.9137 | age_years | wear-out (k>1)
66789 | 0 | 23 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 127 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 93.7465 | age_years | wear-out (k>1)
66790 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 197 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 145.4179 | age_years | wear-out (k>1)
66791 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 168.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 124.3803 | age_years | wear-out (k>1)
66792 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 94 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 69.3872 | age_years | wear-out (k>1)
66794 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 101 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 74.5543 | age_years | wear-out (k>1)
66795 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 145 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 107.0335 | age_years | wear-out (k>1)
66799 | 1 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.7 | 1.3 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 0 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
66801 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 2294 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 318.8763 | age_years | wear-out (k>1)
66804 | 0 | 17 | 1.5-2.5h | LIB | CT | ERCO | 2024 | 0 | 150 | 300 | N | Y | inland | ERCO | LIB | CT | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 10807 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1502.2214 | age_years | wear-out (k>1)
66807 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 3 | 12 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.0025597 | ba_g+dur_band+vintage_g | 0 | 0.0025597 | 384 | FULL_OUTAGE | inf | 0.03025 | 6.1162 | 1 | 72.1419 | age_years | wear-out (k>1)
66814 | 0 | 21 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5684.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 2948.4825 | age_years | wear-out (k>1)
66871 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 300 | 467 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 9676.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1345.0769 | age_years | wear-out (k>1)
66872 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 158.3 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 4434 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 616.3459 | age_years | wear-out (k>1)
66885 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 25 | 100 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 1544.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 500.8436 | age_years | wear-out (k>1)
66890 | 0 | 1 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 38 | 152 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 4 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1.2971 | age_years | wear-out (k>1)
66905 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 157.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 2260 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 314.1501 | age_years | wear-out (k>1)
66925 | 0 | 23 | <1.5h | LIB | BL | TEPC | 2023 | 1 | 20 | 20 | N | N | arid | other | LIB | BL | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 2244 | FULL_OUTAGE | inf | 0.20148 | 6.1162 | 1 | 3088.068 | age_years | wear-out (k>1)
66926 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 161.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 10.5643 | age_years | wear-out (k>1)
66927 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 76 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 4.9715 | age_years | wear-out (k>1)
66928 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 82.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 5.3966 | age_years | wear-out (k>1)
66929 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 101 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 6.6068 | age_years | wear-out (k>1)
66930 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 149 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 9.7467 | age_years | wear-out (k>1)
66931 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 109.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 7.1628 | age_years | wear-out (k>1)
66932 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 77.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 5.0696 | age_years | wear-out (k>1)
66933 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 145.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 9.5177 | age_years | wear-out (k>1)
66934 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 97.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 6.3779 | age_years | wear-out (k>1)
66935 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 98.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 6.4433 | age_years | wear-out (k>1)
66946 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 45 | 180 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 5659 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1835.0753 | age_years | wear-out (k>1)
66949 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 40 | 160 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 4135 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1340.8794 | age_years | wear-out (k>1)
66950 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 59 | 236 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 6534.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2118.9786 | age_years | wear-out (k>1)
66951 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 9087 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2946.6919 | age_years | wear-out (k>1)
66966 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 2.1 | 4.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 40.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 38.4924 | age_years | wear-out (k>1)
67019 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 2238 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 1652.0059 | age_years | wear-out (k>1)
67036 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 76 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 93.7599 | age_years | wear-out (k>1)
67037 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 85 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 104.8631 | age_years | wear-out (k>1)
67039 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 92 | 368 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 11494 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3727.2232 | age_years | wear-out (k>1)
67040 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 103 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 29.1877 | age_years | wear-out (k>1)
67041 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 15 | 30 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 145.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 41.2312 | age_years | wear-out (k>1)
67042 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 91.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 25.9289 | age_years | wear-out (k>1)
67043 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 48 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 13.602 | age_years | wear-out (k>1)
67044 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 58.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 16.5775 | age_years | wear-out (k>1)
67083 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 174 | 407.4 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 9349 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1299.5529 | age_years | wear-out (k>1)
67091 | 0 | 19 | 2.5-4.5h | LIB | CS | NEVP | 2024 | 1 | 85 | 340 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 10076 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 5226.3013 | age_years | wear-out (k>1)
67092 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 15 | 60 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 1518.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 492.4124 | age_years | wear-out (k>1)
67093 | 0 | 22 | <1.5h | LIB | CS | CISO | 2020 | 0 | 77 | 77 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.03 | ba_g+dur_band+vintage_g | 0 | 0.03 | 1735 | FULL_OUTAGE | inf | 0.30232 | 6.1162 | 1 | 3820.1768 | age_years | wear-out (k>1)
67122 | 0 | 24 | 1.5-2.5h | LIB | CS | SWPP | 2023 | 0 | 1 | 2.4 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0057143 | ba_g+dur_band+vintage_g | 0 | 0.0057143 | 46.5 | FULL_OUTAGE | inf | 0.066273 | 6.1162 | 1 | 19.5019 | age_years | wear-out (k>1)
67162 | 0 | 19 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.011494 | ba_g+dur_band+vintage_g | 0 | 0.011494 | 121 | FULL_OUTAGE | inf | 0.12884 | 6.1162 | 1 | 102.0772 | age_years | wear-out (k>1)
67170 | 1 | 22 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 2.4 | 8.9 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 116 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 37.616 | age_years | wear-out (k>1)
67175 | 0 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 300 | 600 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 13821 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 2734.1874 | age_years | wear-out (k>1)
67183 | 0 | 14 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 60 | 240 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5888 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 3054.0355 | age_years | wear-out (k>1)
67185 | 0 | 18 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | Y | N | inland | ISNE | LIB | CS | 2024+ | 1 | 0 | 0.011494 | ba_g+dur_band+vintage_g | 0 | 0.011494 | 164.5 | FULL_OUTAGE | inf | 0.12884 | 6.1162 | 1 | 138.7744 | age_years | wear-out (k>1)
67186 | 0 | 17 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 5 | 22.4 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.011494 | ba_g+dur_band+vintage_g | 0 | 0.011494 | 418 | FULL_OUTAGE | inf | 0.12884 | 6.1162 | 1 | 352.6304 | age_years | wear-out (k>1)
67187 | 1 | 14 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 3 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.011494 | ba_g+dur_band+vintage_g | 0 | 0.011494 | 212.5 | FULL_OUTAGE | inf | 0.12884 | 6.1162 | 1 | 179.2678 | age_years | wear-out (k>1)
67236 | 0 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 9298.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1292.5332 | age_years | wear-out (k>1)
67237 | 0 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 207.9 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 10541 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1465.2462 | age_years | wear-out (k>1)
67275 | 3 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 1.3 | 5.1 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.025806 | ba_g+dur_band+vintage_g | 0 | 0.025806 | 0 | FULL_OUTAGE | inf | 0.26632 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
67278 | 1 | 3 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 1.1 | 2.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 2 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 8.0801 | age_years | wear-out (k>1)
67281 | 2 | 20 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 4 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.04 | ba_g+dur_band+vintage_g | 0 | 0.04 | 0 | FULL_OUTAGE | inf | 0.38122 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
67282 | 1 | 18 | 1.5-2.5h | LIB | CS | NYIS | 2024 | 1 | 5 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.016809 | dur_band+climate_region | 0 | 0.016809 | 0 | FULL_OUTAGE | inf | 0.18267 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
67284 | 0 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 70.5 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 3063.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 425.8402 | age_years | wear-out (k>1)
67285 | 0 | 19 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 215 | 860 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 23676 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 173.7685 | age_years | wear-out (k>1)
67291 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 33868.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 248.5757 | age_years | wear-out (k>1)
67296 | 2 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 0.4 | 0.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 1 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 1.1417 | age_years | wear-out (k>1)
67299 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 10309 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3342.9566 | age_years | wear-out (k>1)
67300 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1052.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 545.9192 | age_years | wear-out (k>1)
67301 | 0 | 20 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 823.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 427.1397 | age_years | wear-out (k>1)
67302 | 0 | 15 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 723.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 375.2708 | age_years | wear-out (k>1)
67303 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 754 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 391.0908 | age_years | wear-out (k>1)
67304 | 0 | 16 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1109 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 575.2251 | age_years | wear-out (k>1)
67305 | 0 | 18 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1177.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 610.7552 | age_years | wear-out (k>1)
67306 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1210 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 627.6126 | age_years | wear-out (k>1)
67307 | 0 | 18 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 841 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 436.2167 | age_years | wear-out (k>1)
67321 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 70 | 268 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6484 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 47.5889 | age_years | wear-out (k>1)
67323 | 0 | 9 | 1.5-2.5h | LIB | CS | PSCO | 2025 | 1 | 11.2 | 20 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 201 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 307.3389 | age_years | wear-out (k>1)
67328 | 0 | 6 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 75 | 300 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 8034 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 58.965 | age_years | wear-out (k>1)
67454 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 170 | 680 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 20475 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 150.275 | age_years | wear-out (k>1)
67455 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 85 | 340 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 10185.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 74.7558 | age_years | wear-out (k>1)
67474 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 31962 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 234.5831 | age_years | wear-out (k>1)
67489 | 0 | 20 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 45 | 180 | Y | Y | inland | MISO | LIB | CS | 2024+ | 1 | 1 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 7351 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 6660.7653 | age_years | wear-out (k>1)
67493 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 129.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 95.5919 | age_years | wear-out (k>1)
67494 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 126.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 93.3775 | age_years | wear-out (k>1)
67495 | 1 | 17 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 174.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 128.8092 | age_years | wear-out (k>1)
67496 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 164.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 121.4276 | age_years | wear-out (k>1)
67498 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 185 | 740 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 16536 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 5362.2205 | age_years | wear-out (k>1)
67503 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 213.8 | 855 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 24594 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 180.5061 | age_years | wear-out (k>1)
67545 | 0 | 14 | >4.5h | LIB | CS | MISO | 2024 | 1 | 5 | 30.6 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.025862 | dur_band+climate_region | 0 | 0.025862 | 521 | FULL_OUTAGE | inf | 0.26681 | 6.1162 | 1 | 988.9258 | age_years | wear-out (k>1)
67549 | 0 | 7 | 2.5-4.5h | LIB | CT | IPCO | 2025 | 0 | 150 | 600 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 17424 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 9037.6215 | age_years | wear-out (k>1)
67573 | 0 | 6 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 82 | 328 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 9267 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 4806.6826 | age_years | wear-out (k>1)
67577 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 2.2 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 301.5 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 344.2196 | age_years | wear-out (k>1)
67578 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 1 | 2 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015556 | ba_g+dur_band+vintage_g | 0 | 0.015556 | 344 | FULL_OUTAGE | inf | 0.17028 | 6.1162 | 1 | 392.7414 | age_years | wear-out (k>1)
67579 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 82 | 328 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 8077.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2619.3358 | age_years | wear-out (k>1)
67598 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 9219 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1281.4823 | age_years | wear-out (k>1)
67680 | 0 | 6 | >4.5h | LIB | CS | CISO | 2025 | 0 | 400 | 1800 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 20756.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 152.341 | age_years | wear-out (k>1)
67695 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 30 | 127 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 1766 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 572.6706 | age_years | wear-out (k>1)
67698 | 1 | 14 | 1.5-2.5h | LIB | CS | PGE | 2024 | 0 | 17 | 34 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 789.5 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 1207.1844 | age_years | wear-out (k>1)
67710 | 0 | 5 | 2.5-4.5h | OTH | OT | PNM | 2025 | 1 | 57.8 | 231.4 | N | N | arid | other | other | other | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5449 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 2826.3315 | age_years | wear-out (k>1)
67711 | 0 | 6 | 2.5-4.5h | LIB | CS | PGE | 2025 | 0 | 200 | 800 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 15765 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 8177.1179 | age_years | wear-out (k>1)
67712 | 0 | 13 | 2.5-4.5h | LIB | CS | PGE | 2024 | 0 | 75 | 300 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 6637.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 3442.7923 | age_years | wear-out (k>1)
67721 | 0 | 14 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100.3 | 145 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 3587 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 2647.7861 | age_years | wear-out (k>1)
67734 | 0 | 9 | 2.5-4.5h | LIB | CT | CISO | 2025 | 0 | 200 | 800 | Y | Y | arid | CISO | LIB | CT | 2024+ | 1 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 22863 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 7413.9119 | age_years | wear-out (k>1)
67736 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 279 | 1116 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 32710 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 10607.0532 | age_years | wear-out (k>1)
67737 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 304 | 440.8 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 10426 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 7696.0742 | age_years | wear-out (k>1)
67738 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 204 | 298 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 6925 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 5111.77 | age_years | wear-out (k>1)
67739 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 120 | 174 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 4031 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 2975.5299 | age_years | wear-out (k>1)
67740 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 240 | 480 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 12535 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1742.4212 | age_years | wear-out (k>1)
67743 | 1 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 0 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
67745 | 2 | 24 | <1.5h | LIB | CS | NYIS | 2022 | 1 | 5 | 2 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.013793 | dur_band+climate_region | 0 | 0.013793 | 0 | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
67752 | 0 | 7 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 102.6 | 205.1 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 7793 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1083.2619 | age_years | wear-out (k>1)
67758 | 0 | 11 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 14 | 56 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 835 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 756.5962 | age_years | wear-out (k>1)
67762 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72.2 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 2744 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 381.4283 | age_years | wear-out (k>1)
67764 | 0 | 5 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 117 | 472 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 11958 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 3877.687 | age_years | wear-out (k>1)
67828 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 25 | 100 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 2611 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 846.6835 | age_years | wear-out (k>1)
67829 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 20 | 80 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 2208.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 716.1626 | age_years | wear-out (k>1)
67843 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 498 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 69.2242 | age_years | wear-out (k>1)
67845 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 454 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 63.108 | age_years | wear-out (k>1)
67850 | 0 | 1 | 2.5-4.5h | LIB | CS | IID | 2025 | 1 | 35 | 140 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 399 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 206.9566 | age_years | wear-out (k>1)
67851 | 0 | 14 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 20 | N | Y | inland | PJM | LIB | CS | 2024+ | 0 | 1 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 2762.5 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 2458.5926 | age_years | wear-out (k>1)
67855 | 0 | 15 | 2.5-4.5h | LIB | CS | AZPS | 2024.59 | 0 | 200 | 808.4 | N | Y | arid | AZPS | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 11719.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 86.0145 | age_years | wear-out (k>1)
67860 | 0 | 21 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 6750 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 938.2802 | age_years | wear-out (k>1)
67861 | 0 | 17 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 6402.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 889.9762 | age_years | wear-out (k>1)
67869 | 0 | 13 | 2.5-4.5h | LIB | CT | PGE | 2024 | 0 | 200 | 800 | N | N | inland | other | LIB | CT | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 21922.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 11370.9399 | age_years | wear-out (k>1)
67880 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 21.7 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.04 | ba_g+dur_band+vintage_g | 0 | 0.04 | 10.5 | FULL_OUTAGE | inf | 0.38122 | 6.1162 | 1 | 30.8256 | age_years | wear-out (k>1)
67882 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 10 | 43.4 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.04 | ba_g+dur_band+vintage_g | 0 | 0.04 | 32.5 | FULL_OUTAGE | inf | 0.38122 | 6.1162 | 1 | 95.4127 | age_years | wear-out (k>1)
67883 | 0 | 14 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 0 | 8 | 34.1 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.04 | ba_g+dur_band+vintage_g | 0 | 0.04 | 38 | FULL_OUTAGE | inf | 0.38122 | 6.1162 | 1 | 111.5594 | age_years | wear-out (k>1)
67886 | 0 | 24 | 2.5-4.5h | NIB | CS | NYIS | 2023 | 0 | 3 | 12.4 | Y | N | coastal | NYIS | other | CS | 2022-23 | 1 | 0 | 0.025806 | ba_g+dur_band+vintage_g | 0 | 0.025806 | 8 | FULL_OUTAGE | inf | 0.26632 | 6.1162 | 1 | 15.1524 | age_years | wear-out (k>1)
67893 | 0 | 12 | 2.5-4.5h | LIB | CS | MISO | 2025 | 1 | 56.3 | 225 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 9601.5 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 8699.9507 | age_years | wear-out (k>1)
67898 | 0 | 1 | 2.5-4.5h | LIB | CS | NEVP | 2025 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 8671 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 4497.5445 | age_years | wear-out (k>1)
67899 | 0 | 24 | <1.5h | LIB | CS | PJM | 2021 | 0 | 6.2 | 6.2 | N | N | coastal | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.013793 | dur_band+climate_region | 0 | 0.013793 | 735.5 | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 | 744.5732 | age_years | wear-out (k>1)
67905 | 0 | 6 | 2.5-4.5h | LIB | CS | TEPC | 2025 | 0 | 200 | 800 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 23941 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 12417.9118 | age_years | wear-out (k>1)
67931 | 0 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 113.5 | 454 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 7553.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 2449.4154 | age_years | wear-out (k>1)
67948 | 0 | 24 | >4.5h | LIB | CS | SWPP | 2022 | 0 | 1.8 | 9.1 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.025862 | dur_band+climate_region | 0 | 0.025862 | 28 | FULL_OUTAGE | inf | 0.26681 | 6.1162 | 1 | 53.1476 | age_years | wear-out (k>1)
67963 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 125 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 92.2702 | age_years | wear-out (k>1)
67968 | 0 | 9 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 4356 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 605.5035 | age_years | wear-out (k>1)
67973 | 0 | 3 | <1.5h | LIB | BL | AZPS | 2025 | 0 | 113 | 113 | N | N | arid | AZPS | LIB | BL | 2024+ | 0 | 0 | 0.0087159 | dur_band+climate_region | 0 | 0.0087159 | 9962 | FULL_OUTAGE | inf | 0.099307 | 6.1162 | 1 | 6372.6439 | age_years | wear-out (k>1)
68012 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 99.7 | 398.8 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 12581 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 4079.7107 | age_years | wear-out (k>1)
68023 | 0 | 2 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 16.7 | 64 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 955.5 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 309.8453 | age_years | wear-out (k>1)
68058 | 0 | 13 | >4.5h | OTH | CS | WACM | 2024 | 0 | 35.4 | 235 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0 | 0.0001 | 1684.5 | FULL_OUTAGE | inf | 0.0011993 | 6.1162 | 1 | 12.3633 | age_years | wear-out (k>1)
68064 | 0 | 17 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 1.2 | 2.1 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 175.5 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 709.03 | age_years | wear-out (k>1)
68069 | 1 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2.2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 31.5 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 23.3528 | age_years | wear-out (k>1)
68146 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 4583 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 637.0575 | age_years | wear-out (k>1)
68147 | 0 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 45.5 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 41.2277 | age_years | wear-out (k>1)
68148 | 1 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 43 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 38.9624 | age_years | wear-out (k>1)
68189 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 2254 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 313.3161 | age_years | wear-out (k>1)
68266 | 2 | 24 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.3 | 0.5 | N | Y | inland | CISO | LIB | CS | <=2019 | 0 | 1 | 0.026846 | ba_g+dur_band+vintage_g | 0 | 0.026846 | 5.5 | FULL_OUTAGE | inf | 0.27541 | 6.1162 | 1 | 10.8368 | age_years | wear-out (k>1)
68322 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 300 | 1200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 3358 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 1088.9173 | age_years | wear-out (k>1)
68324 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 1833 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 594.3971 | age_years | wear-out (k>1)
68335 | 0 | 16 | 2.5-4.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 7.1 | N | Y | coastal | PJM | LIB | CS | 2024+ | 0 | 1 | 0.016591 | dur_band+climate_region | 0 | 0.016591 | 0 | FULL_OUTAGE | inf | 0.18053 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
68423 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 5663.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 787.2519 | age_years | wear-out (k>1)
68424 | 0 | 7 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 104.9 | 400 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.012346 | ba_g+dur_band+vintage_g | 0 | 0.012346 | 7156 | FULL_OUTAGE | inf | 0.1377 | 6.1162 | 1 | 6484.0751 | age_years | wear-out (k>1)
68475 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 58 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 67.3201 | age_years | wear-out (k>1)
68476 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 58 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 67.3201 | age_years | wear-out (k>1)
68493 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2020.8182 | 0 | 3.3 | 3.3 | N | N | industrial | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0037879 | ba_g+dur_band+vintage_g | 0 | 0.0037879 | 87.5 | FULL_OUTAGE | inf | 0.044437 | 6.1162 | 1 | 24.3258 | age_years | wear-out (k>1)
68496 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 60 | 120 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 1722 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 239.3657 | age_years | wear-out (k>1)
68522 | 1 | 9 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 0 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
68523 | 1 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 0 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
68524 | 1 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 3 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 12.1202 | age_years | wear-out (k>1)
68525 | 1 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 0 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
68547 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 94 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 30.4819 | age_years | wear-out (k>1)
68548 | 1 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 0.7 | 2.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 52 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 16.8623 | age_years | wear-out (k>1)
68576 | 0 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 260 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 6390 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 3314.417 | age_years | wear-out (k>1)
68577 | 0 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 40 | 160 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 4343.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 2252.9218 | age_years | wear-out (k>1)
68596 | 0 | 1 | 2.5-4.5h | LIB | CS | PACE | 2025 | 0 | 200 | 800 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 2851 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 1478.7798 | age_years | wear-out (k>1)
68605 | 2 | 24 | 2.5-4.5h | LIB | CS | HECO | 2021 | 1 | 0.5 | 1.3 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0.0078125 | ba_g+dur_band+vintage_g | 0 | 0.0078125 | 9 | FULL_OUTAGE | inf | 0.08949 | 6.1162 | 1 | 5.1605 | age_years | wear-out (k>1)
68611 | 0 | 10 | 1.5-2.5h | LIB | CS | CEA | 2024 | 0 | 40 | 80 | N | N | coastal | other | LIB | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 1 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 1.529 | age_years | wear-out (k>1)
68613 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 228.7 | 228.7 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 5939 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 4383.9425 | age_years | wear-out (k>1)
68617 | 0 | 2 | 2.5-4.5h | LIB | CT | PNM | 2025 | 0 | 100 | 400 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 11974.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 6211.0307 | age_years | wear-out (k>1)
68679 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 45.5 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 33.7318 | age_years | wear-out (k>1)
68680 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 50 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 37.0679 | age_years | wear-out (k>1)
68683 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 337.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 46.914 | age_years | wear-out (k>1)
68684 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 386.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 53.7252 | age_years | wear-out (k>1)
68685 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 12.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 216 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 159.4429 | age_years | wear-out (k>1)
68686 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 33 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 4.5871 | age_years | wear-out (k>1)
68687 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 43.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 6.0467 | age_years | wear-out (k>1)
68742 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 50 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 37.0679 | age_years | wear-out (k>1)
68743 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3.3 | 3.3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 119 | FULL_OUTAGE | inf | 0.11415 | 6.1162 | 1 | 88.2215 | age_years | wear-out (k>1)
68773 | 2 | 23 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 2.8 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.01295 | ba_g+dur_band+vintage_g | 0 | 0.01295 | 68.5 | FULL_OUTAGE | inf | 0.14392 | 6.1162 | 1 | 65.1045 | age_years | wear-out (k>1)
68801 | 0 | 3 | 2.5-4.5h | LIB | CS | WALC | 2025 | 0 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 239 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 123.9665 | age_years | wear-out (k>1)
68802 | 0 | 8 | <1.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 65 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 8224 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 7319.2636 | age_years | wear-out (k>1)
68809 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 220 | 440 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 189 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 26.2718 | age_years | wear-out (k>1)
68816 | 1 | 20 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 2.6 | 5.3 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0.055046 | ba_g+dur_band+vintage_g | 0 | 0.055046 | 21.5 | FULL_OUTAGE | inf | 0.48343 | 6.1162 | 1 | 86.8612 | age_years | wear-out (k>1)
68842 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 7672 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 5663.1768 | age_years | wear-out (k>1)
68868 | 0 | 5 | 2.5-4.5h | LIB | CS | PNM | 2025 | 1 | 50 | 200 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5754 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 2984.5313 | age_years | wear-out (k>1)
68874 | 0 | 8 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 13 | 45 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 1183 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 955.9537 | age_years | wear-out (k>1)
68875 | 0 | 7 | 2.5-4.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 22.4 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.011494 | ba_g+dur_band+vintage_g | 0 | 0.011494 | 334 | FULL_OUTAGE | inf | 0.12884 | 6.1162 | 1 | 281.7669 | age_years | wear-out (k>1)
68878 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 165 | 165 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 6053 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 4468.0929 | age_years | wear-out (k>1)
68879 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 5874 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 816.5123 | age_years | wear-out (k>1)
68891 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 84 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 27.2391 | age_years | wear-out (k>1)
68895 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 236.3 | 236.3 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.00089127 | ba_g+dur_band+vintage_g | 0 | 0.00089127 | 4965.5 | FULL_OUTAGE | inf | 0.010638 | 6.1162 | 1 | 324.8126 | age_years | wear-out (k>1)
68896 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 123.3 | 123 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 3260.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 2406.7763 | age_years | wear-out (k>1)
68906 | 0 | 1 | <1.5h | LIB | CS | DOPD | 2025 | 1 | 200 | 200 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 9840 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 8757.4846 | age_years | wear-out (k>1)
68912 | 0 | 6 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 50 | 200 | Y | Y | inland | ERCO | LIB | CS | 2024+ | 1 | 1 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 1967 | FULL_OUTAGE | inf | 0.12376 | 6.1162 | 1 | 1589.4852 | age_years | wear-out (k>1)
68997 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 0.7 | 2.6 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0044183 | ba_g+dur_band+vintage_g | 0 | 0.0044183 | 55 | FULL_OUTAGE | inf | 0.051638 | 6.1162 | 1 | 17.8352 | age_years | wear-out (k>1)
69023 | 0 | 2 | 1.5-2.5h | LIB | CS | CPLE | 2025 | 0 | 100 | 200 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.003861 | ba_g+dur_band+vintage_g | 0 | 0.003861 | 2900.5 | FULL_OUTAGE | inf | 0.045275 | 6.1162 | 1 | 821.9319 | age_years | wear-out (k>1)
69026 | 0 | 2 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 283.2 | 283.2 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 13663 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 10085.5037 | age_years | wear-out (k>1)
69045 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 10338 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 1437.0283 | age_years | wear-out (k>1)
69122 | 0 | 4 | <1.5h | LIB | CS | PSCO | 2025 | 0 | 100 | 100 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 11212 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 9978.5485 | age_years | wear-out (k>1)
69128 | 0 | 12 | 1.5-2.5h | LIB | CS | PJM | 2023 | 0 | 1.1 | 2.3 | N | Y | coastal | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.015814 | dur_band+climate_region | 0 | 0.015814 | 58 | FULL_OUTAGE | inf | 0.17285 | 6.1162 | 1 | 67.3201 | age_years | wear-out (k>1)
69171 | 0 | 2 | 2.5-4.5h | LIB | CS | DUK | 2025 | 0 | 50 | 200 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5839.5 | FULL_OUTAGE | inf | 0.081309 | 6.1162 | 1 | 3028.8792 | age_years | wear-out (k>1)
69187 | 0 | 1 | 1.5-2.5h | LIB | CS | TEC | 2019 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.027174 | ba_g+dur_band+vintage_g | 0 | 0.027174 | 24 | FULL_OUTAGE | inf | 0.27826 | 6.1162 | 1 | 47.8659 | age_years | wear-out (k>1)
69190 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 4 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 1.6728 | age_years | wear-out (k>1)
69191 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 8 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 3.3456 | age_years | wear-out (k>1)
69210 | 0 | 12 | 1.5-2.5h | LIB | CS | PGE | 2024 | 1 | 1 | 2 | Y | N | industrial | other | LIB | CS | 2024+ | 1 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 6.5 | FULL_OUTAGE | inf | 0.2212 | 6.1162 | 1 | 9.9388 | age_years | wear-out (k>1)
69244 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 58.3 | 114 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 2411.5 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 335.2093 | age_years | wear-out (k>1)
69250 | 0 | 8 | <1.5h | NAB | CS | FPC | 2025 | 0 | 5 | 5 | N | Y | inland | other | other | CS | 2024+ | 0 | 1 | 0.012126 | dur_band+climate_region | 0 | 0.012126 | 424 | FULL_OUTAGE | inf | 0.13542 | 6.1162 | 1 | 377.355 | age_years | wear-out (k>1)
69288 | 0 | 10 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.3 | 0.6 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.005698 | ba_g+dur_band+vintage_g | 0 | 0.005698 | 7.5 | FULL_OUTAGE | inf | 0.066091 | 6.1162 | 1 | 3.1365 | age_years | wear-out (k>1)
69298 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 300 | 680 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 23114 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 3212.9496 | age_years | wear-out (k>1)
69300 | 1 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 0 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
69301 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 20 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 14.7632 | age_years | wear-out (k>1)
69302 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 88 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 64.9582 | age_years | wear-out (k>1)
69331 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 8 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 5.9053 | age_years | wear-out (k>1)
69333 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 20 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 14.7632 | age_years | wear-out (k>1)
69334 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 2.3 | 4.5 | N | N | inland | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 18 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 11.8484 | age_years | wear-out (k>1)
69344 | 1 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 2 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 1.4763 | age_years | wear-out (k>1)
69345 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 189.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 139.8816 | age_years | wear-out (k>1)
69346 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 187 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 138.0362 | age_years | wear-out (k>1)
69347 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 221.5 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 163.5028 | age_years | wear-out (k>1)
69348 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 47 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 34.6936 | age_years | wear-out (k>1)
69349 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 39 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 28.7883 | age_years | wear-out (k>1)
69350 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 23.2 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 368.5 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 72.8998 | age_years | wear-out (k>1)
69353 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 19.8 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0026954 | ba_g+dur_band+vintage_g | 0 | 0.0026954 | 109.5 | FULL_OUTAGE | inf | 0.031828 | 6.1162 | 1 | 21.6622 | age_years | wear-out (k>1)
69358 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 11.3 | 11.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.016 | ba_g+dur_band+vintage_g | 0 | 0.016 | 0 | FULL_OUTAGE | inf | 0.17469 | 6.1162 | 1 | 0 | age_years | wear-out (k>1)
69365 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 206 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 152.0613 | age_years | wear-out (k>1)
69366 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 122 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 90.0557 | age_years | wear-out (k>1)
69407 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 75 | 75 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 2149 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 1586.3096 | age_years | wear-out (k>1)
69411 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 300 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 197.4736 | age_years | wear-out (k>1)
69413 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 391 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 257.374 | age_years | wear-out (k>1)
69414 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 180 | 360 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 3630 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 504.5863 | age_years | wear-out (k>1)
69415 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0 | 0.0089686 | 437 | FULL_OUTAGE | inf | 0.10203 | 6.1162 | 1 | 287.6533 | age_years | wear-out (k>1)
69454 | 0 | 9 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 561 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 77.9815 | age_years | wear-out (k>1)
69456 | 0 | 8 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 418 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 58.1039 | age_years | wear-out (k>1)
69459 | 0 | 5 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 369 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 51.2927 | age_years | wear-out (k>1)
69460 | 0 | 12 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0018939 | ba_g+dur_band+vintage_g | 0 | 0.0018939 | 478 | FULL_OUTAGE | inf | 0.022471 | 6.1162 | 1 | 66.4441 | age_years | wear-out (k>1)
69576 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 13.7 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.010057 | ba_g+dur_band+vintage_g | 0 | 0.010057 | 215 | FULL_OUTAGE | inf | 0.11369 | 6.1162 | 1 | 158.7048 | age_years | wear-out (k>1)
69727 | 1 | 12 | <1.5h | LIB | CS | PJM | 2022 | 1 | 10.1 | 10.1 | N | Y | inland | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.0092593 | ba_g+dur_band+vintage_g | 0 | 0.0092593 | 98 | FULL_OUTAGE | inf | 0.10516 | 6.1162 | 1 | 66.5986 | age_years | wear-out (k>1)
69803 | 1 | 7 | <1.5h | LIB | CT | NYIS | 2025 | 0 | 4.6 | 4.6 | N | N | coastal | NYIS | LIB | CT | 2024+ | 0 | 0 | 0.013793 | dur_band+climate_region | 0 | 0.013793 | 126 | FULL_OUTAGE | inf | 0.15254 | 6.1162 | 1 | 127.5543 | age_years | wear-out (k>1)
141 | 2 | 52 | 2.5-4.5h | LIB | CS | SRP | 2021 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 1432 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 74.8404 | age_years | random (k~1)
260 | 1 | 55 | 2.5-4.5h | LIB | BL | CISO | 2021.9333 | 1 | 750 | 3000 | Y | N | coastal | CISO | LIB | BL | 2022-23 | 1 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 0 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
389 | 3 | 84 | <1.5h | LIB | BL | IID | 2016 | 0 | 30 | 20 | N | Y | arid | other | LIB | BL | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 379.5 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 16.4674 | age_years | random (k~1)
645 | 0 | 33 | 1.5-2.5h | LIB | CS | TEC | 2017 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 5 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0.16361 | age_years | random (k~1)
1016 | 0 | 48 | <1.5h | LIB | CS | CPLE | 2019 | 1 | 0.5 | 0.5 | N | N | inland | CPLE | LIB | CS | <=2019 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 20.5 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0.81484 | age_years | random (k~1)
1482 | 0 | 33 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 585 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 15.6538 | age_years | random (k~1)
1507 | 1 | 84 | <1.5h | LIB | CS | ISNE | 2016 | 0 | 16.7 | 10.9 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.004386 | ba_g+dur_band+vintage_g | 0 | 0.004386 | 288 | PARTIAL_AVAILABILITY | inf | 0.051271 | 2.3101 | 0.14479 | 5.07 | age_years | random (k~1)
1615 | 0 | 36 | >4.5h | LIB | BL | ISNE | 2019 | 0 | 6 | 48 | N | N | coastal | ISNE | LIB | BL | <=2019 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 1 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 0.053517 | age_years | random (k~1)
1682 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 3 | 6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 27.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.79409 | age_years | random (k~1)
2324 | 0 | 23 | <1.5h | LIB | CS | NEVP | 2023 | 0 | 220 | 220 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 13845.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 5.5573 | age_years | random (k~1)
2830 | 1 | 84 | <1.5h | LIB | CS | PJM | 2015 | 1 | 4 | 1.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 91.5 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 4.1373 | age_years | random (k~1)
6304 | 0 | 36 | <1.5h | LIB | CT |  | 2015 | 1 | 1.2 | 1 | N | N | coastal | other | LIB | CT | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 4 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0.17357 | age_years | random (k~1)
6377 | 0 | 36 | <1.5h | LIB | CS | PJM | 2017 | 1 | 1 | 1 | Y | N | coastal | PJM | LIB | CS | <=2019 | 1 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 3 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 0.13565 | age_years | random (k~1)
8063 | 2 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 269.1 | 263 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 2501.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 44.7437 | age_years | random (k~1)
10156 | 0 | 34 | <1.5h | LIB | CS | CISO | 2023 | 0 | 16 | 16 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 13.5 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 1.0066 | age_years | random (k~1)
10444 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 69 | 69 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 4203 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 134.9596 | age_years | random (k~1)
10493 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 613.5 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 16.4164 | age_years | random (k~1)
50064 | 0 | 24 | <1.5h | LIB | CS | CISO | 2022 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 12 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 0.89471 | age_years | random (k~1)
50300 | 0 | 84 | <1.5h | LIB | BL | CISO | 2019.5 | 0 | 40 | 40 | N | Y | inland | CISO | LIB | BL | <=2019 | 0 | 1 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 1235.5 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 49.1093 | age_years | random (k~1)
54134 | 1 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 0 | 20 | 20 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 729.5 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 55.4556 | age_years | random (k~1)
54296 | 0 | 76 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.3 | 0.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 1 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 0.067345 | age_years | random (k~1)
54639 | 2 | 24 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 14 | 14 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 751.5 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 30.4683 | age_years | random (k~1)
55370 | 0 | 36 | <1.5h | LIB | CT | PJM | 2016 | 0 | 10.4 | 10.4 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
56961 | 1 | 84 | <1.5h | LIB | BL | ERCO | 2012 | 0 | 36 | 13.6 | N | N | arid | ERCO | LIB | BL | <=2019 | 0 | 0 | 0.014563 | ba_g+dur_band+vintage_g | 0 | 0.014563 | 227.5 | PARTIAL_AVAILABILITY | inf | 0.16034 | 2.3101 | 0.14479 | 13.2981 | age_years | random (k~1)
56981 | 1 | 84 | <1.5h | LIB | CS | ERCO | 2018 | 1 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.014563 | ba_g+dur_band+vintage_g | 0 | 0.014563 | 43.5 | PARTIAL_AVAILABILITY | inf | 0.16034 | 2.3101 | 0.14479 | 2.5427 | age_years | random (k~1)
56984 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2018 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.014563 | ba_g+dur_band+vintage_g | 0 | 0.014563 | 68 | PARTIAL_AVAILABILITY | inf | 0.16034 | 2.3101 | 0.14479 | 3.9748 | age_years | random (k~1)
57206 | 3 | 36 | 1.5-2.5h | LIB | CS |  | 2022 | 0 | 46.5 | 93 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.034286 | ba_g+dur_band+vintage_g | 0 | 0.034286 | 268.5 | PARTIAL_AVAILABILITY | inf | 0.3373 | 2.3101 | 0.14479 | 36.9498 | age_years | random (k~1)
57242 | 3 | 30 | 2.5-4.5h | LIB | CS |  | 2022 | 1 | 39 | 156 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 3159 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 402.9016 | age_years | random (k~1)
57325 | 1 | 84 | <1.5h | LIB | CS | PJM | 2014 | 1 | 20 | 8.3 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 446 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 20.1663 | age_years | random (k~1)
57447 | 2 | 78 | <1.5h | LIB | CS | PJM | 2011 | 0 | 16 | 16 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 628.5 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 28.4182 | age_years | random (k~1)
57560 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 19 | 76 | Y | N | arid | AZPS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1891 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.75901 | age_years | random (k~1)
57561 | 1 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 1278.5 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 217.852 | age_years | random (k~1)
57562 | 1 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 1289 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 219.6412 | age_years | random (k~1)
57563 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 16 | 48 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 1141 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 194.4225 | age_years | random (k~1)
57583 | 2 | 84 | <1.5h | NIB | BL |  | 2003 | 0 | 40 | 11 | N | Y | inland | other | other | BL | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 17 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0.73767 | age_years | random (k~1)
57584 | 2 | 78 | 1.5-2.5h | LIB | CS | CISO | 2015 | 0 | 2.5 | 5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 13.5 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 0.90916 | age_years | random (k~1)
57996 | 2 | 36 | <1.5h | LIB | CS |  | 2012 | 0 | 11 | 4.4 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 106.5 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 4.6213 | age_years | random (k~1)
57997 | 1 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 35 | 105 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 2396 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 408.2702 | age_years | random (k~1)
58236 | 1 | 62 | 1.5-2.5h | LIB | CS | MISO | 2020 | 1 | 0.3 | 0.6 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
58256 | 0 | 41 | >4.5h | NAB | CS | PNM | 2012 | 1 | 1.8 | 8.3 | N | N | inland | other | other | CS | <=2019 | 0 | 0 | 0.0043103 | dur_band+climate_region | 0 | 0.0043103 |  | PARTIAL_AVAILABILITY | inf | 0.050409 | 2.3101 | 0.14479 |  | age_years | random (k~1)
58383 | 2 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 14 | 42 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 1015.5 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 173.0377 | age_years | random (k~1)
58405 | 0 | 36 | <1.5h | LIB | CS |  | 2012 | 1 | 3 | 3 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 0.5 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0.021696 | age_years | random (k~1)
58462 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 230 | 920 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 23132.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 1737.5235 | age_years | random (k~1)
58585 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2017 | 1 | 0.5 | 1 | N | N | industrial | CISO | LIB | CS | <=2019 | 0 | 0 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 2 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 0.13469 | age_years | random (k~1)
58639 | 0 | 48 | <1.5h | LIB | CS |  | 2015 | 1 | 6 | 4.6 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 |  | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 |  | age_years | random (k~1)
59020 | 1 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 32 | 96 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 2334.5 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 397.7908 | age_years | random (k~1)
59118 | 1 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 16.4 | 32.8 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 548.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 16.6785 | age_years | random (k~1)
59150 | 1 | 36 | <1.5h | LIB | CS | CISO | 2021 | 1 | 75 | 75 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 7373 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 369.9206 | age_years | random (k~1)
59256 | 1 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 2 | 14 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 |  | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 |  | age_years | random (k~1)
59257 | 0 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 4 | 28 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 |  | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 |  | age_years | random (k~1)
59444 | 2 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 10 | 30 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 840.5 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 143.2183 | age_years | random (k~1)
59871 | 0 | 13 | <1.5h | LIB | CS | CISO | 2024 | 1 | 150 | 150 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 12527 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 402.2456 | age_years | random (k~1)
59939 | 2 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021.4861 | 1 | 72 | 288 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 6176.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 463.928 | age_years | random (k~1)
59949 | 1 | 70 | <1.5h | LIB | BL | PJM | 2015 | 0 | 11 | 5 | N | N | inland | PJM | LIB | BL | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 |  | age_years | random (k~1)
59957 | 0 | 84 | <1.5h | LIB | CT | PJM | 2014.75 | 1 | 36 | 13.5 | Y | Y | inland | PJM | LIB | CT | <=2019 | 1 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
59959 | 1 | 34 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 |  | age_years | random (k~1)
59960 | 0 | 30 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 |  | age_years | random (k~1)
59993 | 3 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 10 | 40 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 13 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 1.4132 | age_years | random (k~1)
60014 | 2 | 48 | 1.5-2.5h | LIB | CS | FPL | 2021 | 1 | 409 | 900 | N | Y | coastal | other | LIB | CS | 2020-21 | 0 | 1 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 6521 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 678.5826 | age_years | random (k~1)
60016 | 0 | 74 | <1.5h | LIB | CS | BPAT | 2015.5 | 0 | 2 | 1 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 0 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60061 | 2 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 4 | 16 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 110.5 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 12.0121 | age_years | random (k~1)
60092 | 1 | 57 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 12058.5 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 545.8674 | age_years | random (k~1)
60093 | 0 | 36 | >4.5h | LIB | CS | CISO | 2021 | 1 | 63 | 301.2 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 7022 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 317.8738 | age_years | random (k~1)
60094 | 1 | 51 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 11924 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 539.7788 | age_years | random (k~1)
60095 | 0 | 36 | <1.5h | LIB | CS | CISO | 2022 | 1 | 47 | 47 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 4070 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 303.4572 | age_years | random (k~1)
60123 | 2 | 76 | 2.5-4.5h | LIB | CS | ERCO | 2019 | 1 | 9.9 | 42 | N | Y | arid | ERCO | LIB | CS | <=2019 | 0 | 1 | 0.017874 | dur_band+climate_region | 0 | 0.017874 | 29.5 | PARTIAL_AVAILABILITY | inf | 0.19305 | 2.3101 | 0.14479 | 2.1164 | age_years | random (k~1)
60231 | 1 | 36 | <1.5h | LIB | CS | CISO | 2016 | 1 | 2 | 2 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.011724 | dur_band+climate_region | 0 | 0.011724 | 25 | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 | 1.1765 | age_years | random (k~1)
60233 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 88 | 352 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 8494.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 638.0371 | age_years | random (k~1)
60249 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2020 | 0 | 1 | 2 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 0 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60297 | 0 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 10 | 4.1 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 75.5 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 3.4138 | age_years | random (k~1)
60299 | 0 | 24 | <1.5h | LIB | CS | PJM | 2016 | 1 | 7 | 7 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 |  | age_years | random (k~1)
60316 | 0 | 24 | <1.5h | LIB | CS | PJM | 2022 | 1 | 40 | 48 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.018519 | ba_g+dur_band+vintage_g | 0 | 0.018519 | 308 | PARTIAL_AVAILABILITY | inf | 0.19926 | 2.3101 | 0.14479 | 22.8934 | age_years | random (k~1)
60390 | 1 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 31.5 | 12.5 | N | Y | inland | PJM | LIB | CT | <=2019 | 0 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60441 | 1 | 67 | <1.5h | LIB | BL | PGE | 2013 | 1 | 5 | 5 | N | N | inland | other | LIB | BL | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 |  | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 |  | age_years | random (k~1)
60444 | 0 | 36 | 1.5-2.5h | LIB | CT | PSEI | 2016 | 0 | 2 | 4.4 | Y | Y | inland | other | LIB | CT | <=2019 | 1 | 1 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 0 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60467 | 1 | 14 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 41 | 164 | Y | N | arid | AZPS | LIB | CS | 2022-23 | 1 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 3200.5 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 545.3543 | age_years | random (k~1)
60491 | 0 | 64 | <1.5h | LIB | CT | LDWP | 2019 | 1 | 1.5 | 1.5 | N | Y | arid | other | LIB | CT | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 0 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60506 | 0 | 48 | <1.5h | NAB | BL | ERCO | 2010 | 1 | 4 | 4 | N | N | arid | ERCO | other | BL | <=2019 | 0 | 0 | 0.014563 | ba_g+dur_band+vintage_g | 0 | 0.014563 |  | PARTIAL_AVAILABILITY | inf | 0.16034 | 2.3101 | 0.14479 |  | age_years | random (k~1)
60518 | 0 | 72 | 1.5-2.5h | LIB | CS | ISNE | 2015 | 1 | 2 | 3.4 | N | Y | inland | ISNE | LIB | CS | <=2019 | 0 | 1 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 0 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60546 | 3 | 36 | 2.5-4.5h | LIB | CS |  | 2017 | 1 | 13 | 52 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 1150.5 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 125.0671 | age_years | random (k~1)
60562 | 2 | 71 | 2.5-4.5h | LIB | OT | ISNE | 2018 | 1 | 1 | 4 | N | Y | inland | ISNE | LIB | other | <=2019 | 0 | 1 | 0.0083565 | ba_g+dur_band+vintage_g | 0 | 0.0083565 | 52.5 | PARTIAL_AVAILABILITY | inf | 0.095415 | 2.3101 | 0.14479 | 1.7609 | age_years | random (k~1)
60565 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2013.3333 | 1 | 1.5 | 4.5 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 0 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60566 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2015 | 1 | 1 | 2 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 1082.5 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 72.9014 | age_years | random (k~1)
60567 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2015 | 1 | 2 | 6 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 0 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60568 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2014 | 1 | 1 | 3 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 0 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60569 | 1 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 7.5 | 30 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 405 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 13.5465 | age_years | random (k~1)
60570 | 2 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 0 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60607 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2017 | 1 | 0.8 | 3.3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0083565 | ba_g+dur_band+vintage_g | 0 | 0.0083565 | 3.5 | PARTIAL_AVAILABILITY | inf | 0.095415 | 2.3101 | 0.14479 | 0.11739 | age_years | random (k~1)
60609 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2016 | 1 | 0.8 | 3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0083565 | ba_g+dur_band+vintage_g | 0 | 0.0083565 | 0 | PARTIAL_AVAILABILITY | inf | 0.095415 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60641 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 10 | 40 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 758.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 56.9723 | age_years | random (k~1)
60649 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 165.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 11.105 | age_years | random (k~1)
60654 | 1 | 48 | 2.5-4.5h | LIB | CS | WALC | 2021 | 1 | 90 | 360 | Y | Y | arid | other | LIB | CS | 2020-21 | 1 | 1 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 7749.5 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 405.0109 | age_years | random (k~1)
60656 | 0 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 20 | 7.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 2935 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 132.7089 | age_years | random (k~1)
60660 | 0 | 33 | <1.5h | LIB | CS | PJM | 2016 | 0 | 6 | 2 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 593 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 26.8131 | age_years | random (k~1)
60661 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2016 | 0 | 20 | 80 | Y | Y | arid | CISO | LIB | CS | <=2019 | 1 | 1 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 1040.5 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 34.8029 | age_years | random (k~1)
60690 | 3 | 84 | <1.5h | LIB | CS | ERCO | 2017 | 0 | 30 | 12.6 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.014563 | ba_g+dur_band+vintage_g | 0 | 0.014563 | 463.5 | PARTIAL_AVAILABILITY | inf | 0.16034 | 2.3101 | 0.14479 | 27.0931 | age_years | random (k~1)
60698 | 1 | 65 | <1.5h | LIB | CS | CISO | 2020 | 1 | 20 | 9 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 14 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 0.70241 | age_years | random (k~1)
60760 | 0 | 24 | 2.5-4.5h | LIB | BL | CISO | 2016 | 0 | 2 | 8 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 |  | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 |  | age_years | random (k~1)
60815 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2017 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.004386 | ba_g+dur_band+vintage_g | 0 | 0.004386 | 6.5 | PARTIAL_AVAILABILITY | inf | 0.051271 | 2.3101 | 0.14479 | 0.11443 | age_years | random (k~1)
60906 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.1 | 6.1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 23 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.40848 | age_years | random (k~1)
60959 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2017 | 1 | 2 | 3.9 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 7 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.12432 | age_years | random (k~1)
60974 | 0 | 36 | <1.5h | LIB | CS | LDWP | 2017 | 1 | 2 | 1 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 0 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
60996 | 0 | 36 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 2.5 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 74 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 3.211 | age_years | random (k~1)
61068 | 1 | 72 | >4.5h | LIB | CS |  | 2018 | 1 | 20 | 100 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 1857 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 99.3814 | age_years | random (k~1)
61098 | 2 | 55 | <1.5h | LIB | CS | NEVP | 2021 | 1 | 25 | 25 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 2105 | PARTIAL_AVAILABILITY | inf | 0.10609 | 2.3101 | 0.14479 | 78.9628 | age_years | random (k~1)
61107 | 0 | 36 | 2.5-4.5h | FLB | CS | CISO | 2017 | 1 | 2 | 8 | N | Y | coastal | CISO | other | CS | <=2019 | 0 | 1 | 0.0083333 | ba_g+dur_band+vintage_g | 0 | 0.0083333 | 106 | PARTIAL_AVAILABILITY | inf | 0.095163 | 2.3101 | 0.14479 | 3.5455 | age_years | random (k~1)
61168 | 0 | 14 | 2.5-4.5h | LIB | CS | LDWP | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 14026 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 397.8613 | age_years | random (k~1)
61169 | 0 | 6 | 2.5-4.5h | LIB | CS | LDWP | 2025 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 13805 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 391.5924 | age_years | random (k~1)
61186 | 0 | 32 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 1 | 1.1 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 2 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 0.081087 | age_years | random (k~1)
61197 | 1 | 84 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 10 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 6 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0.26035 | age_years | random (k~1)
61204 | 2 | 60 | 2.5-4.5h | LIB | BL | CISO | 2021 | 0 | 100 | 400 | Y | N | coastal | CISO | LIB | BL | 2020-21 | 1 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 7946.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 596.8759 | age_years | random (k~1)
61334 | 0 | 36 | >4.5h | LIB | CT | MISO | 2019 | 1 | 1 | 4.6 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.0043103 | dur_band+climate_region | 0 | 0.0043103 | 0 | PARTIAL_AVAILABILITY | inf | 0.050409 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61365 | 0 | 31 | <1.5h | LIB | CS | CISO | 2023 | 0 | 40 | 40 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 3338 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 248.8796 | age_years | random (k~1)
61366 | 1 | 54 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 2929.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 220.04 | age_years | random (k~1)
61431 | 0 | 84 | <1.5h | LIB | CS | LDWP | 2018 | 1 | 20 | 10 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 337 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 14.6232 | age_years | random (k~1)
61439 | 0 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2017 | 1 | 1 | 2.2 | Y | Y | arid | other | LIB | CS | <=2019 | 1 | 1 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 0 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61473 | 0 | 36 | <1.5h | LIB | BL | PJM | 2015 | 1 | 1 | 1 | Y | Y | inland | PJM | LIB | BL | <=2019 | 1 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61552 | 0 | 22 | <1.5h | LIB | CS | PJM | 2024 | 1 | 6 | 6 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 455 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 18.0856 | age_years | random (k~1)
61661 | 1 | 84 | <1.5h | LIB | BL | CISO | 2018 | 0 | 40 | 38 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.011724 | dur_band+climate_region | 0 | 0.011724 | 1280.5 | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 | 60.258 | age_years | random (k~1)
61667 | 0 | 9 | 1.5-2.5h | LIB | CS | TEC | 2025 | 1 | 40 | 80 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 447 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 18.6892 | age_years | random (k~1)
61678 | 5 | 84 | 2.5-4.5h | LIB | CS | SRP | 2018 | 1 | 10 | 40 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 1032 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 112.1853 | age_years | random (k~1)
61721 | 2 | 72 | >4.5h | LIB | CS | CISO | 2019 | 1 | 1 | 6.9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 16.5 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 1.5694 | age_years | random (k~1)
61722 | 0 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.5 | 33.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 455 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 43.2766 | age_years | random (k~1)
61723 | 0 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.8 | 34.8 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 378 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 35.9529 | age_years | random (k~1)
61730 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 1 | 1 | 2 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 19.5 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.34632 | age_years | random (k~1)
61737 | 0 | 12 | <1.5h | LIB | CS | PJM | 2021 | 1 | 6.2 | 6.2 | N | Y | coastal | PJM | LIB | CS | 2020-21 | 0 | 1 | 0.011724 | dur_band+climate_region | 0 | 0.011724 |  | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 |  | age_years | random (k~1)
61739 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2017 | 0 | 1 | 1.3 | Y | N | industrial | NYIS | LIB | CS | <=2019 | 1 | 0 | 0.010373 | dur_band | 0 | 0.010373 | 0 | PARTIAL_AVAILABILITY | inf | 0.11705 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61741 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2018 | 1 | 1.5 | 3 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61763 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 647.5 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 33.8402 | age_years | random (k~1)
61795 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2020 | 1 | 1 | 2 | Y | N | industrial | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 2.5 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 0.16865 | age_years | random (k~1)
61801 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 2194.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 129.7239 | age_years | random (k~1)
61803 | 0 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 10 | 40 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 705 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 41.6748 | age_years | random (k~1)
61861 | 0 | 84 | 2.5-4.5h | LIB | BL | SRP | 2019 | 1 | 10 | 40 | N | N | arid | other | LIB | BL | <=2019 | 0 | 0 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 0 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61891 | 4 | 83 | <1.5h | LIB | CS | PJM | 2018 | 0 | 19.8 | 19.8 | Y | N | inland | PJM | LIB | CS | <=2019 | 1 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 2740 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 123.8917 | age_years | random (k~1)
61892 | 1 | 83 | <1.5h | LIB | CS | PJM | 2019 | 0 | 19.8 | 19.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 2919 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 131.9854 | age_years | random (k~1)
61901 | 0 | 36 | 1.5-2.5h | LIB | CS | TVA | 2017 | 1 | 1 | 2 | Y | N | inland | other | LIB | CS | <=2019 | 1 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 0 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61909 | 0 | 36 | <1.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 1 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 0 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61923 | 0 | 36 | <1.5h | LIB | CS | PJM | 2018 | 0 | 1 | 1 | N | N | coastal | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 127 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 5.7424 | age_years | random (k~1)
61925 | 1 | 84 | <1.5h | LIB | CS | PNM | 2018 | 0 | 1 | 1 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 4.5 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0.19527 | age_years | random (k~1)
61956 | 1 | 36 | 1.5-2.5h | LIB | CS | SCEG | 2018 | 1 | 4 | 8 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 23 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0.75258 | age_years | random (k~1)
61990 | 0 | 36 | 1.5-2.5h | LIB | CT | MISO | 2017 | 1 | 0.3 | 0.5 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
61995 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.5 | 0.9 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 0 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62027 | 0 | 36 | 1.5-2.5h | OTH | CS | PJM | 2016 | 1 | 1 | 2 | Y | Y | coastal | PJM | other | CS | <=2019 | 1 | 1 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 0 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62147 | 1 | 36 | <1.5h | LIB | CS | NYIS | 2019 | 0 | 20 | 8.4 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 2179 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 86.612 | age_years | random (k~1)
62175 | 1 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 200 | 800 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 17609 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1326.7345 | age_years | random (k~1)
62219 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 1 | 3 | 3 | N | N | inland | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.004386 | ba_g+dur_band+vintage_g | 0 | 0.004386 | 19.5 | PARTIAL_AVAILABILITY | inf | 0.051271 | 2.3101 | 0.14479 | 0.34328 | age_years | random (k~1)
62235 | 0 | 13 | 2.5-4.5h | LIB | CS | SCEG | 2024 | 1 | 66 | 198 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1632.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 46.3075 | age_years | random (k~1)
62248 | 0 | 25 | >4.5h | LIB | CS | NEVP | 2023 | 1 | 75 | 375 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 8731 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 395.2372 | age_years | random (k~1)
62257 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 0 | 2 | 4.2 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 26.5 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.47064 | age_years | random (k~1)
62373 | 0 | 84 | 2.5-4.5h | LIB | CS | WACM | 2018 | 0 | 4 | 16 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 0 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62381 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0.0083565 | ba_g+dur_band+vintage_g | 0 | 0.0083565 | 94 | PARTIAL_AVAILABILITY | inf | 0.095415 | 2.3101 | 0.14479 | 3.1529 | age_years | random (k~1)
62382 | 1 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0.0083565 | ba_g+dur_band+vintage_g | 0 | 0.0083565 | 92 | PARTIAL_AVAILABILITY | inf | 0.095415 | 2.3101 | 0.14479 | 3.0858 | age_years | random (k~1)
62383 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0.0083565 | ba_g+dur_band+vintage_g | 0 | 0.0083565 | 105.5 | PARTIAL_AVAILABILITY | inf | 0.095415 | 2.3101 | 0.14479 | 3.5386 | age_years | random (k~1)
62441 | 1 | 24 | <1.5h | LIB | CS | CISO | 2020 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 48.5 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 2.4334 | age_years | random (k~1)
62444 | 1 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 18 | 12.1 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 1974 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 89.2563 | age_years | random (k~1)
62490 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 558 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 29.1627 | age_years | random (k~1)
62494 | 0 | 2 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 1 | 252 | 1008 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 8863.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 251.4219 | age_years | random (k~1)
62497 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 9 | 36 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 0 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62499 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 6 | 24 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 0 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62541 | 0 | 34 | 1.5-2.5h | LIB | CS | FPC | 2023 | 1 | 17.3 | 36 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.034286 | ba_g+dur_band+vintage_g | 0 | 0.034286 | 160 | PARTIAL_AVAILABILITY | inf | 0.3373 | 2.3101 | 0.14479 | 22.0185 | age_years | random (k~1)
62561 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 63.3 | 108.6 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 0 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62562 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 63.3 | 81 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 0 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62564 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 182.5 | 730 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 0 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62569 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 4 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 0 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62585 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 0 | 3 | 3 | N | N | coastal | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.004386 | ba_g+dur_band+vintage_g | 0 | 0.004386 | 16.5 | PARTIAL_AVAILABILITY | inf | 0.051271 | 2.3101 | 0.14479 | 0.29047 | age_years | random (k~1)
62604 | 0 | 41 | 1.5-2.5h | LIB | BL | ISNE | 2022 | 0 | 25 | 38 | N | N | coastal | ISNE | LIB | BL | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 64.5 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 1.7259 | age_years | random (k~1)
62609 | 1 | 76 | <1.5h | LIB | CS | ERCO | 2019 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | <=2019 | 1 | 1 | 0.014563 | ba_g+dur_band+vintage_g | 0 | 0.014563 | 156.5 | PARTIAL_AVAILABILITY | inf | 0.16034 | 2.3101 | 0.14479 | 9.1479 | age_years | random (k~1)
62644 | 0 | 80 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 5 | 10 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 42.5 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.7548 | age_years | random (k~1)
62652 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.3 | 6.6 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 98.5 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 1.7494 | age_years | random (k~1)
62682 | 0 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 0 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62683 | 0 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 0 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62695 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 19 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.54865 | age_years | random (k~1)
62714 | 0 | 36 | <1.5h | LIB | CS |  | 2019 | 0 | 1 | 0.9 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 11 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0.47732 | age_years | random (k~1)
62733 | 0 | 36 | >4.5h | LIB | BL | NYIS | 2018 | 0 | 5 | 40 | Y | N | coastal | NYIS | LIB | BL | <=2019 | 1 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 25 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 1.3379 | age_years | random (k~1)
62734 | 0 | 36 | >4.5h | LIB | BL | NYIS | 2019 | 0 | 5 | 40 | N | N | coastal | NYIS | LIB | BL | <=2019 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 0 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62745 | 1 | 45 | 2.5-4.5h | LIB | CS | BPAT | 2022 | 1 | 30 | 120 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 1836 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 234.165 | age_years | random (k~1)
62753 | 1 | 72 | <1.5h | LIB | CS | ERCO | 2020 | 1 | 9.9 | 10 | Y | Y | inland | ERCO | LIB | CS | 2020-21 | 1 | 1 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 14 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 0.9394 | age_years | random (k~1)
62754 | 0 | 20 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 2 | 4 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 0 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62801 | 0 | 24 | <1.5h | LIB | CS | CISO | 2021 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 908 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 45.5565 | age_years | random (k~1)
62835 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 1.5 | 3 | N | Y | coastal | ISNE | LIB | CS | <=2019 | 0 | 1 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 6 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.10656 | age_years | random (k~1)
62839 | 0 | 36 | >4.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 10 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 0 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62844 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 150 | 300 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 6721.5 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 255.9915 | age_years | random (k~1)
62856 | 0 | 83 | <1.5h | LIB | CS | PJM | 2018 | 1 | 20 | 20 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | PARTIAL_AVAILABILITY | inf | 0.12644 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
62862 | 0 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 74 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 2.9414 | age_years | random (k~1)
62874 | 2 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 2 | 6 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 83.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 6.2718 | age_years | random (k~1)
62875 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 3 | 12 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 86 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 6.4596 | age_years | random (k~1)
62889 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 20 | 80 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 1815.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 136.3655 | age_years | random (k~1)
62907 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2019 | 0 | 1.9 | 1.9 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.004386 | ba_g+dur_band+vintage_g | 0 | 0.004386 | 155 | PARTIAL_AVAILABILITY | inf | 0.051271 | 2.3101 | 0.14479 | 2.7287 | age_years | random (k~1)
62908 | 1 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 0 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 9.5 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0.31538 | age_years | random (k~1)
62937 | 0 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 4 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0.13279 | age_years | random (k~1)
62964 | 1 | 16 | <1.5h | LIB | CS | AZPS | 2023 | 0 | 50 | 50 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.01104 | dur_band+climate_region | 0 | 0.01104 | 4547.5 | PARTIAL_AVAILABILITY | inf | 0.12408 | 2.3101 | 0.14479 | 201.5114 | age_years | random (k~1)
62968 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 4 | Y | N | coastal | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 53 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 1.4182 | age_years | random (k~1)
62969 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 74.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 2.1513 | age_years | random (k~1)
62970 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 64.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.8625 | age_years | random (k~1)
62971 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 2.9 | 6 | Y | N | inland | ISNE | other | CT | 2022-23 | 1 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 62.5 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 1.6724 | age_years | random (k~1)
62972 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2021 | 1 | 2 | 4.2 | Y | N | inland | ISNE | other | CT | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 57 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.6459 | age_years | random (k~1)
62973 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 1.6 | 3.2 | Y | N | coastal | ISNE | other | CT | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 36.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.054 | age_years | random (k~1)
62974 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 3.8 | 7.9 | Y | Y | inland | ISNE | other | CT | 2022-23 | 1 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 154 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 4.1208 | age_years | random (k~1)
62975 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 3.9 | 7.9 | Y | Y | inland | ISNE | other | CT | 2020-21 | 1 | 1 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 114 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 3.2919 | age_years | random (k~1)
62976 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2020 | 1 | 2 | 4 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 16 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.46202 | age_years | random (k~1)
62977 | 0 | 12 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 51.5 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 1.3781 | age_years | random (k~1)
62978 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3 | 6 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 65 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.877 | age_years | random (k~1)
62981 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2018 | 0 | 2 | 4.2 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 35.5 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 1.1785 | age_years | random (k~1)
62999 | 0 | 36 | <1.5h | LIB | CT | NYIS | 2020 | 1 | 3 | 4.4 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 0 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63000 | 0 | 36 | 1.5-2.5h | LIB | CT | NYIS | 2020 | 1 | 4 | 8.8 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63011 | 0 | 36 | >4.5h | LIB | CT | ISNE | 2020 | 1 | 1.5 | 7.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0043103 | dur_band+climate_region | 0 | 0.0043103 | 100.5 | PARTIAL_AVAILABILITY | inf | 0.050409 | 2.3101 | 0.14479 | 1.7387 | age_years | random (k~1)
63022 | 2 | 36 | 1.5-2.5h | LIB | CS | WACM | 2018 | 0 | 4.2 | 8.5 | N | N | industrial | other | LIB | CS | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 238 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 7.7876 | age_years | random (k~1)
63044 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 4.3 | 14 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 196 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 8.1948 | age_years | random (k~1)
63064 | 0 | 64 | <1.5h | LIB | CS | CPLW | 2020 | 0 | 8.8 | 8.8 | Y | Y | inland | other | LIB | CS | 2020-21 | 1 | 1 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 31 | PARTIAL_AVAILABILITY | inf | 0.10609 | 2.3101 | 0.14479 | 1.1629 | age_years | random (k~1)
63090 | 1 | 36 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 3 | 6 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 9 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0.29879 | age_years | random (k~1)
63172 | 3 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 14374.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 1833.3363 | age_years | random (k~1)
63186 | 0 | 36 | <1.5h | LIB | CS | JEA | 2019 | 1 | 5 | 3.8 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.010811 | ba_g+dur_band+vintage_g | 0 | 0.010811 | 0 | PARTIAL_AVAILABILITY | inf | 0.12167 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63214 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3 | 6.6 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 0 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63238 | 0 | 24 | <1.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 20 | Y | N | inland | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 0 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63255 | 1 | 57 | <1.5h | LIB | BL | ERCO | 2021 | 1 | 40 | 40 | Y | Y | arid | ERCO | LIB | BL | 2020-21 | 1 | 1 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 125 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 8.3875 | age_years | random (k~1)
63264 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 32 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 2.4326 | age_years | random (k~1)
63280 | 0 | 36 | >4.5h | LIB | CT |  | 2021 | 1 | 14 | 70 | N | Y | coastal | other | LIB | CT | 2020-21 | 0 | 1 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 1353 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 72.4087 | age_years | random (k~1)
63324 | 0 | 36 | <1.5h | LIB | BL | MISO | 2019 | 1 | 5 | 5 | N | N | inland | MISO | LIB | BL | <=2019 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 64.5 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 2.5638 | age_years | random (k~1)
63337 | 2 | 36 | <1.5h | LIB | CT | NYIS | 2022 | 1 | 3 | 3 | N | N | inland | NYIS | LIB | CT | 2022-23 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 55 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 2.1862 | age_years | random (k~1)
63338 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 63 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 2.5542 | age_years | random (k~1)
63339 | 0 | 17 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0018062 | age_years | random (k~1)
63340 | 0 | 33 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 49 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.019668 | age_years | random (k~1)
63341 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 52.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.021072 | age_years | random (k~1)
63352 | 0 | 21 | <1.5h | LIB | CS | NEVP | 2024 | 1 | 380 | 380 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.01104 | dur_band+climate_region | 0 | 0.01104 | 38646 | PARTIAL_AVAILABILITY | inf | 0.12408 | 2.3101 | 0.14479 | 1712.5038 | age_years | random (k~1)
63398 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 1.6 | 3.8 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 104 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 1.8471 | age_years | random (k~1)
63415 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 1.6 | 6.6 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63420 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 0.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 5 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 0.25086 | age_years | random (k~1)
63421 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.2 | 0.2 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 0 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63422 | 1 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.3 | 0.3 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 0 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63458 | 0 | 24 | 1.5-2.5h | FLB | CS | SWPP | 2020 | 0 | 10 | 20 | Y | N | inland | other | other | CS | 2020-21 | 1 | 0 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 376.5 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 39.179 | age_years | random (k~1)
63468 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 15 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 1.1403 | age_years | random (k~1)
63469 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.5 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 42.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.2272 | age_years | random (k~1)
63470 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.9 | 5.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 50 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.4438 | age_years | random (k~1)
63472 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 2.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 22.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.64971 | age_years | random (k~1)
63473 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.8 | 3.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 52 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.5016 | age_years | random (k~1)
63474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 65 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.877 | age_years | random (k~1)
63475 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.3 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 63 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.8192 | age_years | random (k~1)
63486 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.5 | 0.8 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 18 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 1.2122 | age_years | random (k~1)
63510 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.5 | 0.5 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 0.5 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 0.025086 | age_years | random (k~1)
63522 | 2 | 43 | 1.5-2.5h | LIB | OT | SOCO | 2022 | 1 | 40 | 80 | N | N | inland | other | LIB | other | 2022-23 | 0 | 0 | 0.034286 | ba_g+dur_band+vintage_g | 0 | 0.034286 | 1540.5 | PARTIAL_AVAILABILITY | inf | 0.3373 | 2.3101 | 0.14479 | 211.9967 | age_years | random (k~1)
63535 | 0 | 36 | 2.5-4.5h | LIB | BL | SOCO | 2020 | 1 | 1 | 4 | Y | N | inland | other | LIB | BL | 2020-21 | 1 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 93 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 4.8604 | age_years | random (k~1)
63585 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 3 | 12 | Y | N | coastal | NYIS | LIB | CS | 2020-21 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 98 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.039335 | age_years | random (k~1)
63609 | 1 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 91 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 8.6553 | age_years | random (k~1)
63610 | 1 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.2 | 6.3 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 73 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 6.9433 | age_years | random (k~1)
63611 | 1 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 2.5 | 15 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 218 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 20.7347 | age_years | random (k~1)
63612 | 2 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 1 | 6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 35 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 3.329 | age_years | random (k~1)
63613 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 2 | 13 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 66 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 6.2775 | age_years | random (k~1)
63614 | 1 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1 | 5 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 59 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 5.6117 | age_years | random (k~1)
63615 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 8.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 182 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 17.3106 | age_years | random (k~1)
63616 | 1 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 4.9 | 32.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 326 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 31.007 | age_years | random (k~1)
63617 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.3 | 7.2 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.023697 | ba_g+dur_band+vintage_g | 0 | 0.023697 | 146 | PARTIAL_AVAILABILITY | inf | 0.2475 | 2.3101 | 0.14479 | 13.8866 | age_years | random (k~1)
63685 | 1 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 100 | 400 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 9551.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 719.6493 | age_years | random (k~1)
63721 | 3 | 49 | 1.5-2.5h | LIB | CS | SOCO | 2021 | 1 | 40 | 80 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 2340.5 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 243.5551 | age_years | random (k~1)
63722 | 1 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2021 | 1 | 1 | 2 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 37.5 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 3.9023 | age_years | random (k~1)
63723 | 0 | 6 | 2.5-4.5h | LIB | CS | HECO | 2025 | 1 | 52 | 208 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 4320.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 122.5552 | age_years | random (k~1)
63727 | 2 | 47 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 140.3 | 561 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 15233 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1147.7169 | age_years | random (k~1)
63728 | 1 | 38 | 1.5-2.5h | LIB | CS | PNM | 2022 | 1 | 12.5 | 25 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.034286 | ba_g+dur_band+vintage_g | 0 | 0.034286 | 540.5 | PARTIAL_AVAILABILITY | inf | 0.3373 | 2.3101 | 0.14479 | 74.3812 | age_years | random (k~1)
63731 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 125 | 500 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 6763.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 862.6227 | age_years | random (k~1)
63735 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 11 | 44 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 1053.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 79.1303 | age_years | random (k~1)
63737 | 1 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 125 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 3352 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 224.9184 | age_years | random (k~1)
63757 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 6598 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 118.0168 | age_years | random (k~1)
63763 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 5.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 30.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.88072 | age_years | random (k~1)
63774 | 0 | 9 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 0.7 | 2.1 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0020069 | age_years | random (k~1)
63775 | 0 | 36 | 1.5-2.5h | LIB | BL | SOCO | 2020 | 0 | 0.2 | 0.4 | N | N | inland | other | LIB | BL | 2020-21 | 0 | 0 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 0 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
63776 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 6764.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 862.7502 | age_years | random (k~1)
63804 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2 | 3.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 17.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.50533 | age_years | random (k~1)
63805 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 44 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.2706 | age_years | random (k~1)
63834 | 1 | 66 | 2.5-4.5h | LIB | BL | CISO | 2020 | 0 | 250 | 1000 | N | N | coastal | CISO | LIB | BL | 2020-21 | 0 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 12078.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 907.2378 | age_years | random (k~1)
63843 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021.75 | 1 | 80 | 320 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 7844 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 590.9992 | age_years | random (k~1)
63848 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 225 | 900 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 26478.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1994.9991 | age_years | random (k~1)
63849 | 2 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 135 | 540 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 16258.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1224.9823 | age_years | random (k~1)
63859 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 1 | 147 | 147 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 13900.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 446.3491 | age_years | random (k~1)
63891 | 1 | 57 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 9420.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 707.5906 | age_years | random (k~1)
63892 | 0 | 52 | <1.5h | LIB | CS | ERCO | 2021 | 1 | 55.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 1015.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 68.1398 | age_years | random (k~1)
63900 | 1 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 1 | 30 | 120 | N | Y | coastal | other | LIB | CS | 2022-23 | 0 | 1 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 3080 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 392.8259 | age_years | random (k~1)
63905 | 0 | 43 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 91.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 2243 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 40.12 | age_years | random (k~1)
63913 | 3 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 5017.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 639.9363 | age_years | random (k~1)
63930 | 1 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 60 | 242 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 5428.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 407.7444 | age_years | random (k~1)
63933 | 0 | 20 | 1.5-2.5h | LIB | CS | NEVP | 2024 | 1 | 100 | 150 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 10988.5 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 459.4322 | age_years | random (k~1)
63943 | 1 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 60 | 240 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 6549 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 493.4286 | age_years | random (k~1)
63995 | 0 | 23 | <1.5h | LIB | CS | FPC | 2021 | 0 | 11 | 10.1 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 5 | PARTIAL_AVAILABILITY | inf | 0.10609 | 2.3101 | 0.14479 | 0.18756 | age_years | random (k~1)
63996 | 0 | 24 | 2.5-4.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 14.3 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 39 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 4.9741 | age_years | random (k~1)
63998 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 5.5 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 11 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0044152 | age_years | random (k~1)
63999 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 8.3 | 11.7 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 18 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0072248 | age_years | random (k~1)
64000 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.2 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 48 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.3861 | age_years | random (k~1)
64050 | 0 | 35 | <1.5h | LIB | CS | CPLE | 2023 | 1 | 2 | 2 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 0 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64084 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 0 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64087 | 0 | 22 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 0 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64089 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 6631.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 118.616 | age_years | random (k~1)
64090 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 0 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64092 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 0 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64103 | 0 | 58 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 35 | 140 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 1919.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 144.1771 | age_years | random (k~1)
64105 | 1 | 43 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 50 | 200 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 3994.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 300.9621 | age_years | random (k~1)
64128 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 2 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.057752 | age_years | random (k~1)
64129 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.1 | 6.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 108.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 3.1331 | age_years | random (k~1)
64140 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 1.4 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 13.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.38983 | age_years | random (k~1)
64147 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 50 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.4438 | age_years | random (k~1)
64148 | 2 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 2345 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 299.0834 | age_years | random (k~1)
64164 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 120 | 190 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 4966.5 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 161.1952 | age_years | random (k~1)
64170 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.9 | 1.8 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 14.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.4187 | age_years | random (k~1)
64182 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.7 | 9 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 84.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 2.44 | age_years | random (k~1)
64185 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 1.9 | 3.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 50 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.4438 | age_years | random (k~1)
64187 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 2.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 15.5 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 0.64806 | age_years | random (k~1)
64197 | 1 | 28 | <1.5h | LIB | CS | CISO | 2023 | 1 | 137 | 137 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 13407 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 999.6192 | age_years | random (k~1)
64198 | 0 | 36 | 2.5-4.5h | LIB | CS | BPAT | 2020 | 1 | 1 | 4 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 87.5 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 4.573 | age_years | random (k~1)
64202 | 0 | 12 |  |  |  | ERCO |  | 1 |  |  |  |  | inland | ERCO | other | other | 2020-21 | 0 | 0 | 0.012174 | fleet | 0 | 0.012174 | 1901.5 | PARTIAL_AVAILABILITY | inf | 0.13592 | 2.3101 | 0.14479 | 92.9179 | age_years | random (k~1)
64207 | 1 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 80.5 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 3.1998 | age_years | random (k~1)
64213 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 9.4 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 64 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 1.7125 | age_years | random (k~1)
64222 | 0 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 10 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 0.52263 | age_years | random (k~1)
64223 | 1 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 8.5 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 0.44423 | age_years | random (k~1)
64231 | 0 | 12 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 1 | 1 | 4.4 | N | N | inland | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.022989 | ba_g+dur_band+vintage_g | 0 | 0.022989 | 32.5 | PARTIAL_AVAILABILITY | inf | 0.24108 | 2.3101 | 0.14479 | 2.9988 | age_years | random (k~1)
64256 | 1 | 17 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 60 | 240 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5987.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 169.8413 | age_years | random (k~1)
64293 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 449.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 30.1613 | age_years | random (k~1)
64294 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 437 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 29.3226 | age_years | random (k~1)
64295 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 473 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 31.7382 | age_years | random (k~1)
64296 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 432 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 28.9871 | age_years | random (k~1)
64297 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 486.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 32.644 | age_years | random (k~1)
64298 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 399.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 26.8064 | age_years | random (k~1)
64312 | 0 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 2925 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 196.2668 | age_years | random (k~1)
64314 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 423.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 28.4168 | age_years | random (k~1)
64315 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 458 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 30.7317 | age_years | random (k~1)
64316 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 445 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 7.9596 | age_years | random (k~1)
64317 | 1 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 2799 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 187.8123 | age_years | random (k~1)
64318 | 1 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 804 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 14.3809 | age_years | random (k~1)
64319 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 473.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 31.7717 | age_years | random (k~1)
64321 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 407.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 27.3432 | age_years | random (k~1)
64322 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 874.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 15.642 | age_years | random (k~1)
64374 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64375 | 0 | 24 | <1.5h | LIB | CS | MISO | 2021 | 0 | 2.5 | 2.9 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 0 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64395 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2.5 | 5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 39.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.1406 | age_years | random (k~1)
64400 | 0 | 36 | <1.5h | LIB | CS | HECO | 2021 | 1 | 1.9 | 1.9 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 104 | PARTIAL_AVAILABILITY | inf | 0.10609 | 2.3101 | 0.14479 | 3.9013 | age_years | random (k~1)
64423 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 16.5 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 203 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 14.6152 | age_years | random (k~1)
64424 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 17.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 12.5 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 0.89995 | age_years | random (k~1)
64425 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 11.9 | N | N | coastal | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 5.5 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 0.36905 | age_years | random (k~1)
64426 | 1 | 56 | 1.5-2.5h | LIB | CS | TEPC | 2021 | 1 | 30 | 60 | N | Y | arid | other | LIB | CS | 2020-21 | 0 | 1 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 1502 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 156.2998 | age_years | random (k~1)
64432 | 1 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.2 | 4.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 13 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.37539 | age_years | random (k~1)
64436 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 8 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.23101 | age_years | random (k~1)
64442 | 0 | 10 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 0.7 | 3 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 9 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0036124 | age_years | random (k~1)
64446 | 0 | 36 | <1.5h | LIB | CS | BPAT | 2021 | 1 | 1 | 1.4 | Y | N | coastal | other | LIB | CS | 2020-21 | 1 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 14 | PARTIAL_AVAILABILITY | inf | 0.10609 | 2.3101 | 0.14479 | 0.52517 | age_years | random (k~1)
64450 | 0 | 36 | <1.5h | LIB | CS | PJM | 2021 | 1 | 10 | 10 | N | N | inland | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 42 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 1.6694 | age_years | random (k~1)
64453 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 3 | 12 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64481 | 1 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 132 | 528 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 13892 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1046.6804 | age_years | random (k~1)
64489 | 0 | 29 | 2.5-4.5h | OTH | CS | CISO | 2023 | 1 | 75 | 300 | N | N | arid | CISO | other | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 6828 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 514.4496 | age_years | random (k~1)
64508 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 14 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0056193 | age_years | random (k~1)
64509 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0016055 | age_years | random (k~1)
64510 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 5.1 | 10 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 38 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.015252 | age_years | random (k~1)
64511 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 2.5 | 5 | Y | N | coastal | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 16.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0066227 | age_years | random (k~1)
64512 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.5 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0012041 | age_years | random (k~1)
64513 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0016055 | age_years | random (k~1)
64514 | 1 | 36 | <1.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 2.5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 15 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0.59623 | age_years | random (k~1)
64516 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 16 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0064221 | age_years | random (k~1)
64520 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 15 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0060207 | age_years | random (k~1)
64522 | 1 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2021 | 1 | 1.3 | 2 | N | N | inland | CPLE | LIB | CS | 2020-21 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 8.5 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0.28219 | age_years | random (k~1)
64528 | 1 | 55 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 200 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 3780 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 272.1455 | age_years | random (k~1)
64529 | 0 | 11 | 2.5-4.5h | LIB | CS | TVA | 2025 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 2765 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 78.4319 | age_years | random (k~1)
64545 | 1 | 16 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 73 | 108.6 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 1935.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 34.6198 | age_years | random (k~1)
64546 | 0 | 24 | 2.5-4.5h | LIB | BL | FPL | 2019 | 0 | 10 | 40 | N | N | coastal | other | LIB | BL | <=2019 | 0 | 0 | 0.027083 | ba_g+dur_band+vintage_g | 0 | 0.027083 | 218 | PARTIAL_AVAILABILITY | inf | 0.27747 | 2.3101 | 0.14479 | 23.6981 | age_years | random (k~1)
64564 | 1 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 110 | 440 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 9496.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 715.5054 | age_years | random (k~1)
64601 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 12 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 0.90134 | age_years | random (k~1)
64611 | 1 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 8.3 | 3.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 845.5 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 42.4207 | age_years | random (k~1)
64612 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 0 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
64614 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 823.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 62.0459 | age_years | random (k~1)
64617 | 2 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 9.5 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 175 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 7.3168 | age_years | random (k~1)
64618 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 9 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 145 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 7.76 | age_years | random (k~1)
64619 | 0 | 33 | >4.5h | LIB | CS | ISNE | 2023 | 1 | 0.8 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 69 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 3.6927 | age_years | random (k~1)
64620 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 5.1 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 90 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 3.7629 | age_years | random (k~1)
64624 | 0 | 49 | <1.5h | LIB | CS | CISO | 2021 | 1 | 50 | 50 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 5021.5 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 251.9404 | age_years | random (k~1)
64627 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 17 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 1.2923 | age_years | random (k~1)
64630 | 1 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 20 | 50 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 1453.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 109.5127 | age_years | random (k~1)
64633 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 240 | 960 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 24396 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 1442.1257 | age_years | random (k~1)
64636 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 200 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 8455 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 271.4925 | age_years | random (k~1)
64640 | 0 | 36 | <1.5h | LIB | CS | CPLW | 2022 | 1 | 4.4 | 4.4 | N | Y | inland | other | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 18.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0074255 | age_years | random (k~1)
64656 | 1 | 18 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 12.5 | 50 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1251 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 35.4858 | age_years | random (k~1)
64664 | 1 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 92 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 6.9937 | age_years | random (k~1)
64672 | 0 | 31 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.6 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 1596 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 51.8006 | age_years | random (k~1)
64686 | 0 | 36 | <1.5h | LIB | OT | NYIS | 2022 | 1 | 24.7 | 20 | N | Y | inland | NYIS | LIB | other | 2022-23 | 0 | 1 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 1020 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 40.5435 | age_years | random (k~1)
64695 | 1 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 3.7 | 15 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 186.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 23.7864 | age_years | random (k~1)
64696 | 1 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 4.5 | 20.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 225 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 9.4073 | age_years | random (k~1)
64701 | 1 | 40 | 1.5-2.5h | LIB | CS | CISO | 2022 | 0 | 125 | 250 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 7244 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 911.2095 | age_years | random (k~1)
64712 | 1 | 50 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 100 | 200 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 5802.5 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 391.4285 | age_years | random (k~1)
64713 | 0 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 10979.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 824.6899 | age_years | random (k~1)
64719 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 7.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 28 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 1.1707 | age_years | random (k~1)
64726 | 0 | 35 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 3.6 | 8 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 67 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 1.7928 | age_years | random (k~1)
64727 | 0 | 36 | 2.5-4.5h | LIB | OT | ISNE | 2022 | 1 | 3 | 8 | N | N | coastal | ISNE | LIB | other | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 43.5 | PARTIAL_AVAILABILITY | inf | 0.21337 | 2.3101 | 0.14479 | 3.492 | age_years | random (k~1)
64731 | 0 | 36 | 1.5-2.5h | OTH | CS | ISNE | 2021 | 1 | 2.3 | 4.8 | N | N | inland | ISNE | other | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 0.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.014438 | age_years | random (k~1)
64743 | 1 | 36 | <1.5h | LIB | CS | CISO | 2022 | 0 | 5 | 5 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 351.5 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 26.2077 | age_years | random (k~1)
64752 | 1 | 24 | >4.5h | LIB | CS | FPC | 2023 | 1 | 2.5 | 18 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 35.5 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 1.8999 | age_years | random (k~1)
64759 | 2 | 24 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 4.5 | 13.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 142.5 | PARTIAL_AVAILABILITY | inf | 0.21337 | 2.3101 | 0.14479 | 11.4393 | age_years | random (k~1)
64760 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 0 | 3 | 10 | Y | Y | coastal | ISNE | LIB | CS | 2022-23 | 1 | 1 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 87.5 | PARTIAL_AVAILABILITY | inf | 0.21337 | 2.3101 | 0.14479 | 7.0241 | age_years | random (k~1)
64761 | 0 | 6 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 2 | 11.9 | N | N | coastal | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 42.5 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 2.2745 | age_years | random (k~1)
64763 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | 2020-21 | 1 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 41.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.1984 | age_years | random (k~1)
64764 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 1.5 | 3.1 | Y | Y | inland | ISNE | LIB | CS | 2020-21 | 1 | 1 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 35.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.0251 | age_years | random (k~1)
64765 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.0044248 | ba_g+dur_band+vintage_g | 0 | 0.0044248 | 46.5 | PARTIAL_AVAILABILITY | inf | 0.051712 | 2.3101 | 0.14479 | 0.82585 | age_years | random (k~1)
64766 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 2.2 | 8.8 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 44.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 3.3425 | age_years | random (k~1)
64811 | 0 | 23 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 24.8 | 25 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 565.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 10.115 | age_years | random (k~1)
64844 | 0 | 13 | 1.5-2.5h | PBB | CS | ISNE | 2024 | 1 | 1.4 | 2.8 | Y | N | inland | ISNE | other | CS | 2024+ | 1 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 23 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0.76356 | age_years | random (k~1)
64851 | 0 | 23 | <1.5h | LIB | CS | CISO | 2023 | 1 | 131 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 11681 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 870.9295 | age_years | random (k~1)
64852 | 2 | 29 | <1.5h | LIB | CS | CISO | 2023 | 1 | 149 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 12083.5 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 900.9397 | age_years | random (k~1)
64864 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 88 | 352 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 8291 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 490.1076 | age_years | random (k~1)
64875 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 23 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.66415 | age_years | random (k~1)
64876 | 2 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 286 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 21.7413 | age_years | random (k~1)
64877 | 2 | 44 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 11 | 31.5 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 495 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 37.1803 | age_years | random (k~1)
64878 | 2 | 41 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 144 | 272 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 6838.5 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 860.2024 | age_years | random (k~1)
64879 | 2 | 44 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 120 | 250 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 4492 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 565.0405 | age_years | random (k~1)
64908 | 0 | 19 | >4.5h | LIB | CS | CISO | 2024 | 1 | 40 | 200 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0043103 | dur_band+climate_region | 0 | 0.0043103 | 3315 | PARTIAL_AVAILABILITY | inf | 0.050409 | 2.3101 | 0.14479 | 57.3522 | age_years | random (k~1)
64915 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 524.5 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 37.762 | age_years | random (k~1)
64916 | 1 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 444 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 31.9663 | age_years | random (k~1)
64917 | 1 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 7.5 | 15 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 401.5 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 28.9065 | age_years | random (k~1)
64921 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 20 | 80 | Y | Y | coastal | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 |  | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 |  | age_years | random (k~1)
64928 | 2 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 33 | 70 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 1792.5 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 225.4753 | age_years | random (k~1)
64929 | 2 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 40 | 83.5 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 1178 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 148.1785 | age_years | random (k~1)
64970 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 20.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 99 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 4.1392 | age_years | random (k~1)
64980 | 0 | 36 | 2.5-4.5h | LIB | BL | ISNE | 2021 | 1 | 0.5 | 2.1 | N | N | coastal | ISNE | LIB | BL | 2020-21 | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 3 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 0.12543 | age_years | random (k~1)
64993 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 40 | 160 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 1829 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 137.8044 | age_years | random (k~1)
65007 | 0 | 3 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 100 | 400 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 4 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 0.39642 | age_years | random (k~1)
65011 | 0 | 2 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 75 | 300 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 4.5 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 0.44598 | age_years | random (k~1)
65014 | 0 | 18 | 1.5-2.5h | LIB | CS | ISNE | 2024 | 1 | 2.5 | 4.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 4.5 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 0.17138 | age_years | random (k~1)
65015 | 1 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 12.8 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 153.5 | PARTIAL_AVAILABILITY | inf | 0.21337 | 2.3101 | 0.14479 | 12.3223 | age_years | random (k~1)
65018 | 0 | 15 | 2.5-4.5h | LIB | OT | SOCO | 2024 | 0 | 65 | 260 | N | Y | inland | other | LIB | other | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 7460 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 211.6102 | age_years | random (k~1)
65028 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.8 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 1679 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 54.4945 | age_years | random (k~1)
65029 | 0 | 36 | 1.5-2.5h | LIB | BL | MISO | 2021 | 1 | 0.3 | 0.5 | Y | N | inland | MISO | LIB | BL | 2020-21 | 1 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
65035 | 0 | 16 | 2.5-4.5h | LIB | CS | NYIS | 2023 | 0 | 7.5 | 30 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 646 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.25929 | age_years | random (k~1)
65044 | 0 | 24 | 2.5-4.5h | LIB | CS | PJM | 2023 | 0 | 20 | 80 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 1729 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 89.6963 | age_years | random (k~1)
65053 | 0 | 34 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 112 | 448 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 13042 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 982.6379 | age_years | random (k~1)
65054 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1 | 5.4 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 33.5 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 1.7928 | age_years | random (k~1)
65055 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.2 | 4.8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 20.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.59196 | age_years | random (k~1)
65056 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 36.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.054 | age_years | random (k~1)
65057 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.3 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 23.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0.67859 | age_years | random (k~1)
65058 | 0 | 30 | <1.5h | LIB | CS | HECO | 2023 | 1 | 36 | 4.6 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2776.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 1.1144 | age_years | random (k~1)
65098 | 0 | 21 | 1.5-2.5h | LIB | CS | SWPP | 2020 | 0 | 1.5 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.025926 | ba_g+dur_band+vintage_g | 0 | 0.025926 | 17 | PARTIAL_AVAILABILITY | inf | 0.26737 | 2.3101 | 0.14479 | 1.769 | age_years | random (k~1)
65114 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1.5 | 8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 81.5 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 4.3616 | age_years | random (k~1)
65140 | 1 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 350 | 1400 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 42235.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 3182.1963 | age_years | random (k~1)
65154 | 0 | 12 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 2 | 4.3 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 16 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 0.42814 | age_years | random (k~1)
65174 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 37 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.0684 | age_years | random (k~1)
65217 | 0 | 36 | 2.5-4.5h | LIB | OT | NYIS | 2021 | 1 | 4.5 | 17 | N | N | inland | NYIS | LIB | other | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 43.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.01746 | age_years | random (k~1)
65239 | 0 | 7 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 24.6 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 255 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 13.6469 | age_years | random (k~1)
65240 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 48 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.019266 | age_years | random (k~1)
65241 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 38 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.015252 | age_years | random (k~1)
65242 | 0 | 35 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.5 | 3.8 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 0 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
65243 | 1 | 24 | 2.5-4.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 21.5 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 1.1154 | age_years | random (k~1)
65244 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 25.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.010235 | age_years | random (k~1)
65245 | 0 | 24 | <1.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.011724 | dur_band+climate_region | 0 | 0.011724 | 25.5 | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 | 1.2 | age_years | random (k~1)
65246 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 38.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.015453 | age_years | random (k~1)
65247 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 34.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.013848 | age_years | random (k~1)
65248 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 22.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.009031 | age_years | random (k~1)
65249 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 31 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.012443 | age_years | random (k~1)
65250 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 48 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.019266 | age_years | random (k~1)
65259 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 1228.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 21.9739 | age_years | random (k~1)
65271 | 1 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 125 | 125 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 1227 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 21.947 | age_years | random (k~1)
65291 | 0 | 19 | 2.5-4.5h | LIB | CS | TVA | 2024 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 2637.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 74.8153 | age_years | random (k~1)
65382 | 1 | 12 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 1 | 2 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 39.5 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 4.9686 | age_years | random (k~1)
65396 | 0 | 2 | <1.5h | LIB | CS | CISO | 2025 | 0 | 15 | 15 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 1080.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 34.6952 | age_years | random (k~1)
65397 | 0 | 14 | <1.5h | LIB | CS | CISO | 2024 | 0 | 30 | 30 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 1606 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 51.5691 | age_years | random (k~1)
65408 | 0 | 9 | 2.5-4.5h | LIB | CT | CISO | 2021 | 1 | 0.7 | 3 | Y | N | coastal | CISO | LIB | CT | 2020-21 | 1 | 0 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 24 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 1.8027 | age_years | random (k~1)
65409 | 1 | 36 | 1.5-2.5h | LIB | CT | CISO | 2021 | 1 | 0.5 | 0.9 | N | N | coastal | CISO | LIB | CT | 2020-21 | 0 | 0 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 22 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 1.4841 | age_years | random (k~1)
65410 | 0 | 29 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 190 | 380 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 7814 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 253.615 | age_years | random (k~1)
65422 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 510 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 14.4667 | age_years | random (k~1)
65429 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 555 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 15.7431 | age_years | random (k~1)
65433 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 426 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 12.0839 | age_years | random (k~1)
65441 | 1 | 36 | 2.5-4.5h | LIB | CS | MISO | 2022 | 1 | 1 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 6.5 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0.3372 | age_years | random (k~1)
65456 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 112.5 | 450 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 9593 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 567.0729 | age_years | random (k~1)
65457 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 18390 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 1087.0918 | age_years | random (k~1)
65468 | 0 | 12 | 2.5-4.5h | LIB | BL | PJM | 2019 | 1 | 0.6 | 2.1 | Y | Y | coastal | PJM | LIB | BL | <=2019 | 1 | 1 | 0.016591 | dur_band+climate_region | 0 | 0.016591 | 11.5 | PARTIAL_AVAILABILITY | inf | 0.18053 | 2.3101 | 0.14479 | 0.76583 | age_years | random (k~1)
65469 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 0.8 | 3.1 | N | N | industrial | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 53 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 3.9932 | age_years | random (k~1)
65472 | 1 | 24 | 2.5-4.5h | LIB | CS | NEVP | 2021 | 0 | 10 | 40 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 898.5 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 46.9582 | age_years | random (k~1)
65489 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 10262 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 355.0817 | age_years | random (k~1)
65490 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 8758.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 303.0582 | age_years | random (k~1)
65491 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 7961.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 275.4807 | age_years | random (k~1)
65492 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 175 | 175 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 8880 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 307.2623 | age_years | random (k~1)
65493 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 50 | 50 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 2595 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 89.7912 | age_years | random (k~1)
65499 | 0 | 36 | 1.5-2.5h | LIB | CS | PJM | 2022 | 0 | 10.5 | 24.6 | Y | Y | inland | PJM | LIB | CS | 2022-23 | 1 | 1 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 1144 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 37.9789 | age_years | random (k~1)
65530 | 0 | 24 | 1.5-2.5h | LIB | CS | MISO | 2022 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 140 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 4.6478 | age_years | random (k~1)
65531 | 0 | 24 | 1.5-2.5h | LIB | CS | MISO | 2023 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 121.5 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 4.0336 | age_years | random (k~1)
65562 | 0 | 24 | 2.5-4.5h | MAB | BL | CISO | 2024 | 1 | 1.6 | 5.9 | N | N | arid | CISO | other | BL | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 85 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 5.0246 | age_years | random (k~1)
65568 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 1 | 0.6 | 1.1 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 24.5 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 1.6527 | age_years | random (k~1)
65588 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 70 | 140 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 4197 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 127.6202 | age_years | random (k~1)
65589 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 8060.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 245.0994 | age_years | random (k~1)
65591 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 126 | 504 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 10586 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 625.7723 | age_years | random (k~1)
65614 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 2.1 | 4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 70 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 8.8052 | age_years | random (k~1)
65633 | 0 | 29 | <1.5h | LIB | CS | MISO | 2023 | 0 | 3.6 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 1 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0.039748 | age_years | random (k~1)
65635 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 587 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.23561 | age_years | random (k~1)
65644 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 7236 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 220.0285 | age_years | random (k~1)
65645 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 8723 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 265.2444 | age_years | random (k~1)
65650 | 1 | 24 | <1.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 1.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 27.5 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 2.0905 | age_years | random (k~1)
65656 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 20 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1183.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.47503 | age_years | random (k~1)
65657 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 65 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 3090 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 99.2208 | age_years | random (k~1)
65669 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 40 | PARTIAL_AVAILABILITY | inf | 0.21337 | 2.3101 | 0.14479 | 3.211 | age_years | random (k~1)
65670 | 0 | 35 | >4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 5 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.013333 | dur_band+climate_region | 0 | 0.013333 | 27.5 | PARTIAL_AVAILABILITY | inf | 0.14786 | 2.3101 | 0.14479 | 1.4717 | age_years | random (k~1)
65672 | 1 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 169 | 676 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 18683.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1407.6917 | age_years | random (k~1)
65673 | 0 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 47 | 188 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 5100 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 384.255 | age_years | random (k~1)
65674 | 1 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 136 | 136 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 9030.5 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 673.3096 | age_years | random (k~1)
65675 | 1 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 100 | 100 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 2440.5 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 181.9625 | age_years | random (k~1)
65677 | 0 | 30 | <1.5h | LIB | CS | CISO | 2023 | 1 | 18.8 | 18.8 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.018576 | ba_g+dur_band+vintage_g | 0 | 0.018576 | 548.5 | PARTIAL_AVAILABILITY | inf | 0.19981 | 2.3101 | 0.14479 | 40.8959 | age_years | random (k~1)
65692 | 1 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 42 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 2304 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 76.489 | age_years | random (k~1)
65693 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 5777 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 175.664 | age_years | random (k~1)
65694 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 802 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 14.3452 | age_years | random (k~1)
65695 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 100 | 100 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 1932 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 34.5572 | age_years | random (k~1)
65696 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 2297 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 41.0859 | age_years | random (k~1)
65698 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 6370 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 193.6956 | age_years | random (k~1)
65699 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 111 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 3123 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 101.3616 | age_years | random (k~1)
65700 | 1 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 107 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 3040.5 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 98.684 | age_years | random (k~1)
65701 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 800 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 14.3094 | age_years | random (k~1)
65711 | 0 | 17 | 2.5-4.5h | LIB | CS | IID | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 14331 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 406.5129 | age_years | random (k~1)
65733 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 588 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.23601 | age_years | random (k~1)
65734 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 15606.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1175.8579 | age_years | random (k~1)
65735 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 14596.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1099.7603 | age_years | random (k~1)
65743 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 50 | 200 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 4762 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 281.4971 | age_years | random (k~1)
65744 | 1 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 136 | 544 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 12977.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 767.1416 | age_years | random (k~1)
65809 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 172.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.0855 | age_years | random (k~1)
65810 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 186 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.3269 | age_years | random (k~1)
65811 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 186 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.3269 | age_years | random (k~1)
65812 | 0 | 21 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 136 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.7058 | age_years | random (k~1)
65813 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 182.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.2643 | age_years | random (k~1)
65814 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 184.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.3001 | age_years | random (k~1)
65815 | 1 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 1 | 2.1 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 2 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 0.076171 | age_years | random (k~1)
65829 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 159 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 2.844 | age_years | random (k~1)
65830 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 157.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 2.8172 | age_years | random (k~1)
65831 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 179.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.2107 | age_years | random (k~1)
65832 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 130 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 2.3253 | age_years | random (k~1)
65833 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 177.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.1749 | age_years | random (k~1)
65834 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 186 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.3269 | age_years | random (k~1)
65835 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 182.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 3.2643 | age_years | random (k~1)
65836 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 10.4 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.016717 | ba_g+dur_band+vintage_g | 0 | 0.016717 | 191 | PARTIAL_AVAILABILITY | inf | 0.18177 | 2.3101 | 0.14479 | 12.8161 | age_years | random (k~1)
65837 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 106 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 3.6678 | age_years | random (k~1)
65857 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 22207 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1673.1667 | age_years | random (k~1)
65860 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 160 | 320 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 8869.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 269.6991 | age_years | random (k~1)
65861 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 10423 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 316.9371 | age_years | random (k~1)
65866 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 593 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 16.821 | age_years | random (k~1)
65888 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 524 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 14.8638 | age_years | random (k~1)
65927 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 547 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 15.5162 | age_years | random (k~1)
65933 | 0 | 32 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 80 | 320 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 6966.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 524.8848 | age_years | random (k~1)
65945 | 0 | 36 | 2.5-4.5h | LIB | CS | PJM | 2022 | 1 | 1.5 | 4.3 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.016591 | dur_band+climate_region | 0 | 0.016591 | 12 | PARTIAL_AVAILABILITY | inf | 0.18053 | 2.3101 | 0.14479 | 0.79912 | age_years | random (k~1)
65950 | 1 | 32 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 1.8 | 6.4 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.02 | ba_g+dur_band+vintage_g | 0 | 0.02 | 120 | PARTIAL_AVAILABILITY | inf | 0.21337 | 2.3101 | 0.14479 | 9.6331 | age_years | random (k~1)
65951 | 1 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 12 | 12 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.018519 | ba_g+dur_band+vintage_g | 0 | 0.018519 | 2050.5 | PARTIAL_AVAILABILITY | inf | 0.19926 | 2.3101 | 0.14479 | 152.4124 | age_years | random (k~1)
65952 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 20 | 20 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.018519 | ba_g+dur_band+vintage_g | 0 | 0.018519 | 3327 | PARTIAL_AVAILABILITY | inf | 0.19926 | 2.3101 | 0.14479 | 247.2938 | age_years | random (k~1)
65953 | 1 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 7 | 7 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.018519 | ba_g+dur_band+vintage_g | 0 | 0.018519 | 1143.5 | PARTIAL_AVAILABILITY | inf | 0.19926 | 2.3101 | 0.14479 | 84.9956 | age_years | random (k~1)
65956 | 0 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 88 | 264 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 6630.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 845.6598 | age_years | random (k~1)
65962 | 0 | 24 | >4.5h | LIB | CS | CISO | 2024 | 1 | 10 | 47.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 761.5 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 34.4718 | age_years | random (k~1)
65963 | 0 | 30 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 60 | 240 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.042453 | ba_g+dur_band+vintage_g | 0 | 0.042453 | 6495.5 | PARTIAL_AVAILABILITY | inf | 0.39916 | 2.3101 | 0.14479 | 1106.8111 | age_years | random (k~1)
65980 | 2 | 31 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 131 | 524 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 13311 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1002.9055 | age_years | random (k~1)
65987 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 325 | 1300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 39866.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 3003.7061 | age_years | random (k~1)
65988 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 8284.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 624.1883 | age_years | random (k~1)
66006 | 1 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 73.2 | 120 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 3429.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 104.2824 | age_years | random (k~1)
66007 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 4593 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 149.0727 | age_years | random (k~1)
66008 | 2 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 4727 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 153.4218 | age_years | random (k~1)
66009 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 203 | 400 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 5889 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 191.1363 | age_years | random (k~1)
66023 | 0 | 14 | <1.5h | LIB | CS | CISO | 2024 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 0 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66050 | 2 | 40 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 127 | 508 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 12855 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 968.5486 | age_years | random (k~1)
66067 | 1 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 0 | 185 | 565 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 14604 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 1862.6069 | age_years | random (k~1)
66075 | 1 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 3.3 | N | N | coastal | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 101 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 2.9165 | age_years | random (k~1)
66076 | 1 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 71 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 2.8786 | age_years | random (k~1)
66128 | 0 | 10 | 2.5-4.5h | LIB | CS | TEC | 2025 | 1 | 40 | 103 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 779.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 22.1113 | age_years | random (k~1)
66129 | 0 | 10 | 1.5-2.5h | LIB | CS | TEC | 2024 | 1 | 15 | 30 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 226.5 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 9.47 | age_years | random (k~1)
66137 | 0 | 21 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 40.4 | 80 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 2080 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 63.2475 | age_years | random (k~1)
66163 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 20 | 80 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 1975.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 251.957 | age_years | random (k~1)
66170 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 368.8 | N | N | arid | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 7464 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 242.2553 | age_years | random (k~1)
66180 | 0 | 28 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 3.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 0 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66181 | 0 | 29 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 7.8 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 0 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66182 | 0 | 33 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 0 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66208 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 132 | 528 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 15161.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 1142.3298 | age_years | random (k~1)
66218 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2020 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66222 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2021 | 1 | 4 | 8 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66228 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 2 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 0 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66232 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66263 | 1 | 19 | 2.5-4.5h | LIB | CS | SRP | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 33877.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 960.9685 | age_years | random (k~1)
66265 | 1 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 828.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 26.6034 | age_years | random (k~1)
66266 | 1 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 648.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 20.8235 | age_years | random (k~1)
66270 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 162 | 648 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 12611 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 745.4766 | age_years | random (k~1)
66278 | 0 | 21 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 740.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 23.7777 | age_years | random (k~1)
66279 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 652 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 20.9359 | age_years | random (k~1)
66280 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 1082.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 34.7594 | age_years | random (k~1)
66281 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 20 | 20 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 859 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 27.5827 | age_years | random (k~1)
66285 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 20915 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 1236.3526 | age_years | random (k~1)
66286 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 200 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 10781 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 4.3273 | age_years | random (k~1)
66325 | 0 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 116 | 464 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 4738.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 134.4122 | age_years | random (k~1)
66326 | 0 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2024 | 0 | 40 | 160 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 3490.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 99.0115 | age_years | random (k~1)
66327 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 4 | 16 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 267 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 7.5737 | age_years | random (k~1)
66328 | 0 | 12 | 1.5-2.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 4 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 140 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 5.8534 | age_years | random (k~1)
66329 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 8 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 0 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66330 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 3 | 12 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 274.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 7.7865 | age_years | random (k~1)
66333 | 0 | 18 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 90 | 360 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 10478 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 297.2188 | age_years | random (k~1)
66334 | 0 | 20 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 250 | 1000 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 30035 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 851.9722 | age_years | random (k~1)
66336 | 0 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 102.6 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 5791.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 176.1049 | age_years | random (k~1)
66337 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 11481 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 349.1082 | age_years | random (k~1)
66338 | 1 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 223.4 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 11024.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 381.4654 | age_years | random (k~1)
66357 | 0 | 30 | 2.5-4.5h | LIB | CS | NEVP | 2023 | 1 | 65 | 260 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 6979.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 890.1715 | age_years | random (k~1)
66394 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 60 | 160 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 3423.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 202.374 | age_years | random (k~1)
66408 | 1 | 31 | 2.5-4.5h | LIB | CS | EPE | 2023 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 3308 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 421.9052 | age_years | random (k~1)
66420 | 1 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 262.5 | 250 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 8277 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 286.3975 | age_years | random (k~1)
66423 | 1 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 68.8 | 275.2 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 7325.5 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 551.9333 | age_years | random (k~1)
66461 | 1 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 116.6 | 400 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 10026 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 592.669 | age_years | random (k~1)
66462 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 88 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 8473 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 500.8662 | age_years | random (k~1)
66474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 6.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 0 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66488 | 0 | 27 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66494 | 0 | 19 | 2.5-4.5h | LIB | CS | CISO | 2024.0882 | 0 | 680 | 2720 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 71677 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 4237.0569 | age_years | random (k~1)
66499 | 0 | 36 | 1.5-2.5h | LIB | CT | PJM | 2021 | 1 | 1.2 | 2.4 | N | N | coastal | PJM | LIB | CT | 2020-21 | 0 | 0 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 2 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 0.076171 | age_years | random (k~1)
66500 | 1 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 85 | 212 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.016807 | ba_g+dur_band+vintage_g | 0 | 0.016807 | 4968.5 | PARTIAL_AVAILABILITY | inf | 0.18264 | 2.3101 | 0.14479 | 335.168 | age_years | random (k~1)
66502 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 54 | 216 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.018713 | ba_g+dur_band+vintage_g | 0 | 0.018713 | 3759.5 | PARTIAL_AVAILABILITY | inf | 0.20113 | 2.3101 | 0.14479 | 282.3828 | age_years | random (k~1)
66505 | 0 | 15 | 1.5-2.5h | LIB | CS | CISO | 2024 | 0 | 6 | 12 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 212 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.085092 | age_years | random (k~1)
66533 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 10 | 20 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 |  | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 |  | age_years | random (k~1)
66540 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 100 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 8494 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 293.906 | age_years | random (k~1)
66574 | 1 | 15 | >4.5h | LIB | CS | PNM | 2024 | 1 | 100 | 561.4 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 10717.5 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 485.1627 | age_years | random (k~1)
66575 | 1 | 21 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 24158 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 1428.0567 | age_years | random (k~1)
66598 | 0 | 15 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 4250.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 251.2607 | age_years | random (k~1)
66599 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 0 | 7.3 | 7.1 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 423.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 13.5987 | age_years | random (k~1)
66606 | 0 | 2 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 175 | 350 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 2393 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 91.1386 | age_years | random (k~1)
66616 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 5008 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 89.5768 | age_years | random (k~1)
66617 | 1 | 17 | 2.5-4.5h | LIB | CT | CISO | 2024 | 0 | 100 | 400 | N | N | coastal | CISO | LIB | CT | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 12037 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 711.5456 | age_years | random (k~1)
66619 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 1.2 | 4.6 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 104 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 6.1478 | age_years | random (k~1)
66620 | 0 | 29 | >4.5h | LIB | CS | CISO | 2023 | 1 | 40 | 300 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 3569.5 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 161.5851 | age_years | random (k~1)
66627 | 1 | 31 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 260 | 1040 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 26072.5 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 3325.3095 | age_years | random (k~1)
66636 | 0 | 25 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 9634 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 725.8652 | age_years | random (k~1)
66637 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 15386 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 909.5157 | age_years | random (k~1)
66648 | 0 | 10 | >4.5h | LIB | CS | CISO | 2025 | 0 | 2 | 9 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 24 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 1.0864 | age_years | random (k~1)
66650 | 1 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 13 | 52 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 1254.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 74.1575 | age_years | random (k~1)
66659 | 0 | 10 | <1.5h | LIB | CS | CISO | 2025 | 0 | 97 | 97 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 2732.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 87.7414 | age_years | random (k~1)
66660 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 2132 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 68.4591 | age_years | random (k~1)
66661 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 2374.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 76.2459 | age_years | random (k~1)
66662 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 32 | 32 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 733 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 23.5368 | age_years | random (k~1)
66666 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 125 | 500 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 12549.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 741.8411 | age_years | random (k~1)
66669 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 2180.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 128.8963 | age_years | random (k~1)
66688 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 103.6 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 3953.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 136.7975 | age_years | random (k~1)
66690 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 2817.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 97.49 | age_years | random (k~1)
66694 | 0 | 14 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 34752 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 985.7746 | age_years | random (k~1)
66699 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 59.7 | 59.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 4105.5 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 131.8288 | age_years | random (k~1)
66716 | 0 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 0 | 100 | 400 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.031776 | ba_g+dur_band+vintage_g | 0 | 0.031776 | 7273 | PARTIAL_AVAILABILITY | inf | 0.31703 | 2.3101 | 0.14479 | 927.6048 | age_years | random (k~1)
66717 | 0 | 22 | 2.5-4.5h | OTH | CS | CPLE | 2023 | 1 | 18 | 72 | N | N | inland | CPLE | other | CS | 2022-23 | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 0 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66726 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 70 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 7330 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 433.2998 | age_years | random (k~1)
66727 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 149 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 3.987 | age_years | random (k~1)
66728 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 135 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 3.6124 | age_years | random (k~1)
66757 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 6250 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 369.4575 | age_years | random (k~1)
66758 | 0 | 23 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 18.3 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 3258.5 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 129.5205 | age_years | random (k~1)
66764 | 0 | 23 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66765 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66767 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 9.5 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 25.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.010235 | age_years | random (k~1)
66772 | 1 | 22 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 28 | 112 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 2906 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 218.95 | age_years | random (k~1)
66773 | 1 | 20 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 7680.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 454.0189 | age_years | random (k~1)
66782 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 174.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 6.038 | age_years | random (k~1)
66783 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 107.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 3.7197 | age_years | random (k~1)
66784 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 124 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.2906 | age_years | random (k~1)
66788 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 134 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.6366 | age_years | random (k~1)
66789 | 0 | 23 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 127 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.3944 | age_years | random (k~1)
66790 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 197 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 6.8165 | age_years | random (k~1)
66791 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 168.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 5.8304 | age_years | random (k~1)
66792 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 94 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 3.2526 | age_years | random (k~1)
66794 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 101 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 3.4948 | age_years | random (k~1)
66795 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 145 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 5.0172 | age_years | random (k~1)
66799 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.7 | 1.3 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 0 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
66801 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 2294 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 69.7547 | age_years | random (k~1)
66804 | 0 | 17 | 1.5-2.5h | LIB | CT | ERCO | 2024 | 0 | 150 | 300 | N | Y | inland | ERCO | LIB | CT | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 10807 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 328.6136 | age_years | random (k~1)
66807 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 3 | 12 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.018771 | ba_g+dur_band+vintage_g | 0 | 0.018771 | 384 | PARTIAL_AVAILABILITY | inf | 0.20169 | 2.3101 | 0.14479 | 28.9321 | age_years | random (k~1)
66814 | 0 | 21 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5684.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 161.2464 | age_years | random (k~1)
66871 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 300 | 467 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 9676.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 294.2379 | age_years | random (k~1)
66872 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 158.3 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 4434 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 134.8267 | age_years | random (k~1)
66885 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 25 | 100 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 1544.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 91.3003 | age_years | random (k~1)
66890 | 0 | 1 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 38 | 152 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 4 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 0.23645 | age_years | random (k~1)
66905 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 157.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 2260 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 68.7209 | age_years | random (k~1)
66925 | 0 | 23 | <1.5h | LIB | BL | TEPC | 2023 | 1 | 20 | 20 | N | N | arid | other | LIB | BL | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2244 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.90069 | age_years | random (k~1)
66926 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 161.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 2.8887 | age_years | random (k~1)
66927 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 76 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.3594 | age_years | random (k~1)
66928 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 82.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.4757 | age_years | random (k~1)
66929 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 101 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.8066 | age_years | random (k~1)
66930 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 149 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 2.6651 | age_years | random (k~1)
66931 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 109.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.9586 | age_years | random (k~1)
66932 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 77.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.3862 | age_years | random (k~1)
66933 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 145.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 2.6025 | age_years | random (k~1)
66934 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 97.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.744 | age_years | random (k~1)
66935 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 98.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 1.7618 | age_years | random (k~1)
66946 | 1 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 45 | 180 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 5659 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 334.5216 | age_years | random (k~1)
66949 | 1 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 40 | 160 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 4135 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 244.4331 | age_years | random (k~1)
66950 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 59 | 236 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 6534.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 386.2752 | age_years | random (k~1)
66951 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 9087 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 537.1617 | age_years | random (k~1)
66966 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 2.1 | 4.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 40.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.1695 | age_years | random (k~1)
67019 | 1 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 2238 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 77.4384 | age_years | random (k~1)
67036 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 76 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 2.5231 | age_years | random (k~1)
67037 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 85 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 2.8219 | age_years | random (k~1)
67039 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 92 | 368 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 11494 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 679.4471 | age_years | random (k~1)
67040 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 103 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.041342 | age_years | random (k~1)
67041 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 15 | 30 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 145.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.058401 | age_years | random (k~1)
67042 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 91.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.036726 | age_years | random (k~1)
67043 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 48 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.019266 | age_years | random (k~1)
67044 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 58.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.023481 | age_years | random (k~1)
67083 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 174 | 407.4 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 9349 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 284.2795 | age_years | random (k~1)
67091 | 1 | 19 | 2.5-4.5h | LIB | CS | NEVP | 2024 | 1 | 85 | 340 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 10076 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 285.8156 | age_years | random (k~1)
67092 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 15 | 60 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 1518.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 89.7634 | age_years | random (k~1)
67093 | 0 | 22 | <1.5h | LIB | CS | CISO | 2020 | 0 | 77 | 77 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0125 | ba_g+dur_band+vintage_g | 0 | 0.0125 | 1735 | PARTIAL_AVAILABILITY | inf | 0.13929 | 2.3101 | 0.14479 | 87.049 | age_years | random (k~1)
67122 | 0 | 24 | 1.5-2.5h | LIB | CS | SWPP | 2023 | 0 | 1 | 2.4 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.034286 | ba_g+dur_band+vintage_g | 0 | 0.034286 | 46.5 | PARTIAL_AVAILABILITY | inf | 0.3373 | 2.3101 | 0.14479 | 6.3991 | age_years | random (k~1)
67162 | 0 | 19 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.022989 | ba_g+dur_band+vintage_g | 0 | 0.022989 | 121 | PARTIAL_AVAILABILITY | inf | 0.24108 | 2.3101 | 0.14479 | 11.1648 | age_years | random (k~1)
67170 | 1 | 22 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 2.4 | 8.9 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 116 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 6.8571 | age_years | random (k~1)
67175 | 0 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 300 | 600 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 13821 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 448.5812 | age_years | random (k~1)
67183 | 0 | 14 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 60 | 240 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5888 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 167.0189 | age_years | random (k~1)
67185 | 1 | 18 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | Y | N | inland | ISNE | LIB | CS | 2024+ | 1 | 0 | 0.022989 | ba_g+dur_band+vintage_g | 0 | 0.022989 | 164.5 | PARTIAL_AVAILABILITY | inf | 0.24108 | 2.3101 | 0.14479 | 15.1786 | age_years | random (k~1)
67186 | 0 | 17 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 5 | 22.4 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.022989 | ba_g+dur_band+vintage_g | 0 | 0.022989 | 418 | PARTIAL_AVAILABILITY | inf | 0.24108 | 2.3101 | 0.14479 | 38.5693 | age_years | random (k~1)
67187 | 1 | 14 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 3 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.022989 | ba_g+dur_band+vintage_g | 0 | 0.022989 | 212.5 | PARTIAL_AVAILABILITY | inf | 0.24108 | 2.3101 | 0.14479 | 19.6076 | age_years | random (k~1)
67236 | 1 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 9298.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 282.7439 | age_years | random (k~1)
67237 | 0 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 207.9 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 10541 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 320.5252 | age_years | random (k~1)
67275 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 1.3 | 5.1 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
67278 | 0 | 3 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 1.1 | 2.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.00080276 | age_years | random (k~1)
67281 | 0 | 20 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 4 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
67282 | 0 | 18 | 1.5-2.5h | LIB | CS | NYIS | 2024 | 1 | 5 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.0082711 | dur_band+climate_region | 0 | 0.0082711 | 0 | PARTIAL_AVAILABILITY | inf | 0.094486 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
67284 | 1 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 70.5 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 3063.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 93.1533 | age_years | random (k~1)
67285 | 0 | 19 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 215 | 860 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 23676 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 9.503 | age_years | random (k~1)
67291 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 33868.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 13.5941 | age_years | random (k~1)
67296 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 0.4 | 0.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 1 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 0.026759 | age_years | random (k~1)
67299 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 10309 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 609.398 | age_years | random (k~1)
67300 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1052.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 29.8552 | age_years | random (k~1)
67301 | 0 | 20 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 823.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 23.3594 | age_years | random (k~1)
67302 | 0 | 15 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 723.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 20.5228 | age_years | random (k~1)
67303 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 754 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 21.3879 | age_years | random (k~1)
67304 | 0 | 16 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1109 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 31.4579 | age_years | random (k~1)
67305 | 0 | 18 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1177.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 33.4009 | age_years | random (k~1)
67306 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 1210 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 34.3228 | age_years | random (k~1)
67307 | 0 | 18 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 841 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 23.8558 | age_years | random (k~1)
67321 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 70 | 268 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6484 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 2.6025 | age_years | random (k~1)
67323 | 0 | 9 | 1.5-2.5h | LIB | CS | PSCO | 2025 | 1 | 11.2 | 20 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 201 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 8.4039 | age_years | random (k~1)
67328 | 0 | 6 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 75 | 300 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 8034 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 3.2247 | age_years | random (k~1)
67454 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 170 | 680 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 20475 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 8.2182 | age_years | random (k~1)
67455 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 85 | 340 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 10185.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 4.0882 | age_years | random (k~1)
67474 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 31962 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 12.8289 | age_years | random (k~1)
67489 | 1 | 20 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 45 | 180 | Y | Y | inland | MISO | LIB | CS | 2024+ | 1 | 1 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 7351 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 728.527 | age_years | random (k~1)
67493 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 129.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.4809 | age_years | random (k~1)
67494 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 126.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.3771 | age_years | random (k~1)
67495 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 174.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 6.038 | age_years | random (k~1)
67496 | 1 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 164.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 5.692 | age_years | random (k~1)
67498 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 185 | 740 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 16536 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 977.4959 | age_years | random (k~1)
67503 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 213.8 | 855 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 24594 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 9.8715 | age_years | random (k~1)
67545 | 0 | 14 | >4.5h | LIB | CS | MISO | 2024 | 1 | 5 | 30.6 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.0043103 | dur_band+climate_region | 0 | 0.0043103 | 521 | PARTIAL_AVAILABILITY | inf | 0.050409 | 2.3101 | 0.14479 | 9.0137 | age_years | random (k~1)
67549 | 0 | 7 | 2.5-4.5h | LIB | CT | IPCO | 2025 | 0 | 150 | 600 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 17424 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 494.2489 | age_years | random (k~1)
67573 | 0 | 6 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 82 | 328 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 9267 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 262.8675 | age_years | random (k~1)
67577 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 2.2 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 301.5 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 8.0677 | age_years | random (k~1)
67578 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 1 | 2 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 344 | PARTIAL_AVAILABILITY | inf | 0.076884 | 2.3101 | 0.14479 | 9.205 | age_years | random (k~1)
67579 | 1 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 82 | 328 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 8077.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 477.4869 | age_years | random (k~1)
67598 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 9219 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 280.3265 | age_years | random (k~1)
67680 | 0 | 6 | >4.5h | LIB | CS | CISO | 2025 | 0 | 400 | 1800 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 20756.5 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 939.6108 | age_years | random (k~1)
67695 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 30 | 127 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 1766 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 104.3939 | age_years | random (k~1)
67698 | 0 | 14 | 1.5-2.5h | LIB | CS | PGE | 2024 | 0 | 17 | 34 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 789.5 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 33.0092 | age_years | random (k~1)
67710 | 0 | 5 | 2.5-4.5h | OTH | OT | PNM | 2025 | 1 | 57.8 | 231.4 | N | N | arid | other | other | other | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5449 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 154.5662 | age_years | random (k~1)
67711 | 0 | 6 | 2.5-4.5h | LIB | CS | PGE | 2025 | 0 | 200 | 800 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 15765 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 447.1897 | age_years | random (k~1)
67712 | 0 | 13 | 2.5-4.5h | LIB | CS | PGE | 2024 | 0 | 75 | 300 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 6637.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 188.2792 | age_years | random (k~1)
67721 | 1 | 14 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100.3 | 145 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 3587 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 124.116 | age_years | random (k~1)
67734 | 0 | 9 | 2.5-4.5h | LIB | CT | CISO | 2025 | 0 | 200 | 800 | Y | Y | arid | CISO | LIB | CT | 2024+ | 1 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 22863 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 1351.5051 | age_years | random (k~1)
67736 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 279 | 1116 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 32710 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 1933.5928 | age_years | random (k~1)
67737 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 304 | 440.8 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 10426 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 360.7563 | age_years | random (k~1)
67738 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 204 | 298 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 6925 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 239.6161 | age_years | random (k~1)
67739 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 120 | 174 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 4031 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 139.4791 | age_years | random (k~1)
67740 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 240 | 480 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 12535 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 381.1577 | age_years | random (k~1)
67743 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 0 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
67745 | 0 | 24 | <1.5h | LIB | CS | NYIS | 2022 | 1 | 5 | 2 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.011724 | dur_band+climate_region | 0 | 0.011724 | 0 | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
67752 | 0 | 7 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 102.6 | 205.1 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 7793 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 236.9654 | age_years | random (k~1)
67758 | 0 | 11 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 14 | 56 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 835 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 82.7534 | age_years | random (k~1)
67762 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72.2 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 2744 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 83.4381 | age_years | random (k~1)
67764 | 0 | 5 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 117 | 472 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 11958 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 706.8757 | age_years | random (k~1)
67828 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 25 | 100 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 2611 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 154.3446 | age_years | random (k~1)
67829 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 20 | 80 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 2208.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 130.5515 | age_years | random (k~1)
67843 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 498 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 15.1429 | age_years | random (k~1)
67845 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 454 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 13.805 | age_years | random (k~1)
67850 | 0 | 1 | 2.5-4.5h | LIB | CS | IID | 2025 | 1 | 35 | 140 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 399 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 11.318 | age_years | random (k~1)
67851 | 0 | 14 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 20 | N | Y | inland | PJM | LIB | CS | 2024+ | 0 | 1 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 2762.5 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 109.8052 | age_years | random (k~1)
67855 | 0 | 15 | 2.5-4.5h | LIB | CS | AZPS | 2024.59 | 0 | 200 | 808.4 | N | Y | arid | AZPS | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 11719.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 4.704 | age_years | random (k~1)
67860 | 0 | 21 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 6750 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 205.2504 | age_years | random (k~1)
67861 | 0 | 17 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 6402.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 194.6838 | age_years | random (k~1)
67869 | 0 | 13 | 2.5-4.5h | LIB | CT | PGE | 2024 | 0 | 200 | 800 | N | N | inland | other | LIB | CT | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 21922.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 621.8532 | age_years | random (k~1)
67880 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 21.7 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 10.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0042145 | age_years | random (k~1)
67882 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 10 | 43.4 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 32.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.013045 | age_years | random (k~1)
67883 | 0 | 14 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 0 | 8 | 34.1 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 38 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.015252 | age_years | random (k~1)
67886 | 0 | 24 | 2.5-4.5h | NIB | CS | NYIS | 2023 | 0 | 3 | 12.4 | Y | N | coastal | NYIS | other | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 8 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.003211 | age_years | random (k~1)
67893 | 0 | 12 | 2.5-4.5h | LIB | CS | MISO | 2025 | 1 | 56.3 | 225 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 9601.5 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 951.5647 | age_years | random (k~1)
67898 | 0 | 1 | 2.5-4.5h | LIB | CS | NEVP | 2025 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 8671 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 245.9614 | age_years | random (k~1)
67899 | 0 | 24 | <1.5h | LIB | CS | PJM | 2021 | 0 | 6.2 | 6.2 | N | N | coastal | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.011724 | dur_band+climate_region | 0 | 0.011724 | 735.5 | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 | 34.6113 | age_years | random (k~1)
67905 | 0 | 6 | 2.5-4.5h | LIB | CS | TEPC | 2025 | 0 | 200 | 800 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 23941 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 679.11 | age_years | random (k~1)
67931 | 0 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 113.5 | 454 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 7553.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 446.5116 | age_years | random (k~1)
67948 | 0 | 24 | >4.5h | LIB | CS | SWPP | 2022 | 0 | 1.8 | 9.1 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0043103 | dur_band+climate_region | 0 | 0.0043103 | 28 | PARTIAL_AVAILABILITY | inf | 0.050409 | 2.3101 | 0.14479 | 0.48442 | age_years | random (k~1)
67963 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 125 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.3252 | age_years | random (k~1)
67968 | 0 | 9 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 4356 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 132.4549 | age_years | random (k~1)
67973 | 0 | 3 | <1.5h | LIB | BL | AZPS | 2025 | 0 | 113 | 113 | N | N | arid | AZPS | LIB | BL | 2024+ | 0 | 0 | 0.01104 | dur_band+climate_region | 0 | 0.01104 | 9962 | PARTIAL_AVAILABILITY | inf | 0.12408 | 2.3101 | 0.14479 | 441.4419 | age_years | random (k~1)
68012 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 99.7 | 398.8 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 12581 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 743.7032 | age_years | random (k~1)
68023 | 0 | 2 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 16.7 | 64 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 955.5 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 56.4827 | age_years | random (k~1)
68058 | 0 | 13 | >4.5h | OTH | CS | WACM | 2024 | 0 | 35.4 | 235 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 1684.5 | PARTIAL_AVAILABILITY | inf | 0.12658 | 2.3101 | 0.14479 | 76.2544 | age_years | random (k~1)
68064 | 0 | 17 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 1.2 | 2.1 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 175.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.070442 | age_years | random (k~1)
68069 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2.2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 31.5 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 1.2771 | age_years | random (k~1)
68146 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 4583 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 139.3574 | age_years | random (k~1)
68147 | 0 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 45.5 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 4.5093 | age_years | random (k~1)
68148 | 1 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 43 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 4.2616 | age_years | random (k~1)
68189 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 2254 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 68.5384 | age_years | random (k~1)
68266 | 1 | 24 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.3 | 0.5 | N | Y | inland | CISO | LIB | CS | <=2019 | 0 | 1 | 0.016779 | ba_g+dur_band+vintage_g | 0 | 0.016779 | 5.5 | PARTIAL_AVAILABILITY | inf | 0.18237 | 2.3101 | 0.14479 | 0.3704 | age_years | random (k~1)
68322 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 300 | 1200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 3358 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 198.5021 | age_years | random (k~1)
68324 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 1833 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 108.3545 | age_years | random (k~1)
68335 | 0 | 16 | 2.5-4.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 7.1 | N | Y | coastal | PJM | LIB | CS | 2024+ | 0 | 1 | 0.016591 | dur_band+climate_region | 0 | 0.016591 | 0 | PARTIAL_AVAILABILITY | inf | 0.18053 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
68423 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 5663.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 172.2127 | age_years | random (k~1)
68424 | 0 | 7 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 104.9 | 400 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.024691 | ba_g+dur_band+vintage_g | 0 | 0.024691 | 7156 | PARTIAL_AVAILABILITY | inf | 0.25643 | 2.3101 | 0.14479 | 709.2014 | age_years | random (k~1)
68475 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 58 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 2.209 | age_years | random (k~1)
68476 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 58 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 2.209 | age_years | random (k~1)
68493 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2020.8182 | 0 | 3.3 | 3.3 | N | N | industrial | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.018939 | ba_g+dur_band+vintage_g | 0 | 0.018939 | 87.5 | PARTIAL_AVAILABILITY | inf | 0.2033 | 2.3101 | 0.14479 | 6.6516 | age_years | random (k~1)
68496 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 60 | 120 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 1722 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 52.3617 | age_years | random (k~1)
68522 | 0 | 9 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
68523 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
68524 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0012041 | age_years | random (k~1)
68525 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
68547 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 94 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 5.5566 | age_years | random (k~1)
68548 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 0.7 | 2.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 52 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 3.0739 | age_years | random (k~1)
68576 | 0 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 260 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 6390 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 181.2586 | age_years | random (k~1)
68577 | 0 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 40 | 160 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 4343.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 123.2076 | age_years | random (k~1)
68596 | 0 | 1 | 2.5-4.5h | LIB | CS | PACE | 2025 | 0 | 200 | 800 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 2851 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 80.8714 | age_years | random (k~1)
68605 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2021 | 1 | 0.5 | 1.3 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0.013021 | ba_g+dur_band+vintage_g | 0 | 0.013021 | 9 | PARTIAL_AVAILABILITY | inf | 0.14465 | 2.3101 | 0.14479 | 0.47037 | age_years | random (k~1)
68611 | 0 | 10 | 1.5-2.5h | LIB | CS | CEA | 2024 | 0 | 40 | 80 | N | N | coastal | other | LIB | CS | 2024+ | 0 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 1 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 0.04181 | age_years | random (k~1)
68613 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 228.7 | 228.7 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 5939 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 205.4989 | age_years | random (k~1)
68617 | 0 | 2 | 2.5-4.5h | LIB | CT | PNM | 2025 | 0 | 100 | 400 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 11974.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 339.6684 | age_years | random (k~1)
68679 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 45.5 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 1.8447 | age_years | random (k~1)
68680 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 50 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 2.0272 | age_years | random (k~1)
68683 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 337.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 10.2625 | age_years | random (k~1)
68684 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 386.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 11.7525 | age_years | random (k~1)
68685 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 12.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 216 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 7.4739 | age_years | random (k~1)
68686 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 33 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 1.0034 | age_years | random (k~1)
68687 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 43.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 1.3227 | age_years | random (k~1)
68742 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 50 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 2.0272 | age_years | random (k~1)
68743 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3.3 | 3.3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.010101 | ba_g+dur_band+vintage_g | 0 | 0.010101 | 119 | PARTIAL_AVAILABILITY | inf | 0.11415 | 2.3101 | 0.14479 | 4.8247 | age_years | random (k~1)
68773 | 0 | 23 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 2.8 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.0071942 | ba_g+dur_band+vintage_g | 0 | 0.0071942 | 68.5 | PARTIAL_AVAILABILITY | inf | 0.082709 | 2.3101 | 0.14479 | 1.978 | age_years | random (k~1)
68801 | 0 | 3 | 2.5-4.5h | LIB | CS | WALC | 2025 | 0 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 239 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 6.7795 | age_years | random (k~1)
68802 | 0 | 8 | <1.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 65 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 8224 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 326.8916 | age_years | random (k~1)
68809 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 220 | 440 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 189 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 5.747 | age_years | random (k~1)
68816 | 0 | 20 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 2.6 | 5.3 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 21.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 0.0086296 | age_years | random (k~1)
68842 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 7672 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 265.4635 | age_years | random (k~1)
68868 | 0 | 5 | 2.5-4.5h | LIB | CS | PNM | 2025 | 1 | 50 | 200 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5754 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 163.2179 | age_years | random (k~1)
68874 | 0 | 8 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 13 | 45 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 1183 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 61.3712 | age_years | random (k~1)
68875 | 0 | 7 | 2.5-4.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 22.4 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.022989 | ba_g+dur_band+vintage_g | 0 | 0.022989 | 334 | PARTIAL_AVAILABILITY | inf | 0.24108 | 2.3101 | 0.14479 | 30.8185 | age_years | random (k~1)
68878 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 165 | 165 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 6053 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 209.4435 | age_years | random (k~1)
68879 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 5874 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 178.6135 | age_years | random (k~1)
68891 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 84 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 4.9655 | age_years | random (k~1)
68895 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 236.3 | 236.3 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0044563 | ba_g+dur_band+vintage_g | 0 | 0.0044563 | 4965.5 | PARTIAL_AVAILABILITY | inf | 0.052071 | 2.3101 | 0.14479 | 88.8166 | age_years | random (k~1)
68896 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 123.3 | 123 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 3260.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 112.8185 | age_years | random (k~1)
68906 | 0 | 1 | <1.5h | LIB | CS | DOPD | 2025 | 1 | 200 | 200 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 9840 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 391.1251 | age_years | random (k~1)
68912 | 0 | 6 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 50 | 200 | Y | Y | inland | ERCO | LIB | CS | 2024+ | 1 | 1 | 0.012925 | dur_band+climate_region | 0 | 0.012925 | 1967 | PARTIAL_AVAILABILITY | inf | 0.14367 | 2.3101 | 0.14479 | 102.0432 | age_years | random (k~1)
68997 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 0.7 | 2.6 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.014728 | ba_g+dur_band+vintage_g | 0 | 0.014728 | 55 | PARTIAL_AVAILABILITY | inf | 0.16199 | 2.3101 | 0.14479 | 3.2512 | age_years | random (k~1)
69023 | 0 | 2 | 1.5-2.5h | LIB | CS | CPLE | 2025 | 0 | 100 | 200 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2900.5 | PARTIAL_AVAILABILITY | inf | 0.0011993 | 2.3101 | 0.14479 | 1.1642 | age_years | random (k~1)
69026 | 0 | 2 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 283.2 | 283.2 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 13663 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 472.7617 | age_years | random (k~1)
69045 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 10338 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 314.3524 | age_years | random (k~1)
69122 | 0 | 4 | <1.5h | LIB | CS | PSCO | 2025 | 0 | 100 | 100 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 11212 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 445.6601 | age_years | random (k~1)
69128 | 1 | 12 | 1.5-2.5h | LIB | CS | PJM | 2023 | 0 | 1.1 | 2.3 | N | Y | coastal | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.0094887 | dur_band+climate_region | 0 | 0.0094887 | 58 | PARTIAL_AVAILABILITY | inf | 0.10762 | 2.3101 | 0.14479 | 2.209 | age_years | random (k~1)
69171 | 0 | 2 | 2.5-4.5h | LIB | CS | DUK | 2025 | 0 | 50 | 200 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0070671 | ba_g+dur_band+vintage_g | 0 | 0.0070671 | 5839.5 | PARTIAL_AVAILABILITY | inf | 0.081309 | 2.3101 | 0.14479 | 165.6431 | age_years | random (k~1)
69187 | 0 | 1 | 1.5-2.5h | LIB | CS | TEC | 2019 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0 | 0.0081522 | 24 | PARTIAL_AVAILABILITY | inf | 0.093193 | 2.3101 | 0.14479 | 0.78531 | age_years | random (k~1)
69190 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 4 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 0.50315 | age_years | random (k~1)
69191 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 8 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 1.0063 | age_years | random (k~1)
69210 | 1 | 12 | 1.5-2.5h | LIB | CS | PGE | 2024 | 1 | 1 | 2 | Y | N | industrial | other | LIB | CS | 2024+ | 1 | 0 | 0.010417 | ba_g+dur_band+vintage_g | 0 | 0.010417 | 6.5 | PARTIAL_AVAILABILITY | inf | 0.1175 | 2.3101 | 0.14479 | 0.27177 | age_years | random (k~1)
69244 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 58.3 | 114 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 2411.5 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 73.3276 | age_years | random (k~1)
69250 | 0 | 8 | <1.5h | NAB | CS | FPC | 2025 | 0 | 5 | 5 | N | Y | inland | other | other | CS | 2024+ | 0 | 1 | 0.009903 | dur_band+climate_region | 0 | 0.009903 | 424 | PARTIAL_AVAILABILITY | inf | 0.11205 | 2.3101 | 0.14479 | 16.8534 | age_years | random (k~1)
69288 | 0 | 10 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.3 | 0.6 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.031339 | ba_g+dur_band+vintage_g | 0 | 0.031339 | 7.5 | PARTIAL_AVAILABILITY | inf | 0.31344 | 2.3101 | 0.14479 | 0.94341 | age_years | random (k~1)
69298 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 300 | 680 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 23114 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 702.8383 | age_years | random (k~1)
69300 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 0 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
69301 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 20 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 0.69203 | age_years | random (k~1)
69302 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 88 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 3.0449 | age_years | random (k~1)
69331 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 8 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 0.27681 | age_years | random (k~1)
69333 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 20 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 0.69203 | age_years | random (k~1)
69334 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 2.3 | 4.5 | N | N | inland | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 18 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 1.2959 | age_years | random (k~1)
69344 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 2 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 0.069203 | age_years | random (k~1)
69345 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 189.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 6.557 | age_years | random (k~1)
69346 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 187 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 6.4705 | age_years | random (k~1)
69347 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 221.5 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 7.6643 | age_years | random (k~1)
69348 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 47 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 1.6263 | age_years | random (k~1)
69349 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 39 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 1.3495 | age_years | random (k~1)
69350 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 23.2 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 368.5 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 11.9602 | age_years | random (k~1)
69353 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 19.8 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080863 | ba_g+dur_band+vintage_g | 0 | 0.0080863 | 109.5 | PARTIAL_AVAILABILITY | inf | 0.092476 | 2.3101 | 0.14479 | 3.554 | age_years | random (k~1)
69358 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 11.3 | 11.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.008 | ba_g+dur_band+vintage_g | 0 | 0.008 | 0 | PARTIAL_AVAILABILITY | inf | 0.091536 | 2.3101 | 0.14479 | 0 | age_years | random (k~1)
69365 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 206 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 7.1279 | age_years | random (k~1)
69366 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 122 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 4.2214 | age_years | random (k~1)
69407 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 75 | 75 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 2149 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 74.3589 | age_years | random (k~1)
69411 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 300 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 21.5989 | age_years | random (k~1)
69413 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 391 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 28.1505 | age_years | random (k~1)
69414 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 180 | 360 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 3630 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 110.3791 | age_years | random (k~1)
69415 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.017937 | ba_g+dur_band+vintage_g | 0 | 0.017937 | 437 | PARTIAL_AVAILABILITY | inf | 0.19366 | 2.3101 | 0.14479 | 31.4623 | age_years | random (k~1)
69454 | 0 | 9 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 561 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 17.0586 | age_years | random (k~1)
69456 | 0 | 8 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 418 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 12.7103 | age_years | random (k~1)
69459 | 0 | 5 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 369 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 11.2204 | age_years | random (k~1)
69460 | 0 | 12 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.0075758 | ba_g+dur_band+vintage_g | 0 | 0.0075758 | 478 | PARTIAL_AVAILABILITY | inf | 0.086899 | 2.3101 | 0.14479 | 14.5348 | age_years | random (k~1)
69576 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 13.7 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0086207 | ba_g+dur_band+vintage_g | 0 | 0.0086207 | 215 | PARTIAL_AVAILABILITY | inf | 0.098277 | 2.3101 | 0.14479 | 7.4393 | age_years | random (k~1)
69727 | 0 | 12 | <1.5h | LIB | CS | PJM | 2022 | 1 | 10.1 | 10.1 | N | Y | inland | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.018519 | ba_g+dur_band+vintage_g | 0 | 0.018519 | 98 | PARTIAL_AVAILABILITY | inf | 0.19926 | 2.3101 | 0.14479 | 7.2843 | age_years | random (k~1)
69803 | 0 | 7 | <1.5h | LIB | CT | NYIS | 2025 | 0 | 4.6 | 4.6 | N | N | coastal | NYIS | LIB | CT | 2024+ | 0 | 0 | 0.011724 | dur_band+climate_region | 0 | 0.011724 | 126 | PARTIAL_AVAILABILITY | inf | 0.13124 | 2.3101 | 0.14479 | 5.9293 | age_years | random (k~1)
141 | 0 | 52 | 2.5-4.5h | LIB | CS | SRP | 2021 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.22001 | 0.0040625 | 1432 | THERMAL_AUX | 0.96019 | 0.04644 | 9.7549 | 0.043107 | 29.3554 | age_years | infant mortality (k<1)
260 | 0 | 55 | 2.5-4.5h | LIB | BL | CISO | 2021.9333 | 1 | 750 | 3000 | Y | N | coastal | CISO | LIB | BL | 2022-23 | 1 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.48149 | 0.0084059 | 0 | THERMAL_AUX | 0.96019 | 0.09146 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
389 | 0 | 84 | <1.5h | LIB | BL | IID | 2016 | 0 | 30 | 20 | N | Y | arid | other | LIB | BL | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.22102 | 0.0025264 | 379.5 | THERMAL_AUX | 0.96019 | 0.029407 | 9.7549 | 0.043107 | 4.8381 | age_years | infant mortality (k<1)
645 | 0 | 33 | 1.5-2.5h | LIB | CS | TEC | 2017 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.21886 | 0.006368 | 5 | THERMAL_AUX | 0.96019 | 0.07089 | 9.7549 | 0.043107 | 0.16067 | age_years | infant mortality (k<1)
1016 | 0 | 48 | <1.5h | LIB | CS | CPLE | 2019 | 1 | 0.5 | 0.5 | N | N | inland | CPLE | LIB | CS | <=2019 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.21432 | 0.0042873 | 20.5 | THERMAL_AUX | 0.96019 | 0.048881 | 9.7549 | 0.043107 | 0.44349 | age_years | infant mortality (k<1)
1482 | 1 | 33 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0022222 | ba_g+dur_band+vintage_g | 0.070954 | 0.0042147 | 585 | THERMAL_AUX | 0.96019 | 0.048094 | 9.7549 | 0.043107 | 12.4416 | age_years | infant mortality (k<1)
1507 | 0 | 84 | <1.5h | LIB | CS | ISNE | 2016 | 0 | 16.7 | 10.9 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0087719 | ba_g+dur_band+vintage_g | 0.43419 | 0.0049632 | 288 | THERMAL_AUX | 0.96019 | 0.056147 | 9.7549 | 0.043107 | 7.2129 | age_years | infant mortality (k<1)
1615 | 0 | 36 | >4.5h | LIB | BL | ISNE | 2019 | 0 | 6 | 48 | N | N | coastal | ISNE | LIB | BL | <=2019 | 0 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 1 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.00050461 | age_years | infant mortality (k<1)
1682 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 3 | 6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 27.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.27708 | age_years | infant mortality (k<1)
2324 | 2 | 23 | <1.5h | LIB | CS | NEVP | 2023 | 0 | 220 | 220 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0.23043 | 0.029657 | 13845.5 | THERMAL_AUX | 0.96019 | 0.2612 | 9.7549 | 0.043107 | 2071.979 | age_years | infant mortality (k<1)
2830 | 0 | 84 | <1.5h | LIB | CS | PJM | 2015 | 1 | 4 | 1.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13165 | 0.0015049 | 91.5 | THERMAL_AUX | 0.96019 | 0.017732 | 9.7549 | 0.043107 | 0.69485 | age_years | infant mortality (k<1)
6304 | 0 | 36 | <1.5h | LIB | CT |  | 2015 | 1 | 1.2 | 1 | N | N | coastal | other | LIB | CT | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 4 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 0.058366 | age_years | infant mortality (k<1)
6377 | 0 | 36 | <1.5h | LIB | CS | PJM | 2017 | 1 | 1 | 1 | Y | N | coastal | PJM | LIB | CS | <=2019 | 1 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.061014 | 0.0016274 | 3 | THERMAL_AUX | 0.96019 | 0.019147 | 9.7549 | 0.043107 | 0.024635 | age_years | infant mortality (k<1)
8063 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 269.1 | 263 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 2501.5 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 77.842 | age_years | infant mortality (k<1)
10156 | 0 | 34 | <1.5h | LIB | CS | CISO | 2023 | 0 | 16 | 16 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.006192 | ba_g+dur_band+vintage_g | 0.17983 | 0.0050785 | 13.5 | THERMAL_AUX | 0.96019 | 0.057374 | 9.7549 | 0.043107 | 0.34596 | age_years | infant mortality (k<1)
10444 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 69 | 69 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00041641 | 0.0001 | 4203 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 2.1209 | age_years | infant mortality (k<1)
10493 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0022222 | ba_g+dur_band+vintage_g | 0.052621 | 0.0021053 | 613.5 | THERMAL_AUX | 0.96019 | 0.024628 | 9.7549 | 0.043107 | 6.5175 | age_years | infant mortality (k<1)
50064 | 0 | 24 | <1.5h | LIB | CS | CISO | 2022 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.006192 | ba_g+dur_band+vintage_g | 0.13402 | 0.0053621 | 12 | THERMAL_AUX | 0.96019 | 0.060381 | 9.7549 | 0.043107 | 0.32469 | age_years | infant mortality (k<1)
50300 | 0 | 84 | <1.5h | LIB | BL | CISO | 2019.5 | 0 | 40 | 40 | N | Y | inland | CISO | LIB | BL | <=2019 | 0 | 1 | 0.0054568 | dur_band+climate_region | 0.32312 | 0.0036936 | 1235.5 | THERMAL_AUX | 0.96019 | 0.042405 | 9.7549 | 0.043107 | 23.0273 | age_years | infant mortality (k<1)
54134 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 0 | 20 | 20 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 729.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.36811 | age_years | infant mortality (k<1)
54296 | 0 | 76 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.3 | 0.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0078529 | 0.0001 | 1 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.00050461 | age_years | infant mortality (k<1)
54639 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 14 | 14 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 751.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.37921 | age_years | infant mortality (k<1)
55370 | 0 | 36 | <1.5h | LIB | CT | PJM | 2016 | 0 | 10.4 | 10.4 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.061014 | 0.0016274 | 0 | THERMAL_AUX | 0.96019 | 0.019147 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
56961 | 0 | 84 | <1.5h | LIB | BL | ERCO | 2012 | 0 | 36 | 13.6 | N | N | arid | ERCO | LIB | BL | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0086724 | 0.0001 | 227.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.1148 | age_years | infant mortality (k<1)
56981 | 0 | 84 | <1.5h | LIB | CS | ERCO | 2018 | 1 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0086724 | 0.0001 | 43.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02195 | age_years | infant mortality (k<1)
56984 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2018 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 68 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.034313 | age_years | infant mortality (k<1)
57206 | 0 | 36 | 1.5-2.5h | LIB | CS |  | 2022 | 0 | 46.5 | 93 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 268.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.13549 | age_years | infant mortality (k<1)
57242 | 0 | 30 | 2.5-4.5h | LIB | CS |  | 2022 | 1 | 39 | 156 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10458 | 0.0033474 | 3159 | THERMAL_AUX | 0.96019 | 0.038587 | 9.7549 | 0.043107 | 53.3587 | age_years | infant mortality (k<1)
57325 | 0 | 84 | <1.5h | LIB | CS | PJM | 2014 | 1 | 20 | 8.3 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13165 | 0.0015049 | 446 | THERMAL_AUX | 0.96019 | 0.017732 | 9.7549 | 0.043107 | 3.3869 | age_years | infant mortality (k<1)
57447 | 0 | 78 | <1.5h | LIB | CS | PJM | 2011 | 0 | 16 | 16 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.12341 | 0.0015192 | 628.5 | THERMAL_AUX | 0.96019 | 0.017898 | 9.7549 | 0.043107 | 4.8181 | age_years | infant mortality (k<1)
57560 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 19 | 76 | Y | N | arid | AZPS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 1891 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.95421 | age_years | infant mortality (k<1)
57561 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 1278.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.64514 | age_years | infant mortality (k<1)
57562 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 1289 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.65044 | age_years | infant mortality (k<1)
57563 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 16 | 48 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 1141 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.57576 | age_years | infant mortality (k<1)
57583 | 0 | 84 | <1.5h | NIB | BL |  | 2003 | 0 | 40 | 11 | N | Y | inland | other | other | BL | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.22102 | 0.0025264 | 17 | THERMAL_AUX | 0.96019 | 0.029407 | 9.7549 | 0.043107 | 0.21673 | age_years | infant mortality (k<1)
57584 | 0 | 78 | 1.5-2.5h | LIB | CS | CISO | 2015 | 0 | 2.5 | 5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0080579 | 0.0001 | 13.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0068122 | age_years | infant mortality (k<1)
57996 | 0 | 36 | <1.5h | LIB | CS |  | 2012 | 0 | 11 | 4.4 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 106.5 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 1.554 | age_years | infant mortality (k<1)
57997 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 35 | 105 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 2396 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.209 | age_years | infant mortality (k<1)
58236 | 0 | 62 | 1.5-2.5h | LIB | CS | MISO | 2020 | 1 | 0.3 | 0.6 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.14696 | 0.002276 | 0 | THERMAL_AUX | 0.96019 | 0.026571 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
58256 | 0 | 41 | >4.5h | NAB | CS | PNM | 2012 | 1 | 1.8 | 8.3 | N | N | inland | other | other | CS | <=2019 | 0 | 0 | 0.0086207 | dur_band+climate_region | 0.26906 | 0.0063012 |  | THERMAL_AUX | 0.96019 | 0.070199 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
58383 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 14 | 42 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 1015.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.51243 | age_years | infant mortality (k<1)
58405 | 0 | 36 | <1.5h | LIB | CS |  | 2012 | 1 | 3 | 3 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 0.5 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 0.0072957 | age_years | infant mortality (k<1)
58462 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 230 | 920 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.0062643 | 23132.5 | THERMAL_AUX | 0.96019 | 0.069817 | 9.7549 | 0.043107 | 731.2206 | age_years | infant mortality (k<1)
58585 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2017 | 1 | 0.5 | 1 | N | N | industrial | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 2 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0010092 | age_years | infant mortality (k<1)
58639 | 0 | 48 | <1.5h | LIB | CS |  | 2015 | 1 | 6 | 4.6 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.13951 | 0.0027908 |  | THERMAL_AUX | 0.96019 | 0.032383 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
59020 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 32 | 96 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 2334.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.178 | age_years | infant mortality (k<1)
59118 | 2 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 16.4 | 32.8 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.27468 | 0.03388 | 548.5 | THERMAL_AUX | 0.96019 | 0.28752 | 9.7549 | 0.043107 | 93.7724 | age_years | infant mortality (k<1)
59150 | 0 | 36 | <1.5h | LIB | CS | CISO | 2021 | 1 | 75 | 75 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 7373 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.7205 | age_years | infant mortality (k<1)
59256 | 0 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 2 | 14 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0032181 | 0.0001 |  | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
59257 | 0 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 4 | 28 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0032181 | 0.0001 |  | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
59444 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 10 | 30 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 840.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.42412 | age_years | infant mortality (k<1)
59871 | 0 | 13 | <1.5h | LIB | CS | CISO | 2024 | 1 | 150 | 150 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 12527 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 6.3212 | age_years | infant mortality (k<1)
59939 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021.4861 | 1 | 72 | 288 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.0062643 | 6176.5 | THERMAL_AUX | 0.96019 | 0.069817 | 9.7549 | 0.043107 | 195.2398 | age_years | infant mortality (k<1)
59949 | 0 | 70 | <1.5h | LIB | BL | PJM | 2015 | 0 | 11 | 5 | N | N | inland | PJM | LIB | BL | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.11217 | 0.0015387 |  | THERMAL_AUX | 0.96019 | 0.018123 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
59957 | 0 | 84 | <1.5h | LIB | CT | PJM | 2014.75 | 1 | 36 | 13.5 | Y | Y | inland | PJM | LIB | CT | <=2019 | 1 | 1 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13165 | 0.0015049 | 0 | THERMAL_AUX | 0.96019 | 0.017732 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
59959 | 0 | 34 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.0017331 | ba_g+dur_band+vintage_g | 0.05782 | 0.0016329 |  | THERMAL_AUX | 0.96019 | 0.019211 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
59960 | 1 | 30 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.0017331 | ba_g+dur_band+vintage_g | 0.051367 | 0.0033563 |  | THERMAL_AUX | 0.96019 | 0.038686 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
59993 | 0 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 10 | 40 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0.26714 | 0.0030536 | 13 | THERMAL_AUX | 0.96019 | 0.035322 | 9.7549 | 0.043107 | 0.20031 | age_years | infant mortality (k<1)
60014 | 0 | 48 | 1.5-2.5h | LIB | CS | FPL | 2021 | 1 | 409 | 900 | N | Y | coastal | other | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0049741 | 0.0001 | 6521 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.2906 | age_years | infant mortality (k<1)
60016 | 0 | 74 | <1.5h | LIB | CS | BPAT | 2015.5 | 0 | 2 | 1 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.19997 | 0.0025947 | 0 | THERMAL_AUX | 0.96019 | 0.030178 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60061 | 0 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 4 | 16 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0.26714 | 0.0030536 | 110.5 | THERMAL_AUX | 0.96019 | 0.035322 | 9.7549 | 0.043107 | 1.7027 | age_years | infant mortality (k<1)
60092 | 0 | 57 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0 | dur_band+climate_region | 0.0059013 | 0.0001 | 12058.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 6.0848 | age_years | infant mortality (k<1)
60093 | 0 | 36 | >4.5h | LIB | CS | CISO | 2021 | 1 | 63 | 301.2 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 7022 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.5434 | age_years | infant mortality (k<1)
60094 | 0 | 51 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0 | dur_band+climate_region | 0.0052834 | 0.0001 | 11924 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 6.017 | age_years | infant mortality (k<1)
60095 | 0 | 36 | <1.5h | LIB | CS | CISO | 2022 | 1 | 47 | 47 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.006192 | ba_g+dur_band+vintage_g | 0.18841 | 0.0050253 | 4070 | THERMAL_AUX | 0.96019 | 0.056808 | 9.7549 | 0.043107 | 103.2078 | age_years | infant mortality (k<1)
60123 | 0 | 76 | 2.5-4.5h | LIB | CS | ERCO | 2019 | 1 | 9.9 | 42 | N | Y | arid | ERCO | LIB | CS | <=2019 | 0 | 1 | 0.0073412 | dur_band+climate_region | 0.36751 | 0.0046432 | 29.5 | THERMAL_AUX | 0.96019 | 0.052721 | 9.7549 | 0.043107 | 0.69119 | age_years | infant mortality (k<1)
60231 | 0 | 36 | <1.5h | LIB | CS | CISO | 2016 | 1 | 2 | 2 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.002069 | dur_band+climate_region | 0.071986 | 0.00192 | 25 | THERMAL_AUX | 0.96019 | 0.022511 | 9.7549 | 0.043107 | 0.24222 | age_years | infant mortality (k<1)
60233 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 88 | 352 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.0062643 | 8494.5 | THERMAL_AUX | 0.96019 | 0.069817 | 9.7549 | 0.043107 | 268.512 | age_years | infant mortality (k<1)
60249 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2020 | 0 | 1 | 2 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0.32093 | 0.0085598 | 0 | THERMAL_AUX | 0.96019 | 0.092976 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60297 | 1 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 10 | 4.1 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.061014 | 0.0033222 | 75.5 | THERMAL_AUX | 0.96019 | 0.038308 | 9.7549 | 0.043107 | 1.2657 | age_years | infant mortality (k<1)
60299 | 0 | 24 | <1.5h | LIB | CS | PJM | 2016 | 1 | 7 | 7 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.04152 | 0.0016611 |  | THERMAL_AUX | 0.96019 | 0.019536 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
60316 | 0 | 24 | <1.5h | LIB | CS | PJM | 2022 | 1 | 40 | 48 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0.18794 | 0.0075191 | 308 | THERMAL_AUX | 0.96019 | 0.082624 | 9.7549 | 0.043107 | 11.6861 | age_years | infant mortality (k<1)
60390 | 0 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 31.5 | 12.5 | N | Y | inland | PJM | LIB | CT | <=2019 | 0 | 1 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13165 | 0.0015049 | 0 | THERMAL_AUX | 0.96019 | 0.017732 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60441 | 0 | 67 | <1.5h | LIB | BL | PGE | 2013 | 1 | 5 | 5 | N | N | inland | other | LIB | BL | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.18454 | 0.0026447 |  | THERMAL_AUX | 0.96019 | 0.030741 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
60444 | 0 | 36 | 1.5-2.5h | LIB | CT | PSEI | 2016 | 0 | 2 | 4.4 | Y | Y | inland | other | LIB | CT | <=2019 | 1 | 1 | 0.0081522 | ba_g+dur_band+vintage_g | 0.23409 | 0.0062438 | 0 | THERMAL_AUX | 0.96019 | 0.069605 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60467 | 0 | 14 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 41 | 164 | Y | N | arid | AZPS | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0014559 | 0.0001 | 3200.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.615 | age_years | infant mortality (k<1)
60491 | 0 | 64 | <1.5h | LIB | CT | LDWP | 2019 | 1 | 1.5 | 1.5 | N | Y | arid | other | LIB | CT | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.17775 | 0.0026668 | 0 | THERMAL_AUX | 0.96019 | 0.030989 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60506 | 0 | 48 | <1.5h | NAB | BL | ERCO | 2010 | 1 | 4 | 4 | N | N | arid | ERCO | other | BL | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0049741 | 0.0001 |  | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
60518 | 0 | 72 | 1.5-2.5h | LIB | CS | ISNE | 2015 | 1 | 2 | 3.4 | N | Y | inland | ISNE | LIB | CS | <=2019 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0074427 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60546 | 0 | 36 | 2.5-4.5h | LIB | CS |  | 2017 | 1 | 13 | 52 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.0041667 | ba_g+dur_band+vintage_g | 0.13511 | 0.0036037 | 1150.5 | THERMAL_AUX | 0.96019 | 0.041417 | 9.7549 | 0.043107 | 20.9214 | age_years | infant mortality (k<1)
60562 | 0 | 71 | 2.5-4.5h | LIB | OT | ISNE | 2018 | 1 | 1 | 4 | N | Y | inland | ISNE | LIB | other | <=2019 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0073401 | 0.0001 | 52.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.026492 | age_years | infant mortality (k<1)
60565 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2013.3333 | 1 | 1.5 | 4.5 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0055556 | ba_g+dur_band+vintage_g | 0.17238 | 0.0045979 | 0 | THERMAL_AUX | 0.96019 | 0.052234 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60566 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2015 | 1 | 1 | 2 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 1082.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.54624 | age_years | infant mortality (k<1)
60567 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2015 | 1 | 2 | 6 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0055556 | ba_g+dur_band+vintage_g | 0.17238 | 0.0045979 | 0 | THERMAL_AUX | 0.96019 | 0.052234 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60568 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2014 | 1 | 1 | 3 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0055556 | ba_g+dur_band+vintage_g | 0.17238 | 0.0045979 | 0 | THERMAL_AUX | 0.96019 | 0.052234 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60569 | 0 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 7.5 | 30 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0055556 | ba_g+dur_band+vintage_g | 0.32706 | 0.0037386 | 405 | THERMAL_AUX | 0.96019 | 0.042899 | 9.7549 | 0.043107 | 7.6404 | age_years | infant mortality (k<1)
60570 | 0 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.0055556 | ba_g+dur_band+vintage_g | 0.32706 | 0.0037386 | 0 | THERMAL_AUX | 0.96019 | 0.042899 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60607 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2017 | 1 | 0.8 | 3.3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 3.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0017661 | age_years | infant mortality (k<1)
60609 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2016 | 1 | 0.8 | 3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60641 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 10 | 40 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.16987 | 0.0067964 | 758.5 | THERMAL_AUX | 0.96019 | 0.075292 | 9.7549 | 0.043107 | 26.0127 | age_years | infant mortality (k<1)
60649 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.010638 | ba_g+dur_band+vintage_g | 0.28513 | 0.007605 | 165.5 | THERMAL_AUX | 0.96019 | 0.083488 | 9.7549 | 0.043107 | 6.3511 | age_years | infant mortality (k<1)
60654 | 0 | 48 | 2.5-4.5h | LIB | CS | WALC | 2021 | 1 | 90 | 360 | Y | Y | arid | other | LIB | CS | 2020-21 | 1 | 1 | 0.0052083 | ba_g+dur_band+vintage_g | 0.20658 | 0.0041324 | 7749.5 | THERMAL_AUX | 0.96019 | 0.047201 | 9.7549 | 0.043107 | 161.5962 | age_years | infant mortality (k<1)
60656 | 0 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 20 | 7.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.061014 | 0.0016274 | 2935 | THERMAL_AUX | 0.96019 | 0.019147 | 9.7549 | 0.043107 | 24.1016 | age_years | infant mortality (k<1)
60660 | 0 | 33 | <1.5h | LIB | CS | PJM | 2016 | 0 | 6 | 2 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.056215 | 0.0016357 | 593 | THERMAL_AUX | 0.96019 | 0.019243 | 9.7549 | 0.043107 | 4.8945 | age_years | infant mortality (k<1)
60661 | 2 | 24 | 2.5-4.5h | LIB | CS | CISO | 2016 | 0 | 20 | 80 | Y | Y | arid | CISO | LIB | CS | <=2019 | 1 | 1 | 0.0055556 | ba_g+dur_band+vintage_g | 0.12193 | 0.015039 | 1040.5 | THERMAL_AUX | 0.96019 | 0.15242 | 9.7549 | 0.043107 | 78.9614 | age_years | infant mortality (k<1)
60690 | 0 | 84 | <1.5h | LIB | CS | ERCO | 2017 | 0 | 30 | 12.6 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0086724 | 0.0001 | 463.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.23389 | age_years | infant mortality (k<1)
60698 | 0 | 65 | <1.5h | LIB | CS | CISO | 2020 | 1 | 20 | 9 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0067239 | 0.0001 | 14 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0070645 | age_years | infant mortality (k<1)
60760 | 0 | 24 | 2.5-4.5h | LIB | BL | CISO | 2016 | 0 | 2 | 8 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.0055556 | ba_g+dur_band+vintage_g | 0.12193 | 0.0048782 |  | THERMAL_AUX | 0.96019 | 0.055239 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
60815 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2017 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0087719 | ba_g+dur_band+vintage_g | 0.24749 | 0.006601 | 6.5 | THERMAL_AUX | 0.96019 | 0.073289 | 9.7549 | 0.043107 | 0.21651 | age_years | infant mortality (k<1)
60906 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.1 | 6.1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 23 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.011606 | age_years | infant mortality (k<1)
60959 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2017 | 1 | 2 | 3.9 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 7 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0035323 | age_years | infant mortality (k<1)
60974 | 0 | 36 | <1.5h | LIB | CS | LDWP | 2017 | 1 | 2 | 1 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 0 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
60996 | 0 | 36 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 2.5 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 74 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 1.0798 | age_years | infant mortality (k<1)
61068 | 0 | 72 | >4.5h | LIB | CS |  | 2018 | 1 | 20 | 100 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0 | dur_band+climate_region | 0.0074427 | 0.0001 | 1857 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.93706 | age_years | infant mortality (k<1)
61098 | 0 | 55 | <1.5h | LIB | CS | NEVP | 2021 | 1 | 25 | 25 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0056954 | 0.0001 | 2105 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.0622 | age_years | infant mortality (k<1)
61107 | 0 | 36 | 2.5-4.5h | FLB | CS | CISO | 2017 | 1 | 2 | 8 | N | Y | coastal | CISO | other | CS | <=2019 | 0 | 1 | 0.0055556 | ba_g+dur_band+vintage_g | 0.17238 | 0.0045979 | 106 | THERMAL_AUX | 0.96019 | 0.052234 | 9.7549 | 0.043107 | 2.4593 | age_years | infant mortality (k<1)
61168 | 0 | 14 | 2.5-4.5h | LIB | CS | LDWP | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.048996 | 0.0033604 | 14026 | THERMAL_AUX | 0.96019 | 0.038731 | 9.7549 | 0.043107 | 237.8396 | age_years | infant mortality (k<1)
61169 | 0 | 6 | 2.5-4.5h | LIB | CS | LDWP | 2025 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.021603 | 0.0034572 | 13805 | THERMAL_AUX | 0.96019 | 0.039802 | 9.7549 | 0.043107 | 240.835 | age_years | infant mortality (k<1)
61186 | 0 | 32 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 1 | 1.1 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0033216 | 0.0001 | 2 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0010092 | age_years | infant mortality (k<1)
61197 | 0 | 84 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 10 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.22102 | 0.0025264 | 6 | THERMAL_AUX | 0.96019 | 0.029407 | 9.7549 | 0.043107 | 0.076491 | age_years | infant mortality (k<1)
61204 | 4 | 60 | 2.5-4.5h | LIB | BL | CISO | 2021 | 0 | 100 | 400 | Y | N | coastal | CISO | LIB | BL | 2020-21 | 1 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.33845 | 0.027979 | 7946.5 | THERMAL_AUX | 0.96019 | 0.25018 | 9.7549 | 0.043107 | 1121.9341 | age_years | infant mortality (k<1)
61334 | 0 | 36 | >4.5h | LIB | CT | MISO | 2019 | 1 | 1 | 4.6 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.0086207 | dur_band+climate_region | 0.24426 | 0.006515 | 0 | THERMAL_AUX | 0.96019 | 0.072405 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61365 | 0 | 31 | <1.5h | LIB | CS | CISO | 2023 | 0 | 40 | 40 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.006192 | ba_g+dur_band+vintage_g | 0.1666 | 0.0051604 | 3338 | THERMAL_AUX | 0.96019 | 0.058244 | 9.7549 | 0.043107 | 86.9202 | age_years | infant mortality (k<1)
61366 | 0 | 54 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.31527 | 0.005606 | 2929.5 | THERMAL_AUX | 0.96019 | 0.062951 | 9.7549 | 0.043107 | 82.8702 | age_years | infant mortality (k<1)
61431 | 0 | 84 | <1.5h | LIB | CS | LDWP | 2018 | 1 | 20 | 10 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.22102 | 0.0025264 | 337 | THERMAL_AUX | 0.96019 | 0.029407 | 9.7549 | 0.043107 | 4.2963 | age_years | infant mortality (k<1)
61439 | 0 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2017 | 1 | 1 | 2.2 | Y | Y | arid | other | LIB | CS | <=2019 | 1 | 1 | 0.0081522 | ba_g+dur_band+vintage_g | 0.23409 | 0.0062438 | 0 | THERMAL_AUX | 0.96019 | 0.069605 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61473 | 0 | 36 | <1.5h | LIB | BL | PJM | 2015 | 1 | 1 | 1 | Y | Y | inland | PJM | LIB | BL | <=2019 | 1 | 1 | 0.0017331 | ba_g+dur_band+vintage_g | 0.061014 | 0.0016274 | 0 | THERMAL_AUX | 0.96019 | 0.019147 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61552 | 0 | 22 | <1.5h | LIB | CS | PJM | 2024 | 1 | 6 | 6 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.11113 | 0.0048503 | 455 | THERMAL_AUX | 0.96019 | 0.054941 | 9.7549 | 0.043107 | 11.1362 | age_years | infant mortality (k<1)
61661 | 0 | 84 | <1.5h | LIB | BL | CISO | 2018 | 0 | 40 | 38 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.002069 | dur_band+climate_region | 0.15326 | 0.0017519 | 1280.5 | THERMAL_AUX | 0.96019 | 0.020581 | 9.7549 | 0.043107 | 11.3198 | age_years | infant mortality (k<1)
61667 | 0 | 9 | 1.5-2.5h | LIB | CS | TEC | 2025 | 1 | 40 | 80 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00093643 | 0.0001 | 447 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.22556 | age_years | infant mortality (k<1)
61678 | 0 | 84 | 2.5-4.5h | LIB | CS | SRP | 2018 | 1 | 10 | 40 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0.26714 | 0.0030536 | 1032 | THERMAL_AUX | 0.96019 | 0.035322 | 9.7549 | 0.043107 | 15.9018 | age_years | infant mortality (k<1)
61721 | 0 | 72 | >4.5h | LIB | CS | CISO | 2019 | 1 | 1 | 6.9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0074427 | 0.0001 | 16.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.008326 | age_years | infant mortality (k<1)
61722 | 0 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.5 | 33.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 455 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.2296 | age_years | infant mortality (k<1)
61723 | 0 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.8 | 34.8 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 378 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.19074 | age_years | infant mortality (k<1)
61730 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 1 | 1 | 2 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 19.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0098399 | age_years | infant mortality (k<1)
61737 | 0 | 12 | <1.5h | LIB | CS | PJM | 2021 | 1 | 6.2 | 6.2 | N | Y | coastal | PJM | LIB | CS | 2020-21 | 0 | 1 | 0.002069 | dur_band+climate_region | 0.025205 | 0.0020168 |  | THERMAL_AUX | 0.96019 | 0.023618 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
61739 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2017 | 0 | 1 | 1.3 | Y | N | industrial | NYIS | LIB | CS | <=2019 | 1 | 0 | 0.0045155 | dur_band | 0.14479 | 0.0038617 | 0 | THERMAL_AUX | 0.96019 | 0.044248 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61741 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2018 | 1 | 1.5 | 3 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61763 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.19969 | 0.0041683 | 647.5 | THERMAL_AUX | 0.96019 | 0.04759 | 9.7549 | 0.043107 | 13.6192 | age_years | infant mortality (k<1)
61795 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2020 | 1 | 1 | 2 | Y | N | industrial | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0.23958 | 0.0095851 | 2.5 | THERMAL_AUX | 0.96019 | 0.10294 | 9.7549 | 0.043107 | 0.12092 | age_years | infant mortality (k<1)
61801 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.023953 | 0.0014375 | 2194.5 | THERMAL_AUX | 0.96019 | 0.016951 | 9.7549 | 0.043107 | 15.9181 | age_years | infant mortality (k<1)
61803 | 0 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 10 | 40 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0060978 | 0.0014638 | 705 | THERMAL_AUX | 0.96019 | 0.017256 | 9.7549 | 0.043107 | 5.2074 | age_years | infant mortality (k<1)
61861 | 0 | 84 | 2.5-4.5h | LIB | BL | SRP | 2019 | 1 | 10 | 40 | N | N | arid | other | LIB | BL | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0.26714 | 0.0030536 | 0 | THERMAL_AUX | 0.96019 | 0.035322 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61891 | 0 | 83 | <1.5h | LIB | CS | PJM | 2018 | 0 | 19.8 | 19.8 | Y | N | inland | PJM | LIB | CS | <=2019 | 1 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13029 | 0.0015073 | 2740 | THERMAL_AUX | 0.96019 | 0.01776 | 9.7549 | 0.043107 | 20.8403 | age_years | infant mortality (k<1)
61892 | 0 | 83 | <1.5h | LIB | CS | PJM | 2019 | 0 | 19.8 | 19.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13029 | 0.0015073 | 2919 | THERMAL_AUX | 0.96019 | 0.01776 | 9.7549 | 0.043107 | 22.2017 | age_years | infant mortality (k<1)
61901 | 0 | 36 | 1.5-2.5h | LIB | CS | TVA | 2017 | 1 | 1 | 2 | Y | N | inland | other | LIB | CS | <=2019 | 1 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.23409 | 0.0062438 | 0 | THERMAL_AUX | 0.96019 | 0.069605 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61909 | 0 | 36 | <1.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 1 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 0 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61923 | 0 | 36 | <1.5h | LIB | CS | PJM | 2018 | 0 | 1 | 1 | N | N | coastal | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.061014 | 0.0016274 | 127 | THERMAL_AUX | 0.96019 | 0.019147 | 9.7549 | 0.043107 | 1.0429 | age_years | infant mortality (k<1)
61925 | 3 | 84 | <1.5h | LIB | CS | PNM | 2018 | 0 | 1 | 1 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.0032432 | ba_g+dur_band+vintage_g | 0.22102 | 0.01042 | 4.5 | THERMAL_AUX | 0.96019 | 0.1109 | 9.7549 | 0.043107 | 0.23661 | age_years | infant mortality (k<1)
61956 | 0 | 36 | 1.5-2.5h | LIB | CS | SCEG | 2018 | 1 | 4 | 8 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.23409 | 0.0062438 | 23 | THERMAL_AUX | 0.96019 | 0.069605 | 9.7549 | 0.043107 | 0.72465 | age_years | infant mortality (k<1)
61990 | 0 | 36 | 1.5-2.5h | LIB | CT | MISO | 2017 | 1 | 0.3 | 0.5 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
61995 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.5 | 0.9 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62027 | 0 | 36 | 1.5-2.5h | OTH | CS | PJM | 2016 | 1 | 1 | 2 | Y | Y | coastal | PJM | other | CS | <=2019 | 1 | 1 | 0.0026357 | dur_band+climate_region | 0.089933 | 0.0023987 | 0 | THERMAL_AUX | 0.96019 | 0.027963 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62147 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2019 | 0 | 20 | 8.4 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 2179 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 49.809 | age_years | infant mortality (k<1)
62175 | 4 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 200 | 800 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.43174 | 0.047589 | 17609 | THERMAL_AUX | 0.96019 | 0.36118 | 9.7549 | 0.043107 | 4228.6349 | age_years | infant mortality (k<1)
62219 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 1 | 3 | 3 | N | N | inland | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.0087719 | ba_g+dur_band+vintage_g | 0.24749 | 0.006601 | 19.5 | THERMAL_AUX | 0.96019 | 0.073289 | 9.7549 | 0.043107 | 0.64953 | age_years | infant mortality (k<1)
62235 | 0 | 13 | 2.5-4.5h | LIB | CS | SCEG | 2024 | 1 | 66 | 198 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.045656 | 0.0033722 | 1632.5 | THERMAL_AUX | 0.96019 | 0.038862 | 9.7549 | 0.043107 | 27.7796 | age_years | infant mortality (k<1)
62248 | 0 | 25 | >4.5h | LIB | CS | NEVP | 2023 | 1 | 75 | 375 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0 | dur_band+climate_region | 0.0025969 | 0.0001 | 8731 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 4.4057 | age_years | infant mortality (k<1)
62257 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 0 | 2 | 4.2 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 26.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.013372 | age_years | infant mortality (k<1)
62373 | 1 | 84 | 2.5-4.5h | LIB | CS | WACM | 2018 | 0 | 4 | 16 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0.26714 | 0.0062338 | 0 | THERMAL_AUX | 0.96019 | 0.069501 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62381 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0074427 | 0.0001 | 94 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.047433 | age_years | infant mortality (k<1)
62382 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0074427 | 0.0001 | 92 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.046424 | age_years | infant mortality (k<1)
62383 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0074427 | 0.0001 | 105.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.053236 | age_years | infant mortality (k<1)
62441 | 0 | 24 | <1.5h | LIB | CS | CISO | 2020 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 48.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.024474 | age_years | infant mortality (k<1)
62444 | 0 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 18 | 12.1 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13165 | 0.0015049 | 1974 | THERMAL_AUX | 0.96019 | 0.017732 | 9.7549 | 0.043107 | 14.9906 | age_years | infant mortality (k<1)
62490 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.19969 | 0.0041683 | 558 | THERMAL_AUX | 0.96019 | 0.04759 | 9.7549 | 0.043107 | 11.7367 | age_years | infant mortality (k<1)
62494 | 0 | 2 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 1 | 252 | 1008 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0073063 | 0.0035078 | 8863.5 | THERMAL_AUX | 0.96019 | 0.040359 | 9.7549 | 0.043107 | 156.8876 | age_years | infant mortality (k<1)
62497 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 9 | 36 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.16987 | 0.0067964 | 0 | THERMAL_AUX | 0.96019 | 0.075292 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62499 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 6 | 24 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.16987 | 0.0067964 | 0 | THERMAL_AUX | 0.96019 | 0.075292 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62541 | 0 | 34 | 1.5-2.5h | LIB | CS | FPC | 2023 | 1 | 17.3 | 36 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0035285 | 0.0001 | 160 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.080737 | age_years | infant mortality (k<1)
62561 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 63.3 | 108.6 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.29631 | 0.0094837 | 0 | THERMAL_AUX | 0.96019 | 0.10197 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62562 | 2 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 63.3 | 81 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.2057 | 0.019642 | 0 | THERMAL_AUX | 0.96019 | 0.19005 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62564 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 182.5 | 730 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.43174 | 0.0092124 | 0 | THERMAL_AUX | 0.96019 | 0.099346 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62569 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 4 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.017631 | 0.00047026 | 0 | THERMAL_AUX | 0.96019 | 0.0056108 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62585 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 0 | 3 | 3 | N | N | coastal | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.0087719 | ba_g+dur_band+vintage_g | 0.24749 | 0.006601 | 16.5 | THERMAL_AUX | 0.96019 | 0.073289 | 9.7549 | 0.043107 | 0.5496 | age_years | infant mortality (k<1)
62604 | 0 | 41 | 1.5-2.5h | LIB | BL | ISNE | 2022 | 0 | 25 | 38 | N | N | coastal | ISNE | LIB | BL | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.086665 | 0.0020296 | 64.5 | THERMAL_AUX | 0.96019 | 0.023765 | 9.7549 | 0.043107 | 0.66059 | age_years | infant mortality (k<1)
62609 | 0 | 76 | <1.5h | LIB | CS | ERCO | 2019 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0078529 | 0.0001 | 156.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.078971 | age_years | infant mortality (k<1)
62644 | 0 | 80 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 5 | 10 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0082628 | 0.0001 | 42.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.021446 | age_years | infant mortality (k<1)
62652 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.3 | 6.6 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 98.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.049704 | age_years | infant mortality (k<1)
62682 | 0 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.39531 | 0.0049295 | 0 | THERMAL_AUX | 0.96019 | 0.055787 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62683 | 0 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.39531 | 0.0049295 | 0 | THERMAL_AUX | 0.96019 | 0.055787 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62695 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 19 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.19144 | age_years | infant mortality (k<1)
62714 | 0 | 36 | <1.5h | LIB | CS |  | 2019 | 0 | 1 | 0.9 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 11 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 0.16051 | age_years | infant mortality (k<1)
62733 | 0 | 36 | >4.5h | LIB | BL | NYIS | 2018 | 0 | 5 | 40 | Y | N | coastal | NYIS | LIB | BL | <=2019 | 1 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 25 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.012615 | age_years | infant mortality (k<1)
62734 | 0 | 36 | >4.5h | LIB | BL | NYIS | 2019 | 0 | 5 | 40 | N | N | coastal | NYIS | LIB | BL | <=2019 | 0 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62745 | 0 | 45 | 2.5-4.5h | LIB | CS | BPAT | 2022 | 1 | 30 | 120 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.14908 | 0.003181 | 1836 | THERMAL_AUX | 0.96019 | 0.036741 | 9.7549 | 0.043107 | 29.4708 | age_years | infant mortality (k<1)
62753 | 0 | 72 | <1.5h | LIB | CS | ERCO | 2020 | 1 | 9.9 | 10 | Y | Y | inland | ERCO | LIB | CS | 2020-21 | 1 | 1 | 0.010638 | ba_g+dur_band+vintage_g | 0.44374 | 0.0059177 | 14 | THERMAL_AUX | 0.96019 | 0.066215 | 9.7549 | 0.043107 | 0.41806 | age_years | infant mortality (k<1)
62754 | 0 | 20 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 2 | 4 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0.20795 | 0.0099838 | 0 | THERMAL_AUX | 0.96019 | 0.10676 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62801 | 0 | 24 | <1.5h | LIB | CS | CISO | 2021 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 908 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.45818 | age_years | infant mortality (k<1)
62835 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 1.5 | 3 | N | Y | coastal | ISNE | LIB | CS | <=2019 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 6 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0030277 | age_years | infant mortality (k<1)
62839 | 0 | 36 | >4.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 10 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62844 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 150 | 300 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.0026357 | dur_band+climate_region | 0.021488 | 0.0025791 | 6721.5 | THERMAL_AUX | 0.96019 | 0.030002 | 9.7549 | 0.043107 | 87.4761 | age_years | infant mortality (k<1)
62856 | 0 | 83 | <1.5h | LIB | CS | PJM | 2018 | 1 | 20 | 20 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.0017331 | ba_g+dur_band+vintage_g | 0.13029 | 0.0015073 | 0 | THERMAL_AUX | 0.96019 | 0.01776 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
62862 | 0 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.12002 | 0.0048018 | 74 | THERMAL_AUX | 0.96019 | 0.054422 | 9.7549 | 0.043107 | 1.7931 | age_years | infant mortality (k<1)
62874 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 2 | 6 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.0062643 | 83.5 | THERMAL_AUX | 0.96019 | 0.069817 | 9.7549 | 0.043107 | 2.6394 | age_years | infant mortality (k<1)
62875 | 2 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 3 | 12 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.019312 | 86 | THERMAL_AUX | 0.96019 | 0.18747 | 9.7549 | 0.043107 | 8.3808 | age_years | infant mortality (k<1)
62889 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 20 | 80 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.16987 | 0.0067964 | 1815.5 | THERMAL_AUX | 0.96019 | 0.075292 | 9.7549 | 0.043107 | 62.2625 | age_years | infant mortality (k<1)
62907 | 2 | 36 | <1.5h | LIB | CS | ISNE | 2019 | 0 | 1.9 | 1.9 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.0087719 | ba_g+dur_band+vintage_g | 0.24749 | 0.02035 | 155 | THERMAL_AUX | 0.96019 | 0.19554 | 9.7549 | 0.043107 | 15.9168 | age_years | infant mortality (k<1)
62908 | 0 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 0 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.18741 | 0.0021681 | 9.5 | THERMAL_AUX | 0.96019 | 0.025344 | 9.7549 | 0.043107 | 0.10393 | age_years | infant mortality (k<1)
62937 | 0 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.18741 | 0.0021681 | 4 | THERMAL_AUX | 0.96019 | 0.025344 | 9.7549 | 0.043107 | 0.043761 | age_years | infant mortality (k<1)
62964 | 0 | 16 | <1.5h | LIB | CS | AZPS | 2023 | 0 | 50 | 50 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.0040674 | dur_band+climate_region | 0.063474 | 0.0038092 | 4547.5 | THERMAL_AUX | 0.96019 | 0.043674 | 9.7549 | 0.043107 | 87.4106 | age_years | infant mortality (k<1)
62968 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 4 | Y | N | coastal | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.076909 | 0.0020513 | 53 | THERMAL_AUX | 0.96019 | 0.024013 | 9.7549 | 0.043107 | 0.54861 | age_years | infant mortality (k<1)
62969 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.051185 | 0.0020478 | 74.5 | THERMAL_AUX | 0.96019 | 0.023972 | 9.7549 | 0.043107 | 0.76984 | age_years | infant mortality (k<1)
62970 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.051185 | 0.0020478 | 64.5 | THERMAL_AUX | 0.96019 | 0.023972 | 9.7549 | 0.043107 | 0.6665 | age_years | infant mortality (k<1)
62971 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 2.9 | 6 | Y | N | inland | ISNE | other | CT | 2022-23 | 1 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.027022 | 0.0021622 | 62.5 | THERMAL_AUX | 0.96019 | 0.025277 | 9.7549 | 0.043107 | 0.68191 | age_years | infant mortality (k<1)
62972 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2021 | 1 | 2 | 4.2 | Y | N | inland | ISNE | other | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 57 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.57431 | age_years | infant mortality (k<1)
62973 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 1.6 | 3.2 | Y | N | coastal | ISNE | other | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 36.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.36776 | age_years | infant mortality (k<1)
62974 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 3.8 | 7.9 | Y | Y | inland | ISNE | other | CT | 2022-23 | 1 | 1 | 0.0022222 | ba_g+dur_band+vintage_g | 0.027022 | 0.0021622 | 154 | THERMAL_AUX | 0.96019 | 0.025277 | 9.7549 | 0.043107 | 1.6802 | age_years | infant mortality (k<1)
62975 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 3.9 | 7.9 | Y | Y | inland | ISNE | other | CT | 2020-21 | 1 | 1 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 114 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 1.1486 | age_years | infant mortality (k<1)
62976 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2020 | 1 | 2 | 4 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 16 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.16121 | age_years | infant mortality (k<1)
62977 | 0 | 12 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.027022 | 0.0021622 | 51.5 | THERMAL_AUX | 0.96019 | 0.025277 | 9.7549 | 0.043107 | 0.56189 | age_years | infant mortality (k<1)
62978 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3 | 6 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 65 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.65491 | age_years | infant mortality (k<1)
62981 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2018 | 0 | 2 | 4.2 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 35.5 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0.43449 | age_years | infant mortality (k<1)
62999 | 0 | 36 | <1.5h | LIB | CT | NYIS | 2020 | 1 | 3 | 4.4 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 0 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63000 | 0 | 36 | 1.5-2.5h | LIB | CT | NYIS | 2020 | 1 | 4 | 8.8 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63011 | 0 | 36 | >4.5h | LIB | CT | ISNE | 2020 | 1 | 1.5 | 7.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0086207 | dur_band+climate_region | 0.24426 | 0.006515 | 100.5 | THERMAL_AUX | 0.96019 | 0.072405 | 9.7549 | 0.043107 | 3.304 | age_years | infant mortality (k<1)
63022 | 3 | 36 | 1.5-2.5h | LIB | CS | WACM | 2018 | 0 | 4.2 | 8.5 | N | N | industrial | other | LIB | CS | <=2019 | 0 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.23409 | 0.025752 | 238 | THERMAL_AUX | 0.96019 | 0.23502 | 9.7549 | 0.043107 | 30.927 | age_years | infant mortality (k<1)
63044 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 4.3 | 14 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 196 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.098903 | age_years | infant mortality (k<1)
63064 | 0 | 64 | <1.5h | LIB | CS | CPLW | 2020 | 0 | 8.8 | 8.8 | Y | Y | inland | other | LIB | CS | 2020-21 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0066212 | 0.0001 | 31 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.015643 | age_years | infant mortality (k<1)
63090 | 0 | 36 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 3 | 6 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 9 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0.11015 | age_years | infant mortality (k<1)
63172 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10458 | 0.0033474 | 14374.5 | THERMAL_AUX | 0.96019 | 0.038587 | 9.7549 | 0.043107 | 242.8 | age_years | infant mortality (k<1)
63186 | 0 | 36 | <1.5h | LIB | CS | JEA | 2019 | 1 | 5 | 3.8 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.0032432 | ba_g+dur_band+vintage_g | 0.10841 | 0.0028916 | 0 | THERMAL_AUX | 0.96019 | 0.033513 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63214 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3 | 6.6 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63238 | 0 | 24 | <1.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 20 | Y | N | inland | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.0054568 | dur_band+climate_region | 0.12002 | 0.0048018 | 0 | THERMAL_AUX | 0.96019 | 0.054422 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63255 | 0 | 57 | <1.5h | LIB | BL | ERCO | 2021 | 1 | 40 | 40 | Y | Y | arid | ERCO | LIB | BL | 2020-21 | 1 | 1 | 0.010638 | ba_g+dur_band+vintage_g | 0.38708 | 0.0065205 | 125 | THERMAL_AUX | 0.96019 | 0.072461 | 9.7549 | 0.043107 | 4.1129 | age_years | infant mortality (k<1)
63264 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 32 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.016147 | age_years | infant mortality (k<1)
63280 | 0 | 36 | >4.5h | LIB | CT |  | 2021 | 1 | 14 | 70 | N | Y | coastal | other | LIB | CT | 2020-21 | 0 | 1 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 1353 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.68274 | age_years | infant mortality (k<1)
63324 | 0 | 36 | <1.5h | LIB | BL | MISO | 2019 | 1 | 5 | 5 | N | N | inland | MISO | LIB | BL | <=2019 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 64.5 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 1.4744 | age_years | infant mortality (k<1)
63337 | 0 | 36 | <1.5h | LIB | CT | NYIS | 2022 | 1 | 3 | 3 | N | N | inland | NYIS | LIB | CT | 2022-23 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 55 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 1.2572 | age_years | infant mortality (k<1)
63338 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 63 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.03179 | age_years | infant mortality (k<1)
63339 | 0 | 17 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0017673 | 0.0001 | 4.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0022707 | age_years | infant mortality (k<1)
63340 | 0 | 33 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.003425 | 0.0001 | 49 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.024726 | age_years | infant mortality (k<1)
63341 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 52.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.026492 | age_years | infant mortality (k<1)
63352 | 0 | 21 | <1.5h | LIB | CS | NEVP | 2024 | 1 | 380 | 380 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0040674 | dur_band+climate_region | 0.08169 | 0.0037351 | 38646 | THERMAL_AUX | 0.96019 | 0.042861 | 9.7549 | 0.043107 | 728.3933 | age_years | infant mortality (k<1)
63398 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 1.6 | 3.8 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 104 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.052479 | age_years | infant mortality (k<1)
63415 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 1.6 | 6.6 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63420 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 0.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.002523 | age_years | infant mortality (k<1)
63421 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.2 | 0.2 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63422 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.3 | 0.3 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63458 | 0 | 24 | 1.5-2.5h | FLB | CS | SWPP | 2020 | 0 | 10 | 20 | Y | N | inland | other | other | CS | 2020-21 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 376.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.18999 | age_years | infant mortality (k<1)
63468 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 15 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0075691 | age_years | infant mortality (k<1)
63469 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.5 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 42.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.42821 | age_years | infant mortality (k<1)
63470 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.9 | 5.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 50 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.50378 | age_years | infant mortality (k<1)
63472 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 2.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 22.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.2267 | age_years | infant mortality (k<1)
63473 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.8 | 3.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 52 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.52393 | age_years | infant mortality (k<1)
63474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 65 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.65491 | age_years | infant mortality (k<1)
63475 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.3 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 63 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.63476 | age_years | infant mortality (k<1)
63486 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.5 | 0.8 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 18 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.009083 | age_years | infant mortality (k<1)
63510 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.5 | 0.5 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0002523 | age_years | infant mortality (k<1)
63522 | 0 | 43 | 1.5-2.5h | LIB | OT | SOCO | 2022 | 1 | 40 | 80 | N | N | inland | other | LIB | other | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0044583 | 0.0001 | 1540.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.77735 | age_years | infant mortality (k<1)
63535 | 0 | 36 | 2.5-4.5h | LIB | BL | SOCO | 2020 | 1 | 1 | 4 | Y | N | inland | other | LIB | BL | 2020-21 | 1 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.16337 | 0.0043574 | 93 | THERMAL_AUX | 0.96019 | 0.049641 | 9.7549 | 0.043107 | 2.0449 | age_years | infant mortality (k<1)
63585 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 3 | 12 | Y | N | coastal | NYIS | LIB | CS | 2020-21 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 98 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.049452 | age_years | infant mortality (k<1)
63609 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 91 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.045919 | age_years | infant mortality (k<1)
63610 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.2 | 6.3 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 73 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.036836 | age_years | infant mortality (k<1)
63611 | 0 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 2.5 | 15 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 218 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.11 | age_years | infant mortality (k<1)
63612 | 0 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 1 | 6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 35 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.017661 | age_years | infant mortality (k<1)
63613 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 2 | 13 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 66 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.033304 | age_years | infant mortality (k<1)
63614 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1 | 5 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 59 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.029772 | age_years | infant mortality (k<1)
63615 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 8.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 182 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.091839 | age_years | infant mortality (k<1)
63616 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 4.9 | 32.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 326 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.1645 | age_years | infant mortality (k<1)
63617 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.3 | 7.2 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 146 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.073673 | age_years | infant mortality (k<1)
63685 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 100 | 400 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.40906 | 0.00958 | 9551.5 | THERMAL_AUX | 0.96019 | 0.1029 | 9.7549 | 0.043107 | 461.735 | age_years | infant mortality (k<1)
63721 | 0 | 49 | 1.5-2.5h | LIB | CS | SOCO | 2021 | 1 | 40 | 80 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0050772 | 0.0001 | 2340.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.181 | age_years | infant mortality (k<1)
63722 | 0 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2021 | 1 | 1 | 2 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 37.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.018923 | age_years | infant mortality (k<1)
63723 | 0 | 6 | 2.5-4.5h | LIB | CS | HECO | 2025 | 1 | 52 | 208 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.021603 | 0.0034572 | 4320.5 | THERMAL_AUX | 0.96019 | 0.039802 | 9.7549 | 0.043107 | 75.3732 | age_years | infant mortality (k<1)
63727 | 0 | 47 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 140.3 | 561 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.44244 | 0.0090389 | 15233 | THERMAL_AUX | 0.96019 | 0.097662 | 9.7549 | 0.043107 | 694.7954 | age_years | infant mortality (k<1)
63728 | 0 | 38 | 1.5-2.5h | LIB | CS | PNM | 2022 | 1 | 12.5 | 25 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0039419 | 0.0001 | 540.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.27274 | age_years | infant mortality (k<1)
63731 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 125 | 500 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10769 | 0.0033357 | 6763.5 | THERMAL_AUX | 0.96019 | 0.038458 | 9.7549 | 0.043107 | 113.8456 | age_years | infant mortality (k<1)
63735 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 11 | 44 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.16396 | 0.0068448 | 1053.5 | THERMAL_AUX | 0.96019 | 0.075787 | 9.7549 | 0.043107 | 36.3873 | age_years | infant mortality (k<1)
63737 | 4 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 125 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.010638 | ba_g+dur_band+vintage_g | 0.36104 | 0.035114 | 3352 | THERMAL_AUX | 0.96019 | 0.29486 | 9.7549 | 0.043107 | 593.9413 | age_years | infant mortality (k<1)
63757 | 2 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.2057 | 0.019642 | 6598 | THERMAL_AUX | 0.96019 | 0.19005 | 9.7549 | 0.043107 | 653.9759 | age_years | infant mortality (k<1)
63763 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 5.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 30.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.3073 | age_years | infant mortality (k<1)
63774 | 0 | 9 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 0.7 | 2.1 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00093643 | 0.0001 | 5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.002523 | age_years | infant mortality (k<1)
63775 | 0 | 36 | 1.5-2.5h | LIB | BL | SOCO | 2020 | 0 | 0.2 | 0.4 | N | N | inland | other | LIB | BL | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
63776 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10769 | 0.0033357 | 6764.5 | THERMAL_AUX | 0.96019 | 0.038458 | 9.7549 | 0.043107 | 113.8624 | age_years | infant mortality (k<1)
63804 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2 | 3.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 17.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.17632 | age_years | infant mortality (k<1)
63805 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 44 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.44332 | age_years | infant mortality (k<1)
63834 | 0 | 66 | 2.5-4.5h | LIB | BL | CISO | 2020 | 0 | 250 | 1000 | N | N | coastal | CISO | LIB | BL | 2020-21 | 0 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.3601 | 0.0052389 | 12078.5 | THERMAL_AUX | 0.96019 | 0.059078 | 9.7549 | 0.043107 | 319.3079 | age_years | infant mortality (k<1)
63843 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021.75 | 1 | 80 | 320 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.28836 | 0.011537 | 7844 | THERMAL_AUX | 0.96019 | 0.12131 | 9.7549 | 0.043107 | 456.6439 | age_years | infant mortality (k<1)
63848 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 225 | 900 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.27971 | 0.011677 | 26478.5 | THERMAL_AUX | 0.96019 | 0.1226 | 9.7549 | 0.043107 | 1560.2102 | age_years | infant mortality (k<1)
63849 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 135 | 540 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.27971 | 0.011677 | 16258.5 | THERMAL_AUX | 0.96019 | 0.1226 | 9.7549 | 0.043107 | 958.0104 | age_years | infant mortality (k<1)
63859 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 1 | 147 | 147 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 13900.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 7.0143 | age_years | infant mortality (k<1)
63891 | 0 | 57 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.32706 | 0.0055095 | 9420.5 | THERMAL_AUX | 0.96019 | 0.061936 | 9.7549 | 0.043107 | 261.9015 | age_years | infant mortality (k<1)
63892 | 0 | 52 | <1.5h | LIB | CS | ERCO | 2021 | 1 | 55.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.010638 | ba_g+dur_band+vintage_g | 0.36553 | 0.0067497 | 1015.5 | THERMAL_AUX | 0.96019 | 0.074814 | 9.7549 | 0.043107 | 34.5873 | age_years | infant mortality (k<1)
63900 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 1 | 30 | 120 | N | Y | coastal | other | LIB | CS | 2022-23 | 0 | 1 | 0.0037383 | ba_g+dur_band+vintage_g | 0.085454 | 0.0034189 | 3080 | THERMAL_AUX | 0.96019 | 0.039378 | 9.7549 | 0.043107 | 53.1358 | age_years | infant mortality (k<1)
63905 | 0 | 43 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 91.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.26428 | 0.0059015 | 2243 | THERMAL_AUX | 0.96019 | 0.066046 | 9.7549 | 0.043107 | 66.7951 | age_years | infant mortality (k<1)
63913 | 0 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.15189 | 0.0031705 | 5017.5 | THERMAL_AUX | 0.96019 | 0.036624 | 9.7549 | 0.043107 | 80.2732 | age_years | infant mortality (k<1)
63930 | 0 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 60 | 242 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.2989 | 0.00574 | 5428.5 | THERMAL_AUX | 0.96019 | 0.064357 | 9.7549 | 0.043107 | 157.2343 | age_years | infant mortality (k<1)
63933 | 0 | 20 | 1.5-2.5h | LIB | CS | NEVP | 2024 | 1 | 100 | 150 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0020786 | 0.0001 | 10988.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 5.5449 | age_years | infant mortality (k<1)
63943 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 60 | 240 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.43174 | 0.0092124 | 6549 | THERMAL_AUX | 0.96019 | 0.099346 | 9.7549 | 0.043107 | 304.4395 | age_years | infant mortality (k<1)
63995 | 0 | 23 | <1.5h | LIB | CS | FPC | 2021 | 0 | 11 | 10.1 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0023896 | 0.0001 | 5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.002523 | age_years | infant mortality (k<1)
63996 | 1 | 24 | 2.5-4.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 14.3 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.085454 | 0.0069795 | 39 | THERMAL_AUX | 0.96019 | 0.077161 | 9.7549 | 0.043107 | 1.3735 | age_years | infant mortality (k<1)
63998 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 5.5 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0.23806 | 0.0095243 | 11 | THERMAL_AUX | 0.96019 | 0.10236 | 9.7549 | 0.043107 | 0.52866 | age_years | infant mortality (k<1)
63999 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 8.3 | 11.7 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0.23806 | 0.0095243 | 18 | THERMAL_AUX | 0.96019 | 0.10236 | 9.7549 | 0.043107 | 0.86509 | age_years | infant mortality (k<1)
64000 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.2 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 48 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.48363 | age_years | infant mortality (k<1)
64050 | 0 | 35 | <1.5h | LIB | CS | CPLE | 2023 | 1 | 2 | 2 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.1659 | 0.0045514 | 0 | THERMAL_AUX | 0.96019 | 0.051734 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64084 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.010361 | 0.00047374 | 0 | THERMAL_AUX | 0.96019 | 0.0056521 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64087 | 0 | 22 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.010849 | 0.0004735 | 0 | THERMAL_AUX | 0.96019 | 0.0056493 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64089 | 2 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.2057 | 0.019642 | 6631.5 | THERMAL_AUX | 0.96019 | 0.19005 | 9.7549 | 0.043107 | 657.2964 | age_years | infant mortality (k<1)
64090 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.010361 | 0.00047374 | 0 | THERMAL_AUX | 0.96019 | 0.0056521 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64092 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.010361 | 0.00047374 | 0 | THERMAL_AUX | 0.96019 | 0.0056521 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64103 | 0 | 58 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 35 | 140 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.3309 | 0.005478 | 1919.5 | THERMAL_AUX | 0.96019 | 0.061605 | 9.7549 | 0.043107 | 53.06 | age_years | infant mortality (k<1)
64105 | 0 | 43 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 50 | 200 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.42062 | 0.0093926 | 3994.5 | THERMAL_AUX | 0.96019 | 0.10109 | 9.7549 | 0.043107 | 189.3228 | age_years | infant mortality (k<1)
64128 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 2 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.020151 | age_years | infant mortality (k<1)
64129 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.1 | 6.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.051185 | 0.0020478 | 108.5 | THERMAL_AUX | 0.96019 | 0.023972 | 9.7549 | 0.043107 | 1.1212 | age_years | infant mortality (k<1)
64140 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 1.4 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 13.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.13602 | age_years | infant mortality (k<1)
64147 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 50 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.50378 | age_years | infant mortality (k<1)
64148 | 0 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.15189 | 0.0031705 | 2345 | THERMAL_AUX | 0.96019 | 0.036624 | 9.7549 | 0.043107 | 37.5168 | age_years | infant mortality (k<1)
64164 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 120 | 190 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.14415 | 0.011534 | 4966.5 | THERMAL_AUX | 0.96019 | 0.12129 | 9.7549 | 0.043107 | 289.0671 | age_years | infant mortality (k<1)
64170 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.9 | 1.8 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 14.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.1461 | age_years | infant mortality (k<1)
64182 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.7 | 9 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 84.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.85138 | age_years | infant mortality (k<1)
64185 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 1.9 | 3.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 50 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.50378 | age_years | infant mortality (k<1)
64187 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 2.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 15.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0078214 | age_years | infant mortality (k<1)
64197 | 0 | 28 | <1.5h | LIB | CS | CISO | 2023 | 1 | 137 | 137 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.006192 | ba_g+dur_band+vintage_g | 0.15295 | 0.0052449 | 13407 | THERMAL_AUX | 0.96019 | 0.059141 | 9.7549 | 0.043107 | 354.8338 | age_years | infant mortality (k<1)
64198 | 0 | 36 | 2.5-4.5h | LIB | CS | BPAT | 2020 | 1 | 1 | 4 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.16337 | 0.0043574 | 87.5 | THERMAL_AUX | 0.96019 | 0.049641 | 9.7549 | 0.043107 | 1.924 | age_years | infant mortality (k<1)
64202 | 0 | 12 |  |  |  | ERCO |  | 1 |  |  |  |  | inland | ERCO | other | other | 2020-21 | 0 | 0 | 0.0043268 | fleet | 0.0513 | 0.0041048 | 1901.5 | THERMAL_AUX | 0.96019 | 0.046901 | 9.7549 | 0.043107 | 39.3864 | age_years | infant mortality (k<1)
64207 | 5 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.12002 | 0.029806 | 80.5 | THERMAL_AUX | 0.96019 | 0.26216 | 9.7549 | 0.043107 | 12.1076 | age_years | infant mortality (k<1)
64213 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 9.4 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.076909 | 0.0020513 | 64 | THERMAL_AUX | 0.96019 | 0.024013 | 9.7549 | 0.043107 | 0.66247 | age_years | infant mortality (k<1)
64222 | 0 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.16337 | 0.0043574 | 10 | THERMAL_AUX | 0.96019 | 0.049641 | 9.7549 | 0.043107 | 0.21988 | age_years | infant mortality (k<1)
64223 | 0 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.16337 | 0.0043574 | 8.5 | THERMAL_AUX | 0.96019 | 0.049641 | 9.7549 | 0.043107 | 0.1869 | age_years | infant mortality (k<1)
64231 | 0 | 12 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 1 | 1 | 4.4 | N | N | inland | ISNE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 32.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0164 | age_years | infant mortality (k<1)
64256 | 0 | 17 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 60 | 240 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.058878 | 0.0033255 | 5987.5 | THERMAL_AUX | 0.96019 | 0.038345 | 9.7549 | 0.043107 | 100.4754 | age_years | infant mortality (k<1)
64293 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 449.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 19.0614 | age_years | infant mortality (k<1)
64294 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 437 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 18.5314 | age_years | infant mortality (k<1)
64295 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 473 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 20.058 | age_years | infant mortality (k<1)
64296 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 432 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 18.3193 | age_years | infant mortality (k<1)
64297 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 486.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 20.6305 | age_years | infant mortality (k<1)
64298 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 399.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 16.9412 | age_years | infant mortality (k<1)
64312 | 1 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.36104 | 0.013877 | 2925 | THERMAL_AUX | 0.96019 | 0.14235 | 9.7549 | 0.043107 | 204.8169 | age_years | infant mortality (k<1)
64314 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 423.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 17.9589 | age_years | infant mortality (k<1)
64315 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 458 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 19.4219 | age_years | infant mortality (k<1)
64316 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 445 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 13.8476 | age_years | infant mortality (k<1)
64317 | 2 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.36104 | 0.020956 | 2799 | THERMAL_AUX | 0.96019 | 0.20017 | 9.7549 | 0.043107 | 295.9811 | age_years | infant mortality (k<1)
64318 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 804 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 25.019 | age_years | infant mortality (k<1)
64319 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 473.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 20.0792 | age_years | infant mortality (k<1)
64321 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 407.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 17.2804 | age_years | infant mortality (k<1)
64322 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 874.5 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 27.2128 | age_years | infant mortality (k<1)
64374 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64375 | 0 | 24 | <1.5h | LIB | CS | MISO | 2021 | 0 | 2.5 | 2.9 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.12002 | 0.0048018 | 0 | THERMAL_AUX | 0.96019 | 0.054422 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64395 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2.5 | 5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 39.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.39798 | age_years | infant mortality (k<1)
64400 | 0 | 36 | <1.5h | LIB | CS | HECO | 2021 | 1 | 1.9 | 1.9 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 104 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.052479 | age_years | infant mortality (k<1)
64423 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 16.5 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0.18312 | 0.0073263 | 203 | THERMAL_AUX | 0.96019 | 0.08068 | 9.7549 | 0.043107 | 7.5047 | age_years | infant mortality (k<1)
64424 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 17.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0.18312 | 0.0073263 | 12.5 | THERMAL_AUX | 0.96019 | 0.08068 | 9.7549 | 0.043107 | 0.46211 | age_years | infant mortality (k<1)
64425 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 11.9 | N | N | coastal | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 5.5 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 0.23323 | age_years | infant mortality (k<1)
64426 | 0 | 56 | 1.5-2.5h | LIB | CS | TEPC | 2021 | 1 | 30 | 60 | N | Y | arid | other | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0057983 | 0.0001 | 1502 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.75792 | age_years | infant mortality (k<1)
64432 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.2 | 4.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 13 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.13098 | age_years | infant mortality (k<1)
64436 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 8 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.080604 | age_years | infant mortality (k<1)
64442 | 0 | 10 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 0.7 | 3 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0010404 | 0.0001 | 9 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0045415 | age_years | infant mortality (k<1)
64446 | 0 | 36 | <1.5h | LIB | CS | BPAT | 2021 | 1 | 1 | 1.4 | Y | N | coastal | other | LIB | CS | 2020-21 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 14 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0070645 | age_years | infant mortality (k<1)
64450 | 0 | 36 | <1.5h | LIB | CS | PJM | 2021 | 1 | 10 | 10 | N | N | inland | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 42 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 0.96006 | age_years | infant mortality (k<1)
64453 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 3 | 12 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64481 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 132 | 528 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.40906 | 0.00958 | 13892 | THERMAL_AUX | 0.96019 | 0.1029 | 9.7549 | 0.043107 | 671.5618 | age_years | infant mortality (k<1)
64489 | 0 | 29 | 2.5-4.5h | OTH | CS | CISO | 2023 | 1 | 75 | 300 | N | N | arid | CISO | other | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.32869 | 0.010883 | 6828 | THERMAL_AUX | 0.96019 | 0.11525 | 9.7549 | 0.043107 | 374.9703 | age_years | infant mortality (k<1)
64508 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 14 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0070645 | age_years | infant mortality (k<1)
64509 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 4 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0020184 | age_years | infant mortality (k<1)
64510 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 5.1 | 10 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 38 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.019175 | age_years | infant mortality (k<1)
64511 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 2.5 | 5 | Y | N | coastal | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 16.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.008326 | age_years | infant mortality (k<1)
64512 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.5 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 3 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0015138 | age_years | infant mortality (k<1)
64513 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 4 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0020184 | age_years | infant mortality (k<1)
64514 | 0 | 36 | <1.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 2.5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 15 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 0.34288 | age_years | infant mortality (k<1)
64516 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 16 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0080737 | age_years | infant mortality (k<1)
64520 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 15 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0075691 | age_years | infant mortality (k<1)
64522 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2021 | 1 | 1.3 | 2 | N | N | inland | CPLE | LIB | CS | 2020-21 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 8.5 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0.10403 | age_years | infant mortality (k<1)
64528 | 2 | 55 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 200 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0.33938 | 0.018266 | 3780 | THERMAL_AUX | 0.96019 | 0.17916 | 9.7549 | 0.043107 | 348.4066 | age_years | infant mortality (k<1)
64529 | 0 | 11 | 2.5-4.5h | LIB | CS | TVA | 2025 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.038906 | 0.0033961 | 2765 | THERMAL_AUX | 0.96019 | 0.039126 | 9.7549 | 0.043107 | 47.3837 | age_years | infant mortality (k<1)
64545 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 73 | 108.6 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.1179 | 0.0070756 | 1935.5 | THERMAL_AUX | 0.96019 | 0.078139 | 9.7549 | 0.043107 | 69.1057 | age_years | infant mortality (k<1)
64546 | 1 | 24 | 2.5-4.5h | LIB | BL | FPL | 2019 | 0 | 10 | 40 | N | N | coastal | other | LIB | BL | <=2019 | 0 | 0 | 0.0041667 | ba_g+dur_band+vintage_g | 0.094322 | 0.0077038 | 218 | THERMAL_AUX | 0.96019 | 0.084478 | 9.7549 | 0.043107 | 8.4745 | age_years | infant mortality (k<1)
64564 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 110 | 440 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.40906 | 0.00958 | 9496.5 | THERMAL_AUX | 0.96019 | 0.1029 | 9.7549 | 0.043107 | 459.0762 | age_years | infant mortality (k<1)
64601 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.0062643 | 12 | THERMAL_AUX | 0.96019 | 0.069817 | 9.7549 | 0.043107 | 0.37932 | age_years | infant mortality (k<1)
64611 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 8.3 | 3.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 845.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.42665 | age_years | infant mortality (k<1)
64612 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.28836 | 0.011537 | 0 | THERMAL_AUX | 0.96019 | 0.12131 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
64614 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.28836 | 0.023552 | 823.5 | THERMAL_AUX | 0.96019 | 0.21943 | 9.7549 | 0.043107 | 97.8687 | age_years | infant mortality (k<1)
64617 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 9.5 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 175 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.088307 | age_years | infant mortality (k<1)
64618 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 9 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 145 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.073168 | age_years | infant mortality (k<1)
64619 | 0 | 33 | >4.5h | LIB | CS | ISNE | 2023 | 1 | 0.8 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0 | dur_band+climate_region | 0.003425 | 0.0001 | 69 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.034818 | age_years | infant mortality (k<1)
64620 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 5.1 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 90 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.045415 | age_years | infant mortality (k<1)
64624 | 0 | 49 | <1.5h | LIB | CS | CISO | 2021 | 1 | 50 | 50 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0050772 | 0.0001 | 5021.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 2.5339 | age_years | infant mortality (k<1)
64627 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 17 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0085783 | age_years | infant mortality (k<1)
64630 | 0 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 20 | 50 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.39703 | 0.0097751 | 1453.5 | THERMAL_AUX | 0.96019 | 0.10477 | 9.7549 | 0.043107 | 71.6952 | age_years | infant mortality (k<1)
64633 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 240 | 960 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.016592 | 0.0014483 | 24396 | THERMAL_AUX | 0.96019 | 0.017077 | 9.7549 | 0.043107 | 178.2942 | age_years | infant mortality (k<1)
64636 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 200 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00083247 | 0.0001 | 8455 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 4.2665 | age_years | infant mortality (k<1)
64640 | 0 | 36 | <1.5h | LIB | CS | CPLW | 2022 | 1 | 4.4 | 4.4 | N | Y | inland | other | LIB | CS | 2022-23 | 0 | 1 | 0.0125 | ba_g+dur_band+vintage_g | 0.3191 | 0.0085112 | 18.5 | THERMAL_AUX | 0.96019 | 0.092498 | 9.7549 | 0.043107 | 0.79454 | age_years | infant mortality (k<1)
64656 | 0 | 18 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 12.5 | 50 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.062126 | 0.003314 | 1251 | THERMAL_AUX | 0.96019 | 0.038218 | 9.7549 | 0.043107 | 20.9204 | age_years | infant mortality (k<1)
64664 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 92 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.046424 | age_years | infant mortality (k<1)
64672 | 0 | 31 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.6 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.30319 | 0.009391 | 1596 | THERMAL_AUX | 0.96019 | 0.10107 | 9.7549 | 0.043107 | 75.6308 | age_years | infant mortality (k<1)
64686 | 0 | 36 | <1.5h | LIB | OT | NYIS | 2022 | 1 | 24.7 | 20 | N | Y | inland | NYIS | LIB | other | 2022-23 | 0 | 1 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 1020 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 23.3158 | age_years | infant mortality (k<1)
64695 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 3.7 | 15 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10458 | 0.0033474 | 186.5 | THERMAL_AUX | 0.96019 | 0.038587 | 9.7549 | 0.043107 | 3.1502 | age_years | infant mortality (k<1)
64696 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 4.5 | 20.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 225 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.11354 | age_years | infant mortality (k<1)
64701 | 1 | 40 | 1.5-2.5h | LIB | CS | CISO | 2022 | 0 | 125 | 250 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.002849 | ba_g+dur_band+vintage_g | 0.10609 | 0.0051991 | 7244 | THERMAL_AUX | 0.96019 | 0.058655 | 9.7549 | 0.043107 | 190.0459 | age_years | infant mortality (k<1)
64712 | 0 | 50 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 100 | 200 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0.39627 | 0.00761 | 5802.5 | THERMAL_AUX | 0.96019 | 0.083538 | 9.7549 | 0.043107 | 222.82 | age_years | infant mortality (k<1)
64713 | 0 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.2989 | 0.00574 | 10979.5 | THERMAL_AUX | 0.96019 | 0.064357 | 9.7549 | 0.043107 | 318.0168 | age_years | infant mortality (k<1)
64719 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 7.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 28 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.014129 | age_years | infant mortality (k<1)
64726 | 0 | 35 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 3.6 | 8 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.074932 | 0.0020557 | 67 | THERMAL_AUX | 0.96019 | 0.024063 | 9.7549 | 0.043107 | 0.69501 | age_years | infant mortality (k<1)
64727 | 0 | 36 | 2.5-4.5h | LIB | OT | ISNE | 2022 | 1 | 3 | 8 | N | N | coastal | ISNE | LIB | other | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 43.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02195 | age_years | infant mortality (k<1)
64731 | 0 | 36 | 1.5-2.5h | OTH | CS | ISNE | 2021 | 1 | 2.3 | 4.8 | N | N | inland | ISNE | other | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 0.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.0050378 | age_years | infant mortality (k<1)
64743 | 2 | 36 | <1.5h | LIB | CS | CISO | 2022 | 0 | 5 | 5 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.006192 | ba_g+dur_band+vintage_g | 0.18841 | 0.015493 | 351.5 | THERMAL_AUX | 0.96019 | 0.15629 | 9.7549 | 0.043107 | 27.4792 | age_years | infant mortality (k<1)
64752 | 0 | 24 | >4.5h | LIB | CS | FPC | 2023 | 1 | 2.5 | 18 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0 | dur_band+climate_region | 0.0024933 | 0.0001 | 35.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.017914 | age_years | infant mortality (k<1)
64759 | 0 | 24 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 4.5 | 13.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 142.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.071907 | age_years | infant mortality (k<1)
64760 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 0 | 3 | 10 | Y | Y | coastal | ISNE | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 87.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.044153 | age_years | infant mortality (k<1)
64761 | 0 | 6 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 2 | 11.9 | N | N | coastal | NYIS | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0.00062448 | 0.0001 | 42.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.021446 | age_years | infant mortality (k<1)
64763 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.051185 | 0.0041805 | 41.5 | THERMAL_AUX | 0.96019 | 0.047723 | 9.7549 | 0.043107 | 0.87545 | age_years | infant mortality (k<1)
64764 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 1.5 | 3.1 | Y | Y | inland | ISNE | LIB | CS | 2020-21 | 1 | 1 | 0.0021583 | ba_g+dur_band+vintage_g | 0.051185 | 0.0020478 | 35.5 | THERMAL_AUX | 0.96019 | 0.023972 | 9.7549 | 0.043107 | 0.36684 | age_years | infant mortality (k<1)
64765 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 46.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.023464 | age_years | infant mortality (k<1)
64766 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 2.2 | 8.8 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.0062643 | 44.5 | THERMAL_AUX | 0.96019 | 0.069817 | 9.7549 | 0.043107 | 1.4066 | age_years | infant mortality (k<1)
64811 | 0 | 23 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 24.8 | 25 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16117 | 0.0067286 | 565.5 | THERMAL_AUX | 0.96019 | 0.074598 | 9.7549 | 0.043107 | 19.2004 | age_years | infant mortality (k<1)
64844 | 0 | 13 | 1.5-2.5h | PBB | CS | ISNE | 2024 | 1 | 1.4 | 2.8 | Y | N | inland | ISNE | other | CS | 2024+ | 1 | 0 | 0.0026681 | dur_band+climate_region | 0.034864 | 0.0025751 | 23 | THERMAL_AUX | 0.96019 | 0.029956 | 9.7549 | 0.043107 | 0.29886 | age_years | infant mortality (k<1)
64851 | 0 | 23 | <1.5h | LIB | CS | CISO | 2023 | 1 | 131 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.006192 | ba_g+dur_band+vintage_g | 0.12916 | 0.0053922 | 11681 | THERMAL_AUX | 0.96019 | 0.060699 | 9.7549 | 0.043107 | 317.8335 | age_years | infant mortality (k<1)
64852 | 0 | 29 | <1.5h | LIB | CS | CISO | 2023 | 1 | 149 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.006192 | ba_g+dur_band+vintage_g | 0.15755 | 0.0052164 | 12083.5 | THERMAL_AUX | 0.96019 | 0.058839 | 9.7549 | 0.043107 | 318.0682 | age_years | infant mortality (k<1)
64864 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 88 | 352 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.013616 | 0.0014527 | 8291 | THERMAL_AUX | 0.96019 | 0.017128 | 9.7549 | 0.043107 | 60.7768 | age_years | infant mortality (k<1)
64875 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 23 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.23174 | age_years | infant mortality (k<1)
64876 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 286 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.14432 | age_years | infant mortality (k<1)
64877 | 0 | 44 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 11 | 31.5 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.27282 | 0.0059536 | 495 | THERMAL_AUX | 0.96019 | 0.066589 | 9.7549 | 0.043107 | 14.8709 | age_years | infant mortality (k<1)
64878 | 0 | 41 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 144 | 272 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.002849 | ba_g+dur_band+vintage_g | 0.10846 | 0.00254 | 6838.5 | THERMAL_AUX | 0.96019 | 0.029561 | 9.7549 | 0.043107 | 87.6497 | age_years | infant mortality (k<1)
64879 | 0 | 44 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 120 | 250 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.002849 | ba_g+dur_band+vintage_g | 0.11548 | 0.00252 | 4492 | THERMAL_AUX | 0.96019 | 0.029335 | 9.7549 | 0.043107 | 57.1211 | age_years | infant mortality (k<1)
64908 | 0 | 19 | >4.5h | LIB | CS | CISO | 2024 | 1 | 40 | 200 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | dur_band+climate_region | 0.14573 | 0.0073644 | 3315 | THERMAL_AUX | 0.96019 | 0.081065 | 9.7549 | 0.043107 | 123.1907 | age_years | infant mortality (k<1)
64915 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0.18312 | 0.0073263 | 524.5 | THERMAL_AUX | 0.96019 | 0.08068 | 9.7549 | 0.043107 | 19.3903 | age_years | infant mortality (k<1)
64916 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0.18312 | 0.0073263 | 444 | THERMAL_AUX | 0.96019 | 0.08068 | 9.7549 | 0.043107 | 16.4143 | age_years | infant mortality (k<1)
64917 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 7.5 | 15 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0.18312 | 0.0073263 | 401.5 | THERMAL_AUX | 0.96019 | 0.08068 | 9.7549 | 0.043107 | 14.8431 | age_years | infant mortality (k<1)
64921 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 20 | 80 | Y | Y | coastal | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.16847 | 0.01348 |  | THERMAL_AUX | 0.96019 | 0.13886 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
64928 | 0 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 33 | 70 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.002849 | ba_g+dur_band+vintage_g | 0.11081 | 0.0025333 | 1792.5 | THERMAL_AUX | 0.96019 | 0.029485 | 9.7549 | 0.043107 | 22.914 | age_years | infant mortality (k<1)
64929 | 0 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 40 | 83.5 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.002849 | ba_g+dur_band+vintage_g | 0.11081 | 0.0025333 | 1178 | THERMAL_AUX | 0.96019 | 0.029485 | 9.7549 | 0.043107 | 15.0587 | age_years | infant mortality (k<1)
64970 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 20.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 99 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.049956 | age_years | infant mortality (k<1)
64980 | 0 | 36 | 2.5-4.5h | LIB | BL | ISNE | 2021 | 1 | 0.5 | 2.1 | N | N | coastal | ISNE | LIB | BL | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 3 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0015138 | age_years | infant mortality (k<1)
64993 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 40 | 160 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.37804 | 0.010083 | 1829 | THERMAL_AUX | 0.96019 | 0.1077 | 9.7549 | 0.043107 | 93.0592 | age_years | infant mortality (k<1)
65007 | 0 | 3 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 100 | 400 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00031234 | 0.0001 | 4 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0020184 | age_years | infant mortality (k<1)
65011 | 0 | 2 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 75 | 300 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00020825 | 0.0001 | 4.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0022707 | age_years | infant mortality (k<1)
65014 | 0 | 18 | 1.5-2.5h | LIB | CS | ISNE | 2024 | 1 | 2.5 | 4.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.0026357 | dur_band+climate_region | 0.047084 | 0.0025116 | 4.5 | THERMAL_AUX | 0.96019 | 0.02924 | 9.7549 | 0.043107 | 0.057033 | age_years | infant mortality (k<1)
65015 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 12.8 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 153.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.077457 | age_years | infant mortality (k<1)
65018 | 0 | 15 | 2.5-4.5h | LIB | OT | SOCO | 2024 | 0 | 65 | 260 | N | Y | inland | other | LIB | other | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.052313 | 0.0033487 | 7460 | THERMAL_AUX | 0.96019 | 0.038602 | 9.7549 | 0.043107 | 126.0584 | age_years | infant mortality (k<1)
65028 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.8 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.29631 | 0.0094837 | 1679 | THERMAL_AUX | 0.96019 | 0.10197 | 9.7549 | 0.043107 | 80.3498 | age_years | infant mortality (k<1)
65029 | 0 | 36 | 1.5-2.5h | LIB | BL | MISO | 2021 | 1 | 0.3 | 0.5 | Y | N | inland | MISO | LIB | BL | 2020-21 | 1 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
65035 | 0 | 16 | 2.5-4.5h | LIB | CS | NYIS | 2023 | 0 | 7.5 | 30 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0016636 | 0.0001 | 646 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.32598 | age_years | infant mortality (k<1)
65044 | 0 | 24 | 2.5-4.5h | LIB | CS | PJM | 2023 | 0 | 20 | 80 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.011824 | 0.00047304 | 1729 | THERMAL_AUX | 0.96019 | 0.0056438 | 9.7549 | 0.043107 | 4.1271 | age_years | infant mortality (k<1)
65053 | 0 | 34 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 112 | 448 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.36469 | 0.010299 | 13042 | THERMAL_AUX | 0.96019 | 0.10976 | 9.7549 | 0.043107 | 677.8098 | age_years | infant mortality (k<1)
65054 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1 | 5.4 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 33.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.016904 | age_years | infant mortality (k<1)
65055 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.2 | 4.8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 20.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.20655 | age_years | infant mortality (k<1)
65056 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 36.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.36776 | age_years | infant mortality (k<1)
65057 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.3 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 23.5 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.23678 | age_years | infant mortality (k<1)
65058 | 0 | 30 | <1.5h | LIB | CS | HECO | 2023 | 1 | 36 | 4.6 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0.28086 | 0.0089893 | 2776.5 | THERMAL_AUX | 0.96019 | 0.097179 | 9.7549 | 0.043107 | 125.9439 | age_years | infant mortality (k<1)
65098 | 0 | 21 | 1.5-2.5h | LIB | CS | SWPP | 2020 | 0 | 1.5 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0021823 | 0.0001 | 17 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0085783 | age_years | infant mortality (k<1)
65114 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1.5 | 8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | dur_band+climate_region | 0.0037352 | 0.0001 | 81.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.041126 | age_years | infant mortality (k<1)
65140 | 0 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 350 | 1400 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.39703 | 0.0097751 | 42235.5 | THERMAL_AUX | 0.96019 | 0.10477 | 9.7549 | 0.043107 | 2083.3034 | age_years | infant mortality (k<1)
65154 | 0 | 12 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 2 | 4.3 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.027022 | 0.0021622 | 16 | THERMAL_AUX | 0.96019 | 0.025277 | 9.7549 | 0.043107 | 0.17457 | age_years | infant mortality (k<1)
65174 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 37 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 0.37279 | age_years | infant mortality (k<1)
65217 | 0 | 36 | 2.5-4.5h | LIB | OT | NYIS | 2021 | 1 | 4.5 | 17 | N | N | inland | NYIS | LIB | other | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 43.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02195 | age_years | infant mortality (k<1)
65239 | 0 | 7 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 24.6 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | dur_band+climate_region | 0.00072849 | 0.0001 | 255 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.12868 | age_years | infant mortality (k<1)
65240 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 48 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.024221 | age_years | infant mortality (k<1)
65241 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 38 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.019175 | age_years | infant mortality (k<1)
65242 | 0 | 35 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.5 | 3.8 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.072933 | 0.0020009 | 0 | THERMAL_AUX | 0.96019 | 0.023436 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
65243 | 0 | 24 | 2.5-4.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.011824 | 0.00047304 | 21.5 | THERMAL_AUX | 0.96019 | 0.0056438 | 9.7549 | 0.043107 | 0.05132 | age_years | infant mortality (k<1)
65244 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 25.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.012868 | age_years | infant mortality (k<1)
65245 | 0 | 24 | <1.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.002069 | dur_band+climate_region | 0.049171 | 0.0019672 | 25.5 | THERMAL_AUX | 0.96019 | 0.023051 | 9.7549 | 0.043107 | 0.25313 | age_years | infant mortality (k<1)
65246 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 38.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.019427 | age_years | infant mortality (k<1)
65247 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 34.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.017409 | age_years | infant mortality (k<1)
65248 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 22.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.011354 | age_years | infant mortality (k<1)
65249 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 31 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.015643 | age_years | infant mortality (k<1)
65250 | 0 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 48 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.024221 | age_years | infant mortality (k<1)
65259 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 1228.5 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 38.2286 | age_years | infant mortality (k<1)
65271 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 125 | 125 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.24574 | 0.0060502 | 1227 | THERMAL_AUX | 0.96019 | 0.067596 | 9.7549 | 0.043107 | 37.4602 | age_years | infant mortality (k<1)
65291 | 0 | 19 | 2.5-4.5h | LIB | CS | TVA | 2024 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.065352 | 0.0033026 | 2637.5 | THERMAL_AUX | 0.96019 | 0.038091 | 9.7549 | 0.043107 | 43.9551 | age_years | infant mortality (k<1)
65382 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 1 | 2 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.034381 | 0.0027511 | 39.5 | THERMAL_AUX | 0.96019 | 0.031937 | 9.7549 | 0.043107 | 0.54834 | age_years | infant mortality (k<1)
65396 | 0 | 2 | <1.5h | LIB | CS | CISO | 2025 | 0 | 15 | 15 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00020825 | 0.0001 | 1080.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.54523 | age_years | infant mortality (k<1)
65397 | 0 | 14 | <1.5h | LIB | CS | CISO | 2024 | 0 | 30 | 30 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0014559 | 0.0001 | 1606 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.8104 | age_years | infant mortality (k<1)
65408 | 0 | 9 | 2.5-4.5h | LIB | CT | CISO | 2021 | 1 | 0.7 | 3 | Y | N | coastal | CISO | LIB | CT | 2020-21 | 1 | 0 | 0.0081871 | ba_g+dur_band+vintage_g | 0.07127 | 0.0076036 | 24 | THERMAL_AUX | 0.96019 | 0.083474 | 9.7549 | 0.043107 | 0.92085 | age_years | infant mortality (k<1)
65409 | 0 | 36 | 1.5-2.5h | LIB | CT | CISO | 2021 | 1 | 0.5 | 0.9 | N | N | coastal | CISO | LIB | CT | 2020-21 | 0 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0.32093 | 0.0085598 | 22 | THERMAL_AUX | 0.96019 | 0.092976 | 9.7549 | 0.043107 | 0.95025 | age_years | infant mortality (k<1)
65410 | 0 | 29 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 190 | 380 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.28929 | 0.0095783 | 7814 | THERMAL_AUX | 0.96019 | 0.10288 | 9.7549 | 0.043107 | 377.6751 | age_years | infant mortality (k<1)
65422 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 510 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 9.0603 | age_years | infant mortality (k<1)
65429 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 555 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 9.8598 | age_years | infant mortality (k<1)
65433 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 426 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 7.568 | age_years | infant mortality (k<1)
65441 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2022 | 1 | 1 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.017631 | 0.00047026 | 6.5 | THERMAL_AUX | 0.96019 | 0.0056108 | 9.7549 | 0.043107 | 0.015424 | age_years | infant mortality (k<1)
65456 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 112.5 | 450 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.016592 | 0.0014483 | 9593 | THERMAL_AUX | 0.96019 | 0.017077 | 9.7549 | 0.043107 | 70.1089 | age_years | infant mortality (k<1)
65457 | 1 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.016592 | 0.0029567 | 18390 | THERMAL_AUX | 0.96019 | 0.03424 | 9.7549 | 0.043107 | 274.3724 | age_years | infant mortality (k<1)
65468 | 0 | 12 | 2.5-4.5h | LIB | BL | PJM | 2019 | 1 | 0.6 | 2.1 | Y | Y | coastal | PJM | LIB | BL | <=2019 | 1 | 1 | 0.0065359 | dur_band+climate_region | 0.075515 | 0.0060424 | 11.5 | THERMAL_AUX | 0.96019 | 0.067514 | 9.7549 | 0.043107 | 0.35064 | age_years | infant mortality (k<1)
65469 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 0.8 | 3.1 | N | N | industrial | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.37804 | 0.010083 | 53 | THERMAL_AUX | 0.96019 | 0.1077 | 9.7549 | 0.043107 | 2.6966 | age_years | infant mortality (k<1)
65472 | 2 | 24 | 2.5-4.5h | LIB | CS | NEVP | 2021 | 0 | 10 | 40 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.11519 | 0.014207 | 898.5 | THERMAL_AUX | 0.96019 | 0.14524 | 9.7549 | 0.043107 | 64.4146 | age_years | infant mortality (k<1)
65489 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.019081 | 0.0014094 | 10262 | THERMAL_AUX | 0.96019 | 0.016625 | 9.7549 | 0.043107 | 72.9811 | age_years | infant mortality (k<1)
65490 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.019081 | 0.0014094 | 8758.5 | THERMAL_AUX | 0.96019 | 0.016625 | 9.7549 | 0.043107 | 62.2885 | age_years | infant mortality (k<1)
65491 | 1 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.019081 | 0.0028772 | 7961.5 | THERMAL_AUX | 0.96019 | 0.033351 | 9.7549 | 0.043107 | 115.5882 | age_years | infant mortality (k<1)
65492 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 175 | 175 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.019081 | 0.0014094 | 8880 | THERMAL_AUX | 0.96019 | 0.016625 | 9.7549 | 0.043107 | 63.1526 | age_years | infant mortality (k<1)
65493 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 50 | 50 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.014743 | 0.0014156 | 2595 | THERMAL_AUX | 0.96019 | 0.016698 | 9.7549 | 0.043107 | 18.5367 | age_years | infant mortality (k<1)
65499 | 0 | 36 | 1.5-2.5h | LIB | CS | PJM | 2022 | 0 | 10.5 | 24.6 | Y | Y | inland | PJM | LIB | CS | 2022-23 | 1 | 1 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 1144 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 14.0015 | age_years | infant mortality (k<1)
65530 | 0 | 24 | 1.5-2.5h | LIB | CS | MISO | 2022 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.062519 | 0.0025013 | 140 | THERMAL_AUX | 0.96019 | 0.029123 | 9.7549 | 0.043107 | 1.767 | age_years | infant mortality (k<1)
65531 | 0 | 24 | 1.5-2.5h | LIB | CS | MISO | 2023 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.062519 | 0.0025013 | 121.5 | THERMAL_AUX | 0.96019 | 0.029123 | 9.7549 | 0.043107 | 1.5335 | age_years | infant mortality (k<1)
65562 | 0 | 24 | 2.5-4.5h | MAB | BL | CISO | 2024 | 1 | 1.6 | 5.9 | N | N | arid | CISO | other | BL | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.035504 | 0.0014205 | 85 | THERMAL_AUX | 0.96019 | 0.016754 | 9.7549 | 0.043107 | 0.60926 | age_years | infant mortality (k<1)
65568 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 1 | 0.6 | 1.1 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0.32093 | 0.0085598 | 24.5 | THERMAL_AUX | 0.96019 | 0.092976 | 9.7549 | 0.043107 | 1.0582 | age_years | infant mortality (k<1)
65588 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 70 | 140 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.073128 | 0.014044 | 4197 | THERMAL_AUX | 0.96019 | 0.14381 | 9.7549 | 0.043107 | 297.4194 | age_years | infant mortality (k<1)
65589 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.059371 | 0.014252 | 8060.5 | THERMAL_AUX | 0.96019 | 0.14563 | 9.7549 | 0.043107 | 579.6837 | age_years | infant mortality (k<1)
65591 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 126 | 504 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.013616 | 0.0014527 | 10586 | THERMAL_AUX | 0.96019 | 0.017128 | 9.7549 | 0.043107 | 77.6002 | age_years | infant mortality (k<1)
65614 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 2.1 | 4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.096507 | 0.0025741 | 70 | THERMAL_AUX | 0.96019 | 0.029945 | 9.7549 | 0.043107 | 0.90922 | age_years | infant mortality (k<1)
65633 | 0 | 29 | <1.5h | LIB | CS | MISO | 2023 | 0 | 3.6 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.14149 | 0.0046847 | 1 | THERMAL_AUX | 0.96019 | 0.053167 | 9.7549 | 0.043107 | 0.023639 | age_years | infant mortality (k<1)
65635 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00072849 | 0.0001 | 587 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.29621 | age_years | infant mortality (k<1)
65644 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.045199 | 0.014467 | 7236 | THERMAL_AUX | 0.96019 | 0.14749 | 9.7549 | 0.043107 | 528.2288 | age_years | infant mortality (k<1)
65645 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.059371 | 0.014252 | 8723 | THERMAL_AUX | 0.96019 | 0.14563 | 9.7549 | 0.043107 | 627.3284 | age_years | infant mortality (k<1)
65650 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 1.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 27.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.013877 | age_years | infant mortality (k<1)
65656 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 20 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00062448 | 0.0001 | 1183.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.5972 | age_years | infant mortality (k<1)
65657 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 65 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00031234 | 0.0001 | 3090 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.5592 | age_years | infant mortality (k<1)
65669 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 40 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.020184 | age_years | infant mortality (k<1)
65670 | 0 | 35 | >4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 5 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0 | dur_band+climate_region | 0.0036319 | 0.0001 | 27.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.013877 | age_years | infant mortality (k<1)
65672 | 1 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 169 | 676 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.30506 | 0.022999 | 18683.5 | THERMAL_AUX | 0.96019 | 0.21541 | 9.7549 | 0.043107 | 2168.3307 | age_years | infant mortality (k<1)
65673 | 2 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 47 | 188 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.30506 | 0.034732 | 5100 | THERMAL_AUX | 0.96019 | 0.2926 | 9.7549 | 0.043107 | 893.8374 | age_years | infant mortality (k<1)
65674 | 0 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 136 | 136 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.006192 | ba_g+dur_band+vintage_g | 0.14359 | 0.0053028 | 9030.5 | THERMAL_AUX | 0.96019 | 0.059755 | 9.7549 | 0.043107 | 241.6439 | age_years | infant mortality (k<1)
65675 | 0 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 100 | 100 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.006192 | ba_g+dur_band+vintage_g | 0.14359 | 0.0053028 | 2440.5 | THERMAL_AUX | 0.96019 | 0.059755 | 9.7549 | 0.043107 | 65.3045 | age_years | infant mortality (k<1)
65677 | 0 | 30 | <1.5h | LIB | CS | CISO | 2023 | 1 | 18.8 | 18.8 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.006192 | ba_g+dur_band+vintage_g | 0.1621 | 0.0051882 | 548.5 | THERMAL_AUX | 0.96019 | 0.05854 | 9.7549 | 0.043107 | 14.3599 | age_years | infant mortality (k<1)
65692 | 0 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 42 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.062519 | 0.0025013 | 2304 | THERMAL_AUX | 0.96019 | 0.029123 | 9.7549 | 0.043107 | 29.0804 | age_years | infant mortality (k<1)
65693 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.19139 | 0.012252 | 5777 | THERMAL_AUX | 0.96019 | 0.12785 | 9.7549 | 0.043107 | 357.15 | age_years | infant mortality (k<1)
65694 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.24574 | 0.0060502 | 802 | THERMAL_AUX | 0.96019 | 0.067596 | 9.7549 | 0.043107 | 24.485 | age_years | infant mortality (k<1)
65695 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 100 | 100 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.24574 | 0.0060502 | 1932 | THERMAL_AUX | 0.96019 | 0.067596 | 9.7549 | 0.043107 | 58.9838 | age_years | infant mortality (k<1)
65696 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.2004 | 0.0064139 | 2297 | THERMAL_AUX | 0.96019 | 0.071364 | 9.7549 | 0.043107 | 74.3431 | age_years | infant mortality (k<1)
65698 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.19139 | 0.012252 | 6370 | THERMAL_AUX | 0.96019 | 0.12785 | 9.7549 | 0.043107 | 393.8109 | age_years | infant mortality (k<1)
65699 | 1 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 111 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.013477 | ba_g+dur_band+vintage_g | 0.29631 | 0.019361 | 3123 | THERMAL_AUX | 0.96019 | 0.18785 | 9.7549 | 0.043107 | 305.1027 | age_years | infant mortality (k<1)
65700 | 2 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 107 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.013477 | ba_g+dur_band+vintage_g | 0.29631 | 0.029238 | 3040.5 | THERMAL_AUX | 0.96019 | 0.25848 | 9.7549 | 0.043107 | 448.5803 | age_years | infant mortality (k<1)
65701 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.2004 | 0.0064139 | 800 | THERMAL_AUX | 0.96019 | 0.071364 | 9.7549 | 0.043107 | 25.8922 | age_years | infant mortality (k<1)
65711 | 0 | 17 | 2.5-4.5h | LIB | CS | IID | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.058878 | 0.0033255 | 14331 | THERMAL_AUX | 0.96019 | 0.038345 | 9.7549 | 0.043107 | 240.4866 | age_years | infant mortality (k<1)
65733 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00072849 | 0.0001 | 588 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.29671 | age_years | infant mortality (k<1)
65734 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.32099 | 0.011008 | 15606.5 | THERMAL_AUX | 0.96019 | 0.11641 | 9.7549 | 0.043107 | 866.8807 | age_years | infant mortality (k<1)
65735 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.32099 | 0.011008 | 14596.5 | THERMAL_AUX | 0.96019 | 0.11641 | 9.7549 | 0.043107 | 810.7791 | age_years | infant mortality (k<1)
65743 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 50 | 200 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.032642 | 0.0014247 | 4762 | THERMAL_AUX | 0.96019 | 0.016803 | 9.7549 | 0.043107 | 34.2343 | age_years | infant mortality (k<1)
65744 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 136 | 544 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.032642 | 0.0014247 | 12977.5 | THERMAL_AUX | 0.96019 | 0.016803 | 9.7549 | 0.043107 | 93.296 | age_years | infant mortality (k<1)
65809 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 172.5 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 5.3679 | age_years | infant mortality (k<1)
65810 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 186 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 6.2713 | age_years | infant mortality (k<1)
65811 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 186 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 6.2713 | age_years | infant mortality (k<1)
65812 | 0 | 21 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.030466 | 0.001393 | 136 | THERMAL_AUX | 0.96019 | 0.016436 | 9.7549 | 0.043107 | 0.95598 | age_years | infant mortality (k<1)
65813 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 182.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 6.1533 | age_years | infant mortality (k<1)
65814 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 184.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 6.2207 | age_years | infant mortality (k<1)
65815 | 0 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 1 | 2.1 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.0026357 | dur_band+climate_region | 0.061808 | 0.0024728 | 2 | THERMAL_AUX | 0.96019 | 0.028802 | 9.7549 | 0.043107 | 0.024956 | age_years | infant mortality (k<1)
65829 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 159 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 5.3609 | age_years | infant mortality (k<1)
65830 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 157.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 5.3104 | age_years | infant mortality (k<1)
65831 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.23121 | 0.0061668 | 179.5 | THERMAL_AUX | 0.96019 | 0.068807 | 9.7549 | 0.043107 | 5.5857 | age_years | infant mortality (k<1)
65832 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 130 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 4.3832 | age_years | infant mortality (k<1)
65833 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 177.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 5.9847 | age_years | infant mortality (k<1)
65834 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 186 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 6.2713 | age_years | infant mortality (k<1)
65835 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 182.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 6.1533 | age_years | infant mortality (k<1)
65836 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 10.4 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.010638 | ba_g+dur_band+vintage_g | 0.21005 | 0.0084037 | 191 | THERMAL_AUX | 0.96019 | 0.091439 | 9.7549 | 0.043107 | 8.0995 | age_years | infant mortality (k<1)
65837 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 106 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 0.74187 | age_years | infant mortality (k<1)
65857 | 3 | 30 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.33621 | 0.044382 | 22207 | THERMAL_AUX | 0.96019 | 0.34538 | 9.7549 | 0.043107 | 4973.4283 | age_years | infant mortality (k<1)
65860 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 160 | 320 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.059371 | 0.014252 | 8869.5 | THERMAL_AUX | 0.96019 | 0.14563 | 9.7549 | 0.043107 | 637.8642 | age_years | infant mortality (k<1)
65861 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.059371 | 0.014252 | 10423 | THERMAL_AUX | 0.96019 | 0.14563 | 9.7549 | 0.043107 | 749.5866 | age_years | infant mortality (k<1)
65866 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 593 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 10.5348 | age_years | infant mortality (k<1)
65888 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 524 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 9.309 | age_years | infant mortality (k<1)
65927 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 547 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 9.7176 | age_years | infant mortality (k<1)
65933 | 3 | 32 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 80 | 320 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.35077 | 0.043409 | 6966.5 | THERMAL_AUX | 0.96019 | 0.34042 | 9.7549 | 0.043107 | 1525.9971 | age_years | infant mortality (k<1)
65945 | 0 | 36 | 2.5-4.5h | LIB | CS | PJM | 2022 | 1 | 1.5 | 4.3 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0065359 | dur_band+climate_region | 0.19682 | 0.0052496 | 12 | THERMAL_AUX | 0.96019 | 0.05919 | 9.7549 | 0.043107 | 0.31788 | age_years | infant mortality (k<1)
65950 | 0 | 32 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 1.8 | 6.4 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0033216 | 0.0001 | 120 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.060553 | age_years | infant mortality (k<1)
65951 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 12 | 12 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0.18794 | 0.0075191 | 2050.5 | THERMAL_AUX | 0.96019 | 0.082624 | 9.7549 | 0.043107 | 77.8 | age_years | infant mortality (k<1)
65952 | 1 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 20 | 20 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0.18794 | 0.01535 | 3327 | THERMAL_AUX | 0.96019 | 0.15508 | 9.7549 | 0.043107 | 257.6988 | age_years | infant mortality (k<1)
65953 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 7 | 7 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.0092593 | ba_g+dur_band+vintage_g | 0.18794 | 0.0075191 | 1143.5 | THERMAL_AUX | 0.96019 | 0.082624 | 9.7549 | 0.043107 | 43.3866 | age_years | infant mortality (k<1)
65956 | 0 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 88 | 264 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.0037383 | ba_g+dur_band+vintage_g | 0.091921 | 0.0033947 | 6630.5 | THERMAL_AUX | 0.96019 | 0.03911 | 9.7549 | 0.043107 | 113.5797 | age_years | infant mortality (k<1)
65962 | 0 | 24 | >4.5h | LIB | CS | CISO | 2024 | 1 | 10 | 47.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0.0024933 | 0.0001 | 761.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.38426 | age_years | infant mortality (k<1)
65963 | 0 | 30 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 60 | 240 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0031146 | 0.0001 | 6495.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.2777 | age_years | infant mortality (k<1)
65980 | 3 | 31 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 131 | 524 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.34357 | 0.043891 | 13311 | THERMAL_AUX | 0.96019 | 0.34288 | 9.7549 | 0.043107 | 2948.0614 | age_years | infant mortality (k<1)
65987 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 325 | 1300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.33621 | 0.010761 | 39866.5 | THERMAL_AUX | 0.96019 | 0.1141 | 9.7549 | 0.043107 | 2164.7949 | age_years | infant mortality (k<1)
65988 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.33621 | 0.010761 | 8284.5 | THERMAL_AUX | 0.96019 | 0.1141 | 9.7549 | 0.043107 | 449.8575 | age_years | infant mortality (k<1)
66006 | 2 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 73.2 | 120 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.26629 | 0.034272 | 3429.5 | THERMAL_AUX | 0.96019 | 0.28987 | 9.7549 | 0.043107 | 593.1009 | age_years | infant mortality (k<1)
66007 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.33568 | 0.0089532 | 4593 | THERMAL_AUX | 0.96019 | 0.096827 | 9.7549 | 0.043107 | 207.5045 | age_years | infant mortality (k<1)
66008 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.33568 | 0.0089532 | 4727 | THERMAL_AUX | 0.96019 | 0.096827 | 9.7549 | 0.043107 | 213.5584 | age_years | infant mortality (k<1)
66009 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 203 | 400 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.33568 | 0.0089532 | 5889 | THERMAL_AUX | 0.96019 | 0.096827 | 9.7549 | 0.043107 | 266.0557 | age_years | infant mortality (k<1)
66023 | 0 | 14 | <1.5h | LIB | CS | CISO | 2024 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0014559 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66050 | 0 | 40 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 127 | 508 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.40311 | 0.0096766 | 12855 | THERMAL_AUX | 0.96019 | 0.10382 | 9.7549 | 0.043107 | 627.6941 | age_years | infant mortality (k<1)
66067 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 0 | 185 | 565 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.085454 | 0.0034189 | 14604 | THERMAL_AUX | 0.96019 | 0.039378 | 9.7549 | 0.043107 | 251.9464 | age_years | infant mortality (k<1)
66075 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 3.3 | N | N | coastal | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.074861 | 0.0019967 | 101 | THERMAL_AUX | 0.96019 | 0.023389 | 9.7549 | 0.043107 | 1.0176 | age_years | infant mortality (k<1)
66076 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 71 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.035827 | age_years | infant mortality (k<1)
66128 | 0 | 10 | 2.5-4.5h | LIB | CS | TEC | 2025 | 1 | 40 | 103 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.035494 | 0.0034081 | 779.5 | THERMAL_AUX | 0.96019 | 0.039259 | 9.7549 | 0.043107 | 13.4057 | age_years | infant mortality (k<1)
66129 | 0 | 10 | 1.5-2.5h | LIB | CS | TEC | 2024 | 1 | 15 | 30 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0010404 | 0.0001 | 226.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.11429 | age_years | infant mortality (k<1)
66137 | 0 | 21 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 40.4 | 80 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.2489 | 0.01138 | 2080 | THERMAL_AUX | 0.96019 | 0.11987 | 9.7549 | 0.043107 | 119.4468 | age_years | infant mortality (k<1)
66163 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 20 | 80 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10458 | 0.0033474 | 1975.5 | THERMAL_AUX | 0.96019 | 0.038587 | 9.7549 | 0.043107 | 33.3682 | age_years | infant mortality (k<1)
66170 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 368.8 | N | N | arid | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.013477 | ba_g+dur_band+vintage_g | 0.25198 | 0.010081 | 7464 | THERMAL_AUX | 0.96019 | 0.10769 | 9.7549 | 0.043107 | 379.6967 | age_years | infant mortality (k<1)
66180 | 0 | 28 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 3.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0029076 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66181 | 0 | 29 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 7.8 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0022222 | ba_g+dur_band+vintage_g | 0.062895 | 0.0020825 | 0 | THERMAL_AUX | 0.96019 | 0.024368 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66182 | 0 | 33 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.003425 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66208 | 1 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 132 | 528 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.32099 | 0.022472 | 15161.5 | THERMAL_AUX | 0.96019 | 0.21153 | 9.7549 | 0.043107 | 1719.2377 | age_years | infant mortality (k<1)
66218 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2020 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66222 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2021 | 1 | 4 | 8 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66228 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 2 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.16984 | 0.00453 | 0 | THERMAL_AUX | 0.96019 | 0.051503 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66232 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.090936 | 0.0024255 | 0 | THERMAL_AUX | 0.96019 | 0.028266 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66263 | 0 | 19 | 2.5-4.5h | LIB | CS | SRP | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.065352 | 0.0033026 | 33877.5 | THERMAL_AUX | 0.96019 | 0.038091 | 9.7549 | 0.043107 | 564.5831 | age_years | infant mortality (k<1)
66265 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 828.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.41807 | age_years | infant mortality (k<1)
66266 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 648.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.32724 | age_years | infant mortality (k<1)
66270 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 162 | 648 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.026867 | 0.0014332 | 12611 | THERMAL_AUX | 0.96019 | 0.016902 | 9.7549 | 0.043107 | 91.2025 | age_years | infant mortality (k<1)
66278 | 0 | 21 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0021823 | 0.0001 | 740.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.37366 | age_years | infant mortality (k<1)
66279 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 652 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.329 | age_years | infant mortality (k<1)
66280 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 1082.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.54624 | age_years | infant mortality (k<1)
66281 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 20 | 20 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 859 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.43346 | age_years | infant mortality (k<1)
66285 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.026867 | 0.0014332 | 20915 | THERMAL_AUX | 0.96019 | 0.016902 | 9.7549 | 0.043107 | 151.2569 | age_years | infant mortality (k<1)
66286 | 0 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 200 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00072849 | 0.0001 | 10781 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 5.4402 | age_years | infant mortality (k<1)
66325 | 1 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 116 | 464 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.035494 | 0.0069576 | 4738.5 | THERMAL_AUX | 0.96019 | 0.076938 | 9.7549 | 0.043107 | 166.3619 | age_years | infant mortality (k<1)
66326 | 0 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2024 | 0 | 40 | 160 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.035494 | 0.0034081 | 3490.5 | THERMAL_AUX | 0.96019 | 0.039259 | 9.7549 | 0.043107 | 60.0289 | age_years | infant mortality (k<1)
66327 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 4 | 16 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.042293 | 0.0033841 | 267 | THERMAL_AUX | 0.96019 | 0.038994 | 9.7549 | 0.043107 | 4.5594 | age_years | infant mortality (k<1)
66328 | 0 | 12 | 1.5-2.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 4 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 140 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.070645 | age_years | infant mortality (k<1)
66329 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 8 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.042293 | 0.0033841 | 0 | THERMAL_AUX | 0.96019 | 0.038994 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66330 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 3 | 12 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.042293 | 0.0033841 | 274.5 | THERMAL_AUX | 0.96019 | 0.038994 | 9.7549 | 0.043107 | 4.6875 | age_years | infant mortality (k<1)
66333 | 0 | 18 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 90 | 360 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.062126 | 0.003314 | 10478 | THERMAL_AUX | 0.96019 | 0.038218 | 9.7549 | 0.043107 | 175.2231 | age_years | infant mortality (k<1)
66334 | 0 | 20 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 250 | 1000 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.068555 | 0.0032913 | 30035 | THERMAL_AUX | 0.96019 | 0.037966 | 9.7549 | 0.043107 | 498.8304 | age_years | infant mortality (k<1)
66336 | 0 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 102.6 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.25769 | 0.011247 | 5791.5 | THERMAL_AUX | 0.96019 | 0.11864 | 9.7549 | 0.043107 | 328.6891 | age_years | infant mortality (k<1)
66337 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.045199 | 0.014467 | 11481 | THERMAL_AUX | 0.96019 | 0.14749 | 9.7549 | 0.043107 | 838.1143 | age_years | infant mortality (k<1)
66338 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 223.4 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.024807 | 0.0014011 | 11024.5 | THERMAL_AUX | 0.96019 | 0.01653 | 9.7549 | 0.043107 | 77.9462 | age_years | infant mortality (k<1)
66357 | 0 | 30 | 2.5-4.5h | LIB | CS | NEVP | 2023 | 1 | 65 | 260 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10458 | 0.0033474 | 6979.5 | THERMAL_AUX | 0.96019 | 0.038587 | 9.7549 | 0.043107 | 117.8909 | age_years | infant mortality (k<1)
66394 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 60 | 160 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.034075 | 0.0014226 | 3423.5 | THERMAL_AUX | 0.96019 | 0.016779 | 9.7549 | 0.043107 | 24.5753 | age_years | infant mortality (k<1)
66408 | 0 | 31 | 2.5-4.5h | LIB | CS | EPE | 2023 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10769 | 0.0033357 | 3308 | THERMAL_AUX | 0.96019 | 0.038458 | 9.7549 | 0.043107 | 55.6814 | age_years | infant mortality (k<1)
66420 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 262.5 | 250 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.014743 | 0.0014156 | 8277 | THERMAL_AUX | 0.96019 | 0.016698 | 9.7549 | 0.043107 | 59.1246 | age_years | infant mortality (k<1)
66423 | 1 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 68.8 | 275.2 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.30506 | 0.022999 | 7325.5 | THERMAL_AUX | 0.96019 | 0.21541 | 9.7549 | 0.043107 | 850.1676 | age_years | infant mortality (k<1)
66461 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 116.6 | 400 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.025412 | 0.0014353 | 10026 | THERMAL_AUX | 0.96019 | 0.016926 | 9.7549 | 0.043107 | 72.6162 | age_years | infant mortality (k<1)
66462 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 88 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.021022 | 0.0014418 | 8473 | THERMAL_AUX | 0.96019 | 0.017001 | 9.7549 | 0.043107 | 61.6446 | age_years | infant mortality (k<1)
66474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 6.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.076909 | 0.0020513 | 0 | THERMAL_AUX | 0.96019 | 0.024013 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66488 | 0 | 27 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.069789 | 0.0024819 | 0 | THERMAL_AUX | 0.96019 | 0.028904 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66494 | 0 | 19 | 2.5-4.5h | LIB | CS | CISO | 2024.0882 | 0 | 680 | 2720 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.028317 | 0.001431 | 71677 | THERMAL_AUX | 0.96019 | 0.016877 | 9.7549 | 0.043107 | 517.5941 | age_years | infant mortality (k<1)
66499 | 0 | 36 | 1.5-2.5h | LIB | CT | PJM | 2021 | 1 | 1.2 | 2.4 | N | N | coastal | PJM | LIB | CT | 2020-21 | 0 | 0 | 0.0026357 | dur_band+climate_region | 0.089933 | 0.0023987 | 2 | THERMAL_AUX | 0.96019 | 0.027963 | 9.7549 | 0.043107 | 0.024208 | age_years | infant mortality (k<1)
66500 | 3 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 85 | 212 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.012605 | ba_g+dur_band+vintage_g | 0.32093 | 0.035304 | 4968.5 | THERMAL_AUX | 0.96019 | 0.29597 | 9.7549 | 0.043107 | 885.1131 | age_years | infant mortality (k<1)
66502 | 1 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 54 | 216 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0081871 | ba_g+dur_band+vintage_g | 0.23486 | 0.012788 | 3759.5 | THERMAL_AUX | 0.96019 | 0.13269 | 9.7549 | 0.043107 | 242.6029 | age_years | infant mortality (k<1)
66505 | 0 | 15 | 1.5-2.5h | LIB | CS | CISO | 2024 | 0 | 6 | 12 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0015597 | 0.0001 | 212 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.10698 | age_years | infant mortality (k<1)
66533 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 10 | 20 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.034381 | 0.0027511 |  | THERMAL_AUX | 0.96019 | 0.031937 | 9.7549 | 0.043107 |  | age_years | infant mortality (k<1)
66540 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 100 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.017639 | 0.0014114 | 8494 | THERMAL_AUX | 0.96019 | 0.016649 | 9.7549 | 0.043107 | 60.4963 | age_years | infant mortality (k<1)
66574 | 0 | 15 | >4.5h | LIB | CS | PNM | 2024 | 1 | 100 | 561.4 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0.0015597 | 0.0001 | 10717.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 5.4081 | age_years | infant mortality (k<1)
66575 | 0 | 21 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.031205 | 0.0014268 | 24158 | THERMAL_AUX | 0.96019 | 0.016828 | 9.7549 | 0.043107 | 173.9313 | age_years | infant mortality (k<1)
66598 | 0 | 15 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.02249 | 0.0014396 | 4250.5 | THERMAL_AUX | 0.96019 | 0.016976 | 9.7549 | 0.043107 | 30.8778 | age_years | infant mortality (k<1)
66599 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 0 | 7.3 | 7.1 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00041641 | 0.0001 | 423.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.2137 | age_years | infant mortality (k<1)
66606 | 0 | 2 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 175 | 350 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.0026357 | dur_band+climate_region | 0.00546 | 0.0026213 | 2393 | THERMAL_AUX | 0.96019 | 0.030478 | 9.7549 | 0.043107 | 31.6535 | age_years | infant mortality (k<1)
66616 | 3 | 30 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.2004 | 0.026453 | 5008 | THERMAL_AUX | 0.96019 | 0.23987 | 9.7549 | 0.043107 | 668.5 | age_years | infant mortality (k<1)
66617 | 0 | 17 | 2.5-4.5h | LIB | CT | CISO | 2024 | 0 | 100 | 400 | N | N | coastal | CISO | LIB | CT | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.025412 | 0.0014353 | 12037 | THERMAL_AUX | 0.96019 | 0.016926 | 9.7549 | 0.043107 | 87.1815 | age_years | infant mortality (k<1)
66619 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 1.2 | 4.6 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.010623 | 0.0014571 | 104 | THERMAL_AUX | 0.96019 | 0.017179 | 9.7549 | 0.043107 | 0.76468 | age_years | infant mortality (k<1)
66620 | 0 | 29 | >4.5h | LIB | CS | CISO | 2023 | 1 | 40 | 300 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0 | dur_band+climate_region | 0.0030111 | 0.0001 | 3569.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.8012 | age_years | infant mortality (k<1)
66627 | 0 | 31 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 260 | 1040 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.0037383 | ba_g+dur_band+vintage_g | 0.10769 | 0.0033357 | 26072.5 | THERMAL_AUX | 0.96019 | 0.038458 | 9.7549 | 0.043107 | 438.8613 | age_years | infant mortality (k<1)
66636 | 0 | 25 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.29681 | 0.0114 | 9634 | THERMAL_AUX | 0.96019 | 0.12005 | 9.7549 | 0.043107 | 554.1913 | age_years | infant mortality (k<1)
66637 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.01955 | 0.001444 | 15386 | THERMAL_AUX | 0.96019 | 0.017026 | 9.7549 | 0.043107 | 112.1079 | age_years | infant mortality (k<1)
66648 | 0 | 10 | >4.5h | LIB | CS | CISO | 2025 | 0 | 2 | 9 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0 | dur_band+climate_region | 0.0010404 | 0.0001 | 24 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.012111 | age_years | infant mortality (k<1)
66650 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 13 | 52 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.025412 | 0.0014353 | 1254.5 | THERMAL_AUX | 0.96019 | 0.016926 | 9.7549 | 0.043107 | 9.0861 | age_years | infant mortality (k<1)
66659 | 0 | 10 | <1.5h | LIB | CS | CISO | 2025 | 0 | 97 | 97 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0010404 | 0.0001 | 2732.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.3788 | age_years | infant mortality (k<1)
66660 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00052046 | 0.0001 | 2132 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.0758 | age_years | infant mortality (k<1)
66661 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00083247 | 0.0001 | 2374.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.1982 | age_years | infant mortality (k<1)
66662 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 32 | 32 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00052046 | 0.0001 | 733 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.36988 | age_years | infant mortality (k<1)
66666 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 125 | 500 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.026867 | 0.0014332 | 12549.5 | THERMAL_AUX | 0.96019 | 0.016902 | 9.7549 | 0.043107 | 90.7577 | age_years | infant mortality (k<1)
66669 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.025412 | 0.0014353 | 2180.5 | THERMAL_AUX | 0.96019 | 0.016926 | 9.7549 | 0.043107 | 15.7929 | age_years | infant mortality (k<1)
66688 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 103.6 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.017639 | 0.0014114 | 3953.5 | THERMAL_AUX | 0.96019 | 0.016649 | 9.7549 | 0.043107 | 28.1578 | age_years | infant mortality (k<1)
66690 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.023382 | 0.0014032 | 2817.5 | THERMAL_AUX | 0.96019 | 0.016554 | 9.7549 | 0.043107 | 19.9496 | age_years | infant mortality (k<1)
66694 | 0 | 14 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.048996 | 0.0033604 | 34752 | THERMAL_AUX | 0.96019 | 0.038731 | 9.7549 | 0.043107 | 589.2915 | age_years | infant mortality (k<1)
66699 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 59.7 | 59.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00041641 | 0.0001 | 4105.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 2.0717 | age_years | infant mortality (k<1)
66716 | 1 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 0 | 100 | 400 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.0037383 | ba_g+dur_band+vintage_g | 0.091921 | 0.0069301 | 7273 | THERMAL_AUX | 0.96019 | 0.076658 | 9.7549 | 0.043107 | 254.3362 | age_years | infant mortality (k<1)
66717 | 0 | 22 | 2.5-4.5h | OTH | CS | CPLE | 2023 | 1 | 18 | 72 | N | N | inland | CPLE | other | CS | 2022-23 | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.010849 | 0.0004735 | 0 | THERMAL_AUX | 0.96019 | 0.0056493 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66726 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 70 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.021022 | 0.0014418 | 7330 | THERMAL_AUX | 0.96019 | 0.017001 | 9.7549 | 0.043107 | 53.3288 | age_years | infant mortality (k<1)
66727 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0022222 | ba_g+dur_band+vintage_g | 0.052621 | 0.0021053 | 149 | THERMAL_AUX | 0.96019 | 0.024628 | 9.7549 | 0.043107 | 1.5829 | age_years | infant mortality (k<1)
66728 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0022222 | ba_g+dur_band+vintage_g | 0.052621 | 0.0021053 | 135 | THERMAL_AUX | 0.96019 | 0.024628 | 9.7549 | 0.043107 | 1.4342 | age_years | infant mortality (k<1)
66757 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.021022 | 0.0014418 | 6250 | THERMAL_AUX | 0.96019 | 0.017001 | 9.7549 | 0.043107 | 45.4714 | age_years | infant mortality (k<1)
66758 | 0 | 23 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 18.3 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.1156 | 0.004826 | 3258.5 | THERMAL_AUX | 0.96019 | 0.05468 | 9.7549 | 0.043107 | 79.3517 | age_years | infant mortality (k<1)
66764 | 0 | 23 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0023896 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66765 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66767 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 9.5 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 25.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.012868 | age_years | infant mortality (k<1)
66772 | 0 | 22 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 28 | 112 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.016212 | ba_g+dur_band+vintage_g | 0.27084 | 0.011821 | 2906 | THERMAL_AUX | 0.96019 | 0.12392 | 9.7549 | 0.043107 | 173.3402 | age_years | infant mortality (k<1)
66773 | 0 | 20 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.029763 | 0.0014289 | 7680.5 | THERMAL_AUX | 0.96019 | 0.016852 | 9.7549 | 0.043107 | 55.3799 | age_years | infant mortality (k<1)
66782 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 174.5 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 1.2213 | age_years | infant mortality (k<1)
66783 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.029057 | 0.001395 | 107.5 | THERMAL_AUX | 0.96019 | 0.016459 | 9.7549 | 0.043107 | 0.75674 | age_years | infant mortality (k<1)
66784 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 124 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 0.86785 | age_years | infant mortality (k<1)
66788 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 134 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 0.93784 | age_years | infant mortality (k<1)
66789 | 0 | 23 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.033271 | 0.001389 | 127 | THERMAL_AUX | 0.96019 | 0.016389 | 9.7549 | 0.043107 | 0.89013 | age_years | infant mortality (k<1)
66790 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 197 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 1.3788 | age_years | infant mortality (k<1)
66791 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 168.5 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 1.1793 | age_years | infant mortality (k<1)
66792 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.026228 | 0.0013991 | 94 | THERMAL_AUX | 0.96019 | 0.016506 | 9.7549 | 0.043107 | 0.66364 | age_years | infant mortality (k<1)
66794 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.034667 | 0.001387 | 101 | THERMAL_AUX | 0.96019 | 0.016366 | 9.7549 | 0.043107 | 0.70688 | age_years | infant mortality (k<1)
66795 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.026228 | 0.0013991 | 145 | THERMAL_AUX | 0.96019 | 0.016506 | 9.7549 | 0.043107 | 1.0237 | age_years | infant mortality (k<1)
66799 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.7 | 1.3 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.066477 | 0.0026596 | 0 | THERMAL_AUX | 0.96019 | 0.030909 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
66801 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.20158 | 0.012097 | 2294 | THERMAL_AUX | 0.96019 | 0.12645 | 9.7549 | 0.043107 | 140.0346 | age_years | infant mortality (k<1)
66804 | 0 | 17 | 1.5-2.5h | LIB | CT | ERCO | 2024 | 0 | 150 | 300 | N | Y | inland | ERCO | LIB | CT | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.21151 | 0.011947 | 10807 | THERMAL_AUX | 0.96019 | 0.12508 | 9.7549 | 0.043107 | 651.493 | age_years | infant mortality (k<1)
66807 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 3 | 12 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.016212 | ba_g+dur_band+vintage_g | 0.28836 | 0.011537 | 384 | THERMAL_AUX | 0.96019 | 0.12131 | 9.7549 | 0.043107 | 22.3548 | age_years | infant mortality (k<1)
66814 | 0 | 21 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.071737 | 0.0032801 | 5684.5 | THERMAL_AUX | 0.96019 | 0.037841 | 9.7549 | 0.043107 | 94.0874 | age_years | infant mortality (k<1)
66871 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 300 | 467 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.086489 | 0.013841 | 9676.5 | THERMAL_AUX | 0.96019 | 0.14204 | 9.7549 | 0.043107 | 675.8382 | age_years | infant mortality (k<1)
66872 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 158.3 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.1479 | 0.012911 | 4434 | THERMAL_AUX | 0.96019 | 0.13379 | 9.7549 | 0.043107 | 288.8652 | age_years | infant mortality (k<1)
66885 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 25 | 100 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.018073 | 0.0014461 | 1544.5 | THERMAL_AUX | 0.96019 | 0.017052 | 9.7549 | 0.043107 | 11.2707 | age_years | infant mortality (k<1)
66890 | 0 | 1 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 38 | 152 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0015315 | 0.0014705 | 4 | THERMAL_AUX | 0.96019 | 0.017334 | 9.7549 | 0.043107 | 0.029681 | age_years | infant mortality (k<1)
66905 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 157.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 2260 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 145.2806 | age_years | infant mortality (k<1)
66925 | 0 | 23 | <1.5h | LIB | BL | TEPC | 2023 | 1 | 20 | 20 | N | N | arid | other | LIB | BL | 2022-23 | 0 | 0 | 0.0125 | ba_g+dur_band+vintage_g | 0.23043 | 0.0096197 | 2244 | THERMAL_AUX | 0.96019 | 0.10328 | 9.7549 | 0.043107 | 108.9277 | age_years | infant mortality (k<1)
66926 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 161.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 5.4452 | age_years | infant mortality (k<1)
66927 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 76 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 2.5625 | age_years | infant mortality (k<1)
66928 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 82.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 2.7816 | age_years | infant mortality (k<1)
66929 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 101 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 3.4054 | age_years | infant mortality (k<1)
66930 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 149 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 5.0238 | age_years | infant mortality (k<1)
66931 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 109.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 3.692 | age_years | infant mortality (k<1)
66932 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 77.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 2.613 | age_years | infant mortality (k<1)
66933 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 145.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 4.9058 | age_years | infant mortality (k<1)
66934 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 97.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 3.2874 | age_years | infant mortality (k<1)
66935 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.16701 | 0.0066817 | 98.5 | THERMAL_AUX | 0.96019 | 0.074118 | 9.7549 | 0.043107 | 3.3211 | age_years | infant mortality (k<1)
66946 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 45 | 180 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.026867 | 0.0014332 | 5659 | THERMAL_AUX | 0.96019 | 0.016902 | 9.7549 | 0.043107 | 40.9258 | age_years | infant mortality (k<1)
66949 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 40 | 160 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.023953 | 0.0014375 | 4135 | THERMAL_AUX | 0.96019 | 0.016951 | 9.7549 | 0.043107 | 29.9938 | age_years | infant mortality (k<1)
66950 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 59 | 236 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.023953 | 0.0014375 | 6534.5 | THERMAL_AUX | 0.96019 | 0.016951 | 9.7549 | 0.043107 | 47.3989 | age_years | infant mortality (k<1)
66951 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.01955 | 0.001444 | 9087 | THERMAL_AUX | 0.96019 | 0.017026 | 9.7549 | 0.043107 | 66.2111 | age_years | infant mortality (k<1)
66966 | 2 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 2.1 | 4.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0.051185 | 0.0063132 | 40.5 | THERMAL_AUX | 0.96019 | 0.070323 | 9.7549 | 0.043107 | 1.2902 | age_years | infant mortality (k<1)
67019 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.023382 | 0.0014032 | 2238 | THERMAL_AUX | 0.96019 | 0.016554 | 9.7549 | 0.043107 | 15.8464 | age_years | infant mortality (k<1)
67036 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.034864 | 0.0025751 | 76 | THERMAL_AUX | 0.96019 | 0.029956 | 9.7549 | 0.043107 | 0.98755 | age_years | infant mortality (k<1)
67037 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.034864 | 0.0025751 | 85 | THERMAL_AUX | 0.96019 | 0.029956 | 9.7549 | 0.043107 | 1.1045 | age_years | infant mortality (k<1)
67039 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 92 | 368 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0091189 | 0.0014593 | 11494 | THERMAL_AUX | 0.96019 | 0.017204 | 9.7549 | 0.043107 | 84.6404 | age_years | infant mortality (k<1)
67040 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 103 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.051975 | age_years | infant mortality (k<1)
67041 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 15 | 30 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 145.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.073421 | age_years | infant mortality (k<1)
67042 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 91.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.046172 | age_years | infant mortality (k<1)
67043 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 48 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.024221 | age_years | infant mortality (k<1)
67044 | 0 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 58.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02952 | age_years | infant mortality (k<1)
67083 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 174 | 407.4 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.20158 | 0.012097 | 9349 | THERMAL_AUX | 0.96019 | 0.12645 | 9.7549 | 0.043107 | 570.6991 | age_years | infant mortality (k<1)
67091 | 0 | 19 | 2.5-4.5h | LIB | CS | NEVP | 2024 | 1 | 85 | 340 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.065352 | 0.0033026 | 10076 | THERMAL_AUX | 0.96019 | 0.038091 | 9.7549 | 0.043107 | 167.9209 | age_years | infant mortality (k<1)
67092 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 15 | 60 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.026867 | 0.0014332 | 1518.5 | THERMAL_AUX | 0.96019 | 0.016902 | 9.7549 | 0.043107 | 10.9818 | age_years | infant mortality (k<1)
67093 | 0 | 22 | <1.5h | LIB | CS | CISO | 2020 | 0 | 77 | 77 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.002286 | 0.0001 | 1735 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.8755 | age_years | infant mortality (k<1)
67122 | 0 | 24 | 1.5-2.5h | LIB | CS | SWPP | 2023 | 0 | 1 | 2.4 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 46.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.023464 | age_years | infant mortality (k<1)
67162 | 0 | 19 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0019749 | 0.0001 | 121 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.061058 | age_years | infant mortality (k<1)
67170 | 0 | 22 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 2.4 | 8.9 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.032642 | 0.0014247 | 116 | THERMAL_AUX | 0.96019 | 0.016803 | 9.7549 | 0.043107 | 0.83393 | age_years | infant mortality (k<1)
67175 | 2 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 300 | 600 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.013477 | ba_g+dur_band+vintage_g | 0.24404 | 0.031409 | 13821 | THERMAL_AUX | 0.96019 | 0.27236 | 9.7549 | 0.043107 | 2190.5315 | age_years | infant mortality (k<1)
67183 | 0 | 14 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 60 | 240 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.048996 | 0.0033604 | 5888 | THERMAL_AUX | 0.96019 | 0.038731 | 9.7549 | 0.043107 | 99.8431 | age_years | infant mortality (k<1)
67185 | 0 | 18 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | Y | N | inland | ISNE | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0018711 | 0.0001 | 164.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.083008 | age_years | infant mortality (k<1)
67186 | 0 | 17 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 5 | 22.4 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0017673 | 0.0001 | 418 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.21093 | age_years | infant mortality (k<1)
67187 | 0 | 14 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 3 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0014559 | 0.0001 | 212.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.10723 | age_years | infant mortality (k<1)
67236 | 2 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.23066 | 0.035937 | 9298.5 | THERMAL_AUX | 0.96019 | 0.29966 | 9.7549 | 0.043107 | 1686.1796 | age_years | infant mortality (k<1)
67237 | 2 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 207.9 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.23066 | 0.035937 | 10541 | THERMAL_AUX | 0.96019 | 0.29966 | 9.7549 | 0.043107 | 1911.4931 | age_years | infant mortality (k<1)
67275 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 1.3 | 5.1 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0037352 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
67278 | 0 | 3 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 1.1 | 2.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00031234 | 0.0001 | 2 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0010092 | age_years | infant mortality (k<1)
67281 | 0 | 20 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 4 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0020786 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
67282 | 0 | 18 | 1.5-2.5h | LIB | CS | NYIS | 2024 | 1 | 5 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.0026681 | dur_band+climate_region | 0.047634 | 0.002541 | 0 | THERMAL_AUX | 0.96019 | 0.029572 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
67284 | 0 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 70.5 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.25769 | 0.011247 | 3063.5 | THERMAL_AUX | 0.96019 | 0.11864 | 9.7549 | 0.043107 | 173.865 | age_years | infant mortality (k<1)
67285 | 0 | 19 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 215 | 860 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0019749 | 0.0001 | 23676 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 11.9471 | age_years | infant mortality (k<1)
67291 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0010404 | 0.0001 | 33868.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 17.0903 | age_years | infant mortality (k<1)
67296 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 0.4 | 0.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.076909 | 0.0020513 | 1 | THERMAL_AUX | 0.96019 | 0.024013 | 9.7549 | 0.043107 | 0.010351 | age_years | infant mortality (k<1)
67299 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0045803 | 0.001466 | 10309 | THERMAL_AUX | 0.96019 | 0.017282 | 9.7549 | 0.043107 | 76.2619 | age_years | infant mortality (k<1)
67300 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.065352 | 0.0033026 | 1052.5 | THERMAL_AUX | 0.96019 | 0.038091 | 9.7549 | 0.043107 | 17.5404 | age_years | infant mortality (k<1)
67301 | 0 | 20 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.068555 | 0.0032913 | 823.5 | THERMAL_AUX | 0.96019 | 0.037966 | 9.7549 | 0.043107 | 13.6769 | age_years | infant mortality (k<1)
67302 | 0 | 15 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.052313 | 0.0033487 | 723.5 | THERMAL_AUX | 0.96019 | 0.038602 | 9.7549 | 0.043107 | 12.2256 | age_years | infant mortality (k<1)
67303 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.065352 | 0.0033026 | 754 | THERMAL_AUX | 0.96019 | 0.038091 | 9.7549 | 0.043107 | 12.5657 | age_years | infant mortality (k<1)
67304 | 0 | 16 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.055607 | 0.0033371 | 1109 | THERMAL_AUX | 0.96019 | 0.038473 | 9.7549 | 0.043107 | 18.6747 | age_years | infant mortality (k<1)
67305 | 0 | 18 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.062126 | 0.003314 | 1177.5 | THERMAL_AUX | 0.96019 | 0.038218 | 9.7549 | 0.043107 | 19.6913 | age_years | infant mortality (k<1)
67306 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.065352 | 0.0033026 | 1210 | THERMAL_AUX | 0.96019 | 0.038091 | 9.7549 | 0.043107 | 20.1652 | age_years | infant mortality (k<1)
67307 | 0 | 18 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.062126 | 0.003314 | 841 | THERMAL_AUX | 0.96019 | 0.038218 | 9.7549 | 0.043107 | 14.064 | age_years | infant mortality (k<1)
67321 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 70 | 268 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0010404 | 0.0001 | 6484 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.2719 | age_years | infant mortality (k<1)
67323 | 0 | 9 | 1.5-2.5h | LIB | CS | PSCO | 2025 | 1 | 11.2 | 20 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00093643 | 0.0001 | 201 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.10143 | age_years | infant mortality (k<1)
67328 | 0 | 6 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 75 | 300 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00062448 | 0.0001 | 8034 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 4.054 | age_years | infant mortality (k<1)
67454 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 170 | 680 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00083247 | 0.0001 | 20475 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 10.3319 | age_years | infant mortality (k<1)
67455 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 85 | 340 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00083247 | 0.0001 | 10185.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 5.1397 | age_years | infant mortality (k<1)
67474 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00093643 | 0.0001 | 31962 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 16.1283 | age_years | infant mortality (k<1)
67489 | 0 | 20 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 45 | 180 | Y | Y | inland | MISO | LIB | CS | 2024+ | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0020786 | 0.0001 | 7351 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.7094 | age_years | infant mortality (k<1)
67493 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.024807 | 0.0014011 | 129.5 | THERMAL_AUX | 0.96019 | 0.01653 | 9.7549 | 0.043107 | 0.9156 | age_years | infant mortality (k<1)
67494 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.029057 | 0.001395 | 126.5 | THERMAL_AUX | 0.96019 | 0.016459 | 9.7549 | 0.043107 | 0.89049 | age_years | infant mortality (k<1)
67495 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.024807 | 0.0014011 | 174.5 | THERMAL_AUX | 0.96019 | 0.01653 | 9.7549 | 0.043107 | 1.2338 | age_years | infant mortality (k<1)
67496 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.024807 | 0.0014011 | 164.5 | THERMAL_AUX | 0.96019 | 0.01653 | 9.7549 | 0.043107 | 1.1631 | age_years | infant mortality (k<1)
67498 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 185 | 740 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.010623 | 0.0014571 | 16536 | THERMAL_AUX | 0.96019 | 0.017179 | 9.7549 | 0.043107 | 121.5843 | age_years | infant mortality (k<1)
67503 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 213.8 | 855 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00093643 | 0.0001 | 24594 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 12.4103 | age_years | infant mortality (k<1)
67545 | 0 | 14 | >4.5h | LIB | CS | MISO | 2024 | 1 | 5 | 30.6 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.0086207 | dur_band+climate_region | 0.11166 | 0.0076581 | 521 | THERMAL_AUX | 0.96019 | 0.084021 | 9.7549 | 0.043107 | 20.1333 | age_years | infant mortality (k<1)
67549 | 0 | 7 | 2.5-4.5h | LIB | CT | IPCO | 2025 | 0 | 150 | 600 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.025113 | 0.0034448 | 17424 | THERMAL_AUX | 0.96019 | 0.039665 | 9.7549 | 0.043107 | 302.8797 | age_years | infant mortality (k<1)
67573 | 0 | 6 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 82 | 328 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.021603 | 0.0034572 | 9267 | THERMAL_AUX | 0.96019 | 0.039802 | 9.7549 | 0.043107 | 161.6674 | age_years | infant mortality (k<1)
67577 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 2.2 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.052621 | 0.0021053 | 301.5 | THERMAL_AUX | 0.96019 | 0.024628 | 9.7549 | 0.043107 | 3.203 | age_years | infant mortality (k<1)
67578 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 1 | 2 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0022222 | ba_g+dur_band+vintage_g | 0.052621 | 0.0021053 | 344 | THERMAL_AUX | 0.96019 | 0.024628 | 9.7549 | 0.043107 | 3.6545 | age_years | infant mortality (k<1)
67579 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 82 | 328 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.01955 | 0.001444 | 8077.5 | THERMAL_AUX | 0.96019 | 0.017026 | 9.7549 | 0.043107 | 58.8556 | age_years | infant mortality (k<1)
67598 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.11209 | 0.013453 | 9219 | THERMAL_AUX | 0.96019 | 0.13862 | 9.7549 | 0.043107 | 625.8421 | age_years | infant mortality (k<1)
67680 | 0 | 6 | >4.5h | LIB | CS | CISO | 2025 | 0 | 400 | 1800 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0.00062448 | 0.0001 | 20756.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 10.4739 | age_years | infant mortality (k<1)
67695 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 30 | 127 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.023953 | 0.0014375 | 1766 | THERMAL_AUX | 0.96019 | 0.016951 | 9.7549 | 0.043107 | 12.8099 | age_years | infant mortality (k<1)
67698 | 0 | 14 | 1.5-2.5h | LIB | CS | PGE | 2024 | 0 | 17 | 34 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0014559 | 0.0001 | 789.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.39839 | age_years | infant mortality (k<1)
67710 | 0 | 5 | 2.5-4.5h | OTH | OT | PNM | 2025 | 1 | 57.8 | 231.4 | N | N | arid | other | other | other | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.018068 | 0.0034697 | 5449 | THERMAL_AUX | 0.96019 | 0.03994 | 9.7549 | 0.043107 | 95.404 | age_years | infant mortality (k<1)
67711 | 0 | 6 | 2.5-4.5h | LIB | CS | PGE | 2025 | 0 | 200 | 800 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.021603 | 0.0034572 | 15765 | THERMAL_AUX | 0.96019 | 0.039802 | 9.7549 | 0.043107 | 275.0282 | age_years | infant mortality (k<1)
67712 | 1 | 13 | 2.5-4.5h | LIB | CS | PGE | 2024 | 0 | 75 | 300 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.045656 | 0.0068843 | 6637.5 | THERMAL_AUX | 0.96019 | 0.07619 | 9.7549 | 0.043107 | 230.5778 | age_years | infant mortality (k<1)
67721 | 0 | 14 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100.3 | 145 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.020519 | 0.0014073 | 3587 | THERMAL_AUX | 0.96019 | 0.016601 | 9.7549 | 0.043107 | 25.4726 | age_years | infant mortality (k<1)
67734 | 0 | 9 | 2.5-4.5h | LIB | CT | CISO | 2025 | 0 | 200 | 800 | Y | Y | arid | CISO | LIB | CT | 2024+ | 1 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.013616 | 0.0014527 | 22863 | THERMAL_AUX | 0.96019 | 0.017128 | 9.7549 | 0.043107 | 167.5961 | age_years | infant mortality (k<1)
67736 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 279 | 1116 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.010623 | 0.0014571 | 32710 | THERMAL_AUX | 0.96019 | 0.017179 | 9.7549 | 0.043107 | 240.5068 | age_years | infant mortality (k<1)
67737 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 304 | 440.8 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 10426 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 74.8062 | age_years | infant mortality (k<1)
67738 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 204 | 298 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.019081 | 0.0014094 | 6925 | THERMAL_AUX | 0.96019 | 0.016625 | 9.7549 | 0.043107 | 49.2491 | age_years | infant mortality (k<1)
67739 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 120 | 174 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.019081 | 0.0014094 | 4031 | THERMAL_AUX | 0.96019 | 0.016625 | 9.7549 | 0.043107 | 28.6676 | age_years | infant mortality (k<1)
67740 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 240 | 480 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.086489 | 0.013841 | 12535 | THERMAL_AUX | 0.96019 | 0.14204 | 9.7549 | 0.043107 | 875.4852 | age_years | infant mortality (k<1)
67743 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.066477 | 0.0026596 | 0 | THERMAL_AUX | 0.96019 | 0.030909 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
67745 | 0 | 24 | <1.5h | LIB | CS | NYIS | 2022 | 1 | 5 | 2 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.002069 | dur_band+climate_region | 0.049171 | 0.0019672 | 0 | THERMAL_AUX | 0.96019 | 0.023051 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
67752 | 0 | 7 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 102.6 | 205.1 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.09947 | 0.013644 | 7793 | THERMAL_AUX | 0.96019 | 0.14031 | 9.7549 | 0.043107 | 536.5541 | age_years | infant mortality (k<1)
67758 | 0 | 11 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 14 | 56 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0011443 | 0.0001 | 835 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.42135 | age_years | infant mortality (k<1)
67762 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72.2 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.19139 | 0.012252 | 2744 | THERMAL_AUX | 0.96019 | 0.12785 | 9.7549 | 0.043107 | 169.6416 | age_years | infant mortality (k<1)
67764 | 0 | 5 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 117 | 472 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0076107 | 0.0014615 | 11958 | THERMAL_AUX | 0.96019 | 0.01723 | 9.7549 | 0.043107 | 88.1913 | age_years | infant mortality (k<1)
67828 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 25 | 100 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.012122 | 0.0014549 | 2611 | THERMAL_AUX | 0.96019 | 0.017153 | 9.7549 | 0.043107 | 19.1688 | age_years | infant mortality (k<1)
67829 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 20 | 80 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.012122 | 0.0014549 | 2208.5 | THERMAL_AUX | 0.96019 | 0.017153 | 9.7549 | 0.043107 | 16.2138 | age_years | infant mortality (k<1)
67843 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 498 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 32.0131 | age_years | infant mortality (k<1)
67845 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 454 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 29.1847 | age_years | infant mortality (k<1)
67850 | 0 | 1 | 2.5-4.5h | LIB | CS | IID | 2025 | 1 | 35 | 140 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 399 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 7.0884 | age_years | infant mortality (k<1)
67851 | 0 | 14 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 20 | N | Y | inland | PJM | LIB | CS | 2024+ | 0 | 1 | 0.0054568 | dur_band+climate_region | 0.073698 | 0.0050546 | 2762.5 | THERMAL_AUX | 0.96019 | 0.05712 | 9.7549 | 0.043107 | 70.4602 | age_years | infant mortality (k<1)
67855 | 0 | 15 | 2.5-4.5h | LIB | CS | AZPS | 2024.59 | 0 | 200 | 808.4 | N | Y | arid | AZPS | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0015597 | 0.0001 | 11719.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 5.9138 | age_years | infant mortality (k<1)
67860 | 0 | 21 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.2489 | 0.01138 | 6750 | THERMAL_AUX | 0.96019 | 0.11987 | 9.7549 | 0.043107 | 387.6279 | age_years | infant mortality (k<1)
67861 | 0 | 17 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.21151 | 0.011947 | 6402.5 | THERMAL_AUX | 0.96019 | 0.12508 | 9.7549 | 0.043107 | 385.9706 | age_years | infant mortality (k<1)
67869 | 0 | 13 | 2.5-4.5h | LIB | CT | PGE | 2024 | 0 | 200 | 800 | N | N | inland | other | LIB | CT | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.045656 | 0.0033722 | 21922.5 | THERMAL_AUX | 0.96019 | 0.038862 | 9.7549 | 0.043107 | 373.0466 | age_years | infant mortality (k<1)
67880 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 21.7 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 10.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0052984 | age_years | infant mortality (k<1)
67882 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 10 | 43.4 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 32.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0164 | age_years | infant mortality (k<1)
67883 | 0 | 14 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 0 | 8 | 34.1 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0014559 | 0.0001 | 38 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.019175 | age_years | infant mortality (k<1)
67886 | 0 | 24 | 2.5-4.5h | NIB | CS | NYIS | 2023 | 0 | 3 | 12.4 | Y | N | coastal | NYIS | other | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 8 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0040369 | age_years | infant mortality (k<1)
67893 | 0 | 12 | 2.5-4.5h | LIB | CS | MISO | 2025 | 1 | 56.3 | 225 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 9601.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 4.845 | age_years | infant mortality (k<1)
67898 | 0 | 1 | 2.5-4.5h | LIB | CS | NEVP | 2025 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 8671 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 154.0431 | age_years | infant mortality (k<1)
67899 | 3 | 24 | <1.5h | LIB | CS | PJM | 2021 | 0 | 6.2 | 6.2 | N | N | coastal | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.002069 | dur_band+climate_region | 0.049171 | 0.0081136 | 735.5 | THERMAL_AUX | 0.96019 | 0.088567 | 9.7549 | 0.043107 | 30.1128 | age_years | infant mortality (k<1)
67905 | 0 | 6 | 2.5-4.5h | LIB | CS | TEPC | 2025 | 0 | 200 | 800 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.021603 | 0.0034572 | 23941 | THERMAL_AUX | 0.96019 | 0.039802 | 9.7549 | 0.043107 | 417.6625 | age_years | infant mortality (k<1)
67931 | 0 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 113.5 | 454 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0060978 | 0.0014638 | 7553.5 | THERMAL_AUX | 0.96019 | 0.017256 | 9.7549 | 0.043107 | 55.7926 | age_years | infant mortality (k<1)
67948 | 2 | 24 | >4.5h | LIB | CS | SWPP | 2022 | 0 | 1.8 | 9.1 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0086207 | dur_band+climate_region | 0.17728 | 0.021865 | 28 | THERMAL_AUX | 0.96019 | 0.20703 | 9.7549 | 0.043107 | 3.0894 | age_years | infant mortality (k<1)
67963 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.013288 | 0.0014177 | 125 | THERMAL_AUX | 0.96019 | 0.016722 | 9.7549 | 0.043107 | 0.89422 | age_years | infant mortality (k<1)
67968 | 0 | 9 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.12436 | 0.013267 | 4356 | THERMAL_AUX | 0.96019 | 0.13697 | 9.7549 | 0.043107 | 291.626 | age_years | infant mortality (k<1)
67973 | 0 | 3 | <1.5h | LIB | BL | AZPS | 2025 | 0 | 113 | 113 | N | N | arid | AZPS | LIB | BL | 2024+ | 0 | 0 | 0.0040674 | dur_band+climate_region | 0.012549 | 0.0040164 | 9962 | THERMAL_AUX | 0.96019 | 0.045937 | 9.7549 | 0.043107 | 201.899 | age_years | infant mortality (k<1)
68012 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 99.7 | 398.8 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.013616 | 0.0014527 | 12581 | THERMAL_AUX | 0.96019 | 0.017128 | 9.7549 | 0.043107 | 92.2244 | age_years | infant mortality (k<1)
68023 | 0 | 2 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 16.7 | 64 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0030582 | 0.0014683 | 955.5 | THERMAL_AUX | 0.96019 | 0.017308 | 9.7549 | 0.043107 | 7.0792 | age_years | infant mortality (k<1)
68058 | 0 | 13 | >4.5h | OTH | CS | WACM | 2024 | 0 | 35.4 | 235 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0 | dur_band+climate_region | 0.0013521 | 0.0001 | 1684.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.85001 | age_years | infant mortality (k<1)
68064 | 0 | 17 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 1.2 | 2.1 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0017673 | 0.0001 | 175.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.088559 | age_years | infant mortality (k<1)
68069 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2.2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 31.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.015895 | age_years | infant mortality (k<1)
68146 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.1479 | 0.012911 | 4583 | THERMAL_AUX | 0.96019 | 0.13379 | 9.7549 | 0.043107 | 298.5722 | age_years | infant mortality (k<1)
68147 | 0 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 45.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02296 | age_years | infant mortality (k<1)
68148 | 0 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0013521 | 0.0001 | 43 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.021698 | age_years | infant mortality (k<1)
68189 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.1479 | 0.012911 | 2254 | THERMAL_AUX | 0.96019 | 0.13379 | 9.7549 | 0.043107 | 146.8431 | age_years | infant mortality (k<1)
68266 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.3 | 0.5 | N | Y | inland | CISO | LIB | CS | <=2019 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 5.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0027753 | age_years | infant mortality (k<1)
68322 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 300 | 1200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0045803 | 0.001466 | 3358 | THERMAL_AUX | 0.96019 | 0.017282 | 9.7549 | 0.043107 | 24.8412 | age_years | infant mortality (k<1)
68324 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0045803 | 0.001466 | 1833 | THERMAL_AUX | 0.96019 | 0.017282 | 9.7549 | 0.043107 | 13.5598 | age_years | infant mortality (k<1)
68335 | 0 | 16 | 2.5-4.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 7.1 | N | Y | coastal | PJM | LIB | CS | 2024+ | 0 | 1 | 0.0065359 | dur_band+climate_region | 0.098214 | 0.005894 | 0 | THERMAL_AUX | 0.96019 | 0.065968 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
68423 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.059371 | 0.014252 | 5663.5 | THERMAL_AUX | 0.96019 | 0.14563 | 9.7549 | 0.043107 | 407.2996 | age_years | infant mortality (k<1)
68424 | 0 | 7 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 104.9 | 400 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00072849 | 0.0001 | 7156 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 3.611 | age_years | infant mortality (k<1)
68475 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.0026357 | dur_band+climate_region | 0.021488 | 0.0025791 | 58 | THERMAL_AUX | 0.96019 | 0.030002 | 9.7549 | 0.043107 | 0.75483 | age_years | infant mortality (k<1)
68476 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.0026357 | dur_band+climate_region | 0.021488 | 0.0025791 | 58 | THERMAL_AUX | 0.96019 | 0.030002 | 9.7549 | 0.043107 | 0.75483 | age_years | infant mortality (k<1)
68493 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2020.8182 | 0 | 3.3 | 3.3 | N | N | industrial | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 87.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.044153 | age_years | infant mortality (k<1)
68496 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 60 | 120 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.073128 | 0.014044 | 1722 | THERMAL_AUX | 0.96019 | 0.14381 | 9.7549 | 0.043107 | 122.0291 | age_years | infant mortality (k<1)
68522 | 0 | 9 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00093643 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
68523 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00062448 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
68524 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00062448 | 0.0001 | 3 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.0015138 | age_years | infant mortality (k<1)
68525 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00062448 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
68547 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.01955 | 0.001444 | 94 | THERMAL_AUX | 0.96019 | 0.017026 | 9.7549 | 0.043107 | 0.68492 | age_years | infant mortality (k<1)
68548 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 0.7 | 2.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.01955 | 0.001444 | 52 | THERMAL_AUX | 0.96019 | 0.017026 | 9.7549 | 0.043107 | 0.37889 | age_years | infant mortality (k<1)
68576 | 0 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 260 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.028598 | 0.0034325 | 6390 | THERMAL_AUX | 0.96019 | 0.039529 | 9.7549 | 0.043107 | 110.6797 | age_years | infant mortality (k<1)
68577 | 0 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 40 | 160 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.028598 | 0.0034325 | 4343.5 | THERMAL_AUX | 0.96019 | 0.039529 | 9.7549 | 0.043107 | 75.2327 | age_years | infant mortality (k<1)
68596 | 0 | 1 | 2.5-4.5h | LIB | CS | PACE | 2025 | 0 | 200 | 800 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0036666 | 0.0035206 | 2851 | THERMAL_AUX | 0.96019 | 0.040501 | 9.7549 | 0.043107 | 50.6489 | age_years | infant mortality (k<1)
68605 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2021 | 1 | 0.5 | 1.3 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0.0052083 | ba_g+dur_band+vintage_g | 0.11519 | 0.0046084 | 9 | THERMAL_AUX | 0.96019 | 0.052347 | 9.7549 | 0.043107 | 0.20929 | age_years | infant mortality (k<1)
68611 | 0 | 10 | 1.5-2.5h | LIB | CS | CEA | 2024 | 0 | 40 | 80 | N | N | coastal | other | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0010404 | 0.0001 | 1 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.00050461 | age_years | infant mortality (k<1)
68613 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 228.7 | 228.7 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.004469 | 0.0014304 | 5939 | THERMAL_AUX | 0.96019 | 0.016869 | 9.7549 | 0.043107 | 42.8661 | age_years | infant mortality (k<1)
68617 | 0 | 2 | 2.5-4.5h | LIB | CT | PNM | 2025 | 0 | 100 | 400 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0073063 | 0.0035078 | 11974.5 | THERMAL_AUX | 0.96019 | 0.040359 | 9.7549 | 0.043107 | 211.9536 | age_years | infant mortality (k<1)
68679 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 45.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02296 | age_years | infant mortality (k<1)
68680 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 50 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02523 | age_years | infant mortality (k<1)
68683 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 337.5 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 21.6957 | age_years | infant mortality (k<1)
68684 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 386.5 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 24.8455 | age_years | infant mortality (k<1)
68685 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 12.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.017639 | 0.0014114 | 216 | THERMAL_AUX | 0.96019 | 0.016649 | 9.7549 | 0.043107 | 1.5384 | age_years | infant mortality (k<1)
68686 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 33 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 2.1214 | age_years | infant mortality (k<1)
68687 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 43.5 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 2.7963 | age_years | infant mortality (k<1)
68742 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 50 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.02523 | age_years | infant mortality (k<1)
68743 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3.3 | 3.3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.0024933 | 0.0001 | 119 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.060048 | age_years | infant mortality (k<1)
68773 | 0 | 23 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 2.8 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.0021583 | ba_g+dur_band+vintage_g | 0.049157 | 0.0020522 | 68.5 | THERMAL_AUX | 0.96019 | 0.024022 | 9.7549 | 0.043107 | 0.70935 | age_years | infant mortality (k<1)
68801 | 0 | 3 | 2.5-4.5h | LIB | CS | WALC | 2025 | 0 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.01092 | 0.003495 | 239 | THERMAL_AUX | 0.96019 | 0.040219 | 9.7549 | 0.043107 | 4.215 | age_years | infant mortality (k<1)
68802 | 0 | 8 | <1.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 65 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0054568 | dur_band+climate_region | 0.043487 | 0.0052195 | 8224 | THERMAL_AUX | 0.96019 | 0.058871 | 9.7549 | 0.043107 | 216.6022 | age_years | infant mortality (k<1)
68809 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 220 | 440 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.045199 | 0.014467 | 189 | THERMAL_AUX | 0.96019 | 0.14749 | 9.7549 | 0.043107 | 13.797 | age_years | infant mortality (k<1)
68816 | 0 | 20 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 2.6 | 5.3 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0020786 | 0.0001 | 21.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.010849 | age_years | infant mortality (k<1)
68842 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.0088982 | 0.001424 | 7672 | THERMAL_AUX | 0.96019 | 0.016795 | 9.7549 | 0.043107 | 55.128 | age_years | infant mortality (k<1)
68868 | 0 | 5 | 2.5-4.5h | LIB | CS | PNM | 2025 | 1 | 50 | 200 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.0035336 | ba_g+dur_band+vintage_g | 0.018068 | 0.0034697 | 5754 | THERMAL_AUX | 0.96019 | 0.03994 | 9.7549 | 0.043107 | 100.7441 | age_years | infant mortality (k<1)
68874 | 0 | 8 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 13 | 45 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0004787 | dur_band+climate_region | 0.0039725 | 0.0004768 | 1183 | THERMAL_AUX | 0.96019 | 0.0056883 | 9.7549 | 0.043107 | 2.8462 | age_years | infant mortality (k<1)
68875 | 0 | 7 | 2.5-4.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 22.4 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0.00072849 | 0.0001 | 334 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.16854 | age_years | infant mortality (k<1)
68878 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 165 | 165 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.013288 | 0.0014177 | 6053 | THERMAL_AUX | 0.96019 | 0.016722 | 9.7549 | 0.043107 | 43.3019 | age_years | infant mortality (k<1)
68879 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.073128 | 0.014044 | 5874 | THERMAL_AUX | 0.96019 | 0.14381 | 9.7549 | 0.043107 | 416.2596 | age_years | infant mortality (k<1)
68891 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.0091189 | 0.0014593 | 84 | THERMAL_AUX | 0.96019 | 0.017204 | 9.7549 | 0.043107 | 0.61857 | age_years | infant mortality (k<1)
68895 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 236.3 | 236.3 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.0080214 | ba_g+dur_band+vintage_g | 0.062645 | 0.0075189 | 4965.5 | THERMAL_AUX | 0.96019 | 0.082622 | 9.7549 | 0.043107 | 188.3959 | age_years | infant mortality (k<1)
68896 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 123.3 | 123 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.011829 | 0.0014198 | 3260.5 | THERMAL_AUX | 0.96019 | 0.016746 | 9.7549 | 0.043107 | 23.3594 | age_years | infant mortality (k<1)
68906 | 0 | 1 | <1.5h | LIB | CS | DOPD | 2025 | 1 | 200 | 200 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.0054568 | dur_band+climate_region | 0.0056509 | 0.0054259 | 9840 | THERMAL_AUX | 0.96019 | 0.061055 | 9.7549 | 0.043107 | 269.4156 | age_years | infant mortality (k<1)
68912 | 0 | 6 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 50 | 200 | Y | Y | inland | ERCO | LIB | CS | 2024+ | 1 | 1 | 0.0004787 | dur_band+climate_region | 0.0029823 | 0.00047727 | 1967 | THERMAL_AUX | 0.96019 | 0.005694 | 9.7549 | 0.043107 | 4.7372 | age_years | infant mortality (k<1)
68997 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 0.7 | 2.6 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.0014728 | ba_g+dur_band+vintage_g | 0.010623 | 0.0014571 | 55 | THERMAL_AUX | 0.96019 | 0.017179 | 9.7549 | 0.043107 | 0.4044 | age_years | infant mortality (k<1)
69023 | 0 | 2 | 1.5-2.5h | LIB | CS | CPLE | 2025 | 0 | 100 | 200 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00020825 | 0.0001 | 2900.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 1.4636 | age_years | infant mortality (k<1)
69026 | 0 | 2 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 283.2 | 283.2 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.0029838 | 0.0014325 | 13663 | THERMAL_AUX | 0.96019 | 0.016894 | 9.7549 | 0.043107 | 98.7629 | age_years | infant mortality (k<1)
69045 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.073128 | 0.014044 | 10338 | THERMAL_AUX | 0.96019 | 0.14381 | 9.7549 | 0.043107 | 732.5999 | age_years | infant mortality (k<1)
69122 | 0 | 4 | <1.5h | LIB | CS | PSCO | 2025 | 0 | 100 | 100 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.0054568 | dur_band+climate_region | 0.022227 | 0.0053355 | 11212 | THERMAL_AUX | 0.96019 | 0.0601 | 9.7549 | 0.043107 | 301.8631 | age_years | infant mortality (k<1)
69128 | 0 | 12 | 1.5-2.5h | LIB | CS | PJM | 2023 | 0 | 1.1 | 2.3 | N | Y | coastal | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.0026357 | dur_band+climate_region | 0.03189 | 0.0025517 | 58 | THERMAL_AUX | 0.96019 | 0.029692 | 9.7549 | 0.043107 | 0.74681 | age_years | infant mortality (k<1)
69171 | 0 | 2 | 2.5-4.5h | LIB | CS | DUK | 2025 | 0 | 50 | 200 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.0035336 | ba_g+dur_band+vintage_g | 0.0073063 | 0.0035078 | 5839.5 | THERMAL_AUX | 0.96019 | 0.040359 | 9.7549 | 0.043107 | 103.3616 | age_years | infant mortality (k<1)
69187 | 0 | 1 | 1.5-2.5h | LIB | CS | TEC | 2019 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.0081522 | ba_g+dur_band+vintage_g | 0.0084187 | 0.0080835 | 24 | THERMAL_AUX | 0.96019 | 0.088268 | 9.7549 | 0.043107 | 0.97897 | age_years | infant mortality (k<1)
69190 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.034381 | 0.0027511 | 4 | THERMAL_AUX | 0.96019 | 0.031937 | 9.7549 | 0.043107 | 0.055528 | age_years | infant mortality (k<1)
69191 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.034381 | 0.0027511 | 8 | THERMAL_AUX | 0.96019 | 0.031937 | 9.7549 | 0.043107 | 0.11106 | age_years | infant mortality (k<1)
69210 | 0 | 12 | 1.5-2.5h | LIB | CS | PGE | 2024 | 1 | 1 | 2 | Y | N | industrial | other | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0.0012482 | 0.0001 | 6.5 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0.00328 | age_years | infant mortality (k<1)
69244 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 58.3 | 114 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.11209 | 0.013453 | 2411.5 | THERMAL_AUX | 0.96019 | 0.13862 | 9.7549 | 0.043107 | 163.7074 | age_years | infant mortality (k<1)
69250 | 0 | 8 | <1.5h | NAB | CS | FPC | 2025 | 0 | 5 | 5 | N | Y | inland | other | other | CS | 2024+ | 0 | 1 | 0.0054568 | dur_band+climate_region | 0.043487 | 0.0052195 | 424 | THERMAL_AUX | 0.96019 | 0.058871 | 9.7549 | 0.043107 | 11.1672 | age_years | infant mortality (k<1)
69288 | 0 | 10 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.3 | 0.6 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.002849 | ba_g+dur_band+vintage_g | 0.028816 | 0.0027669 | 7.5 | THERMAL_AUX | 0.96019 | 0.032115 | 9.7549 | 0.043107 | 0.10472 | age_years | infant mortality (k<1)
69298 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 300 | 680 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.015535 | 0.014916 | 23114 | THERMAL_AUX | 0.96019 | 0.15137 | 9.7549 | 0.043107 | 1739.7481 | age_years | infant mortality (k<1)
69300 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 0 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
69301 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 20 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 0.1435 | age_years | infant mortality (k<1)
69302 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 88 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 0.6314 | age_years | infant mortality (k<1)
69331 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 8 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 0.0574 | age_years | infant mortality (k<1)
69333 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 20 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 0.1435 | age_years | infant mortality (k<1)
69334 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 2.3 | 4.5 | N | N | inland | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.0089686 | ba_g+dur_band+vintage_g | 0.10079 | 0.0080647 | 18 | THERMAL_AUX | 0.96019 | 0.088081 | 9.7549 | 0.043107 | 0.73251 | age_years | infant mortality (k<1)
69344 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.014743 | 0.0014156 | 2 | THERMAL_AUX | 0.96019 | 0.016698 | 9.7549 | 0.043107 | 0.014286 | age_years | infant mortality (k<1)
69345 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.0088982 | 0.001424 | 189.5 | THERMAL_AUX | 0.96019 | 0.016795 | 9.7549 | 0.043107 | 1.3617 | age_years | infant mortality (k<1)
69346 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 187 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 1.3417 | age_years | infant mortality (k<1)
69347 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.0088982 | 0.001424 | 221.5 | THERMAL_AUX | 0.96019 | 0.016795 | 9.7549 | 0.043107 | 1.5916 | age_years | infant mortality (k<1)
69348 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.016193 | 0.0014135 | 47 | THERMAL_AUX | 0.96019 | 0.016674 | 9.7549 | 0.043107 | 0.33524 | age_years | infant mortality (k<1)
69349 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.0014368 | ba_g+dur_band+vintage_g | 0.016193 | 0.0014135 | 39 | THERMAL_AUX | 0.96019 | 0.016674 | 9.7549 | 0.043107 | 0.27818 | age_years | infant mortality (k<1)
69350 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 23.2 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.14415 | 0.011534 | 368.5 | THERMAL_AUX | 0.96019 | 0.12129 | 9.7549 | 0.043107 | 21.4479 | age_years | infant mortality (k<1)
69353 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 19.8 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.013477 | ba_g+dur_band+vintage_g | 0.14415 | 0.011534 | 109.5 | THERMAL_AUX | 0.96019 | 0.12129 | 9.7549 | 0.043107 | 6.3733 | age_years | infant mortality (k<1)
69358 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 11.3 | 11.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0.00031234 | 0.0001 | 0 | THERMAL_AUX | 0.96019 | 0.0011985 | 9.7549 | 0.043107 | 0 | age_years | infant mortality (k<1)
69365 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.004469 | 0.0014304 | 206 | THERMAL_AUX | 0.96019 | 0.016869 | 9.7549 | 0.043107 | 1.4869 | age_years | infant mortality (k<1)
69366 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.017639 | 0.0014114 | 122 | THERMAL_AUX | 0.96019 | 0.016649 | 9.7549 | 0.043107 | 0.86891 | age_years | infant mortality (k<1)
69407 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 75 | 75 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.010366 | 0.0014219 | 2149 | THERMAL_AUX | 0.96019 | 0.016771 | 9.7549 | 0.043107 | 15.419 | age_years | infant mortality (k<1)
69411 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0.10079 | 0.0080647 | 300 | THERMAL_AUX | 0.96019 | 0.088081 | 9.7549 | 0.043107 | 12.2085 | age_years | infant mortality (k<1)
69413 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0.10079 | 0.0080647 | 391 | THERMAL_AUX | 0.96019 | 0.088081 | 9.7549 | 0.043107 | 15.9118 | age_years | infant mortality (k<1)
69414 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 180 | 360 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.015535 | 0.014916 | 3630 | THERMAL_AUX | 0.96019 | 0.15137 | 9.7549 | 0.043107 | 273.2234 | age_years | infant mortality (k<1)
69415 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0089686 | ba_g+dur_band+vintage_g | 0.10079 | 0.0080647 | 437 | THERMAL_AUX | 0.96019 | 0.088081 | 9.7549 | 0.043107 | 17.7837 | age_years | infant mortality (k<1)
69454 | 0 | 9 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.12436 | 0.013267 | 561 | THERMAL_AUX | 0.96019 | 0.13697 | 9.7549 | 0.043107 | 37.5579 | age_years | infant mortality (k<1)
69456 | 0 | 8 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.11209 | 0.013453 | 418 | THERMAL_AUX | 0.96019 | 0.13862 | 9.7549 | 0.043107 | 28.3764 | age_years | infant mortality (k<1)
69459 | 0 | 5 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.073128 | 0.014044 | 369 | THERMAL_AUX | 0.96019 | 0.14381 | 9.7549 | 0.043107 | 26.1491 | age_years | infant mortality (k<1)
69460 | 0 | 12 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.015152 | ba_g+dur_band+vintage_g | 0.15921 | 0.012739 | 478 | THERMAL_AUX | 0.96019 | 0.13225 | 9.7549 | 0.043107 | 30.7275 | age_years | infant mortality (k<1)
69576 | 0 | 8 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 13.7 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.0014368 | ba_g+dur_band+vintage_g | 0.011829 | 0.0014198 | 215 | THERMAL_AUX | 0.96019 | 0.016746 | 9.7549 | 0.043107 | 1.5403 | age_years | infant mortality (k<1)
69727 | 0 | 12 | <1.5h | LIB | CS | PJM | 2022 | 1 | 10.1 | 10.1 | N | Y | inland | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.0092593 | ba_g+dur_band+vintage_g | 0.10372 | 0.0082989 | 98 | THERMAL_AUX | 0.96019 | 0.090404 | 9.7549 | 0.043107 | 4.104 | age_years | infant mortality (k<1)
69803 | 0 | 7 | <1.5h | LIB | CT | NYIS | 2025 | 0 | 4.6 | 4.6 | N | N | coastal | NYIS | LIB | CT | 2024+ | 0 | 0 | 0.002069 | dur_band+climate_region | 0.014859 | 0.0020382 | 126 | THERMAL_AUX | 0.96019 | 0.023863 | 9.7549 | 0.043107 | 1.2959 | age_years | infant mortality (k<1)
141 | 0 | 52 | 2.5-4.5h | LIB | CS | SRP | 2021 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1432 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.18332 | age_years | infant mortality (k<1)
260 | 0 | 55 | 2.5-4.5h | LIB | BL | CISO | 2021.9333 | 1 | 750 | 3000 | Y | N | coastal | CISO | LIB | BL | 2022-23 | 1 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 0 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
389 | 5 | 84 | <1.5h | LIB | BL | IID | 2016 | 0 | 30 | 20 | N | Y | arid | other | LIB | BL | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 379.5 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 5.7773 | age_years | infant mortality (k<1)
645 | 0 | 33 | 1.5-2.5h | LIB | CS | TEC | 2017 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00064008 | age_years | infant mortality (k<1)
1016 | 0 | 48 | <1.5h | LIB | CS | CPLE | 2019 | 1 | 0.5 | 0.5 | N | N | inland | CPLE | LIB | CS | <=2019 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 20.5 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0.5569 | age_years | infant mortality (k<1)
1482 | 0 | 33 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 585 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 4.9926 | age_years | infant mortality (k<1)
1507 | 5 | 84 | <1.5h | LIB | CS | ISNE | 2016 | 0 | 16.7 | 10.9 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.026316 | ba_g+dur_band+vintage_g | 0 | 0.026316 | 288 | UNATTRIBUTED | inf | 0.27079 | 5.4106 | 0.019717 | 9.7023 | age_years | infant mortality (k<1)
1615 | 2 | 36 | >4.5h | LIB | BL | ISNE | 2019 | 0 | 6 | 48 | N | N | coastal | ISNE | LIB | BL | <=2019 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 1 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.012414 | age_years | infant mortality (k<1)
1682 | 3 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 3 | 6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 27.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.075981 | age_years | infant mortality (k<1)
2324 | 3 | 23 | <1.5h | LIB | CS | NEVP | 2023 | 0 | 220 | 220 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 13845.5 | UNATTRIBUTED | inf | 0.20148 | 5.4106 | 0.019717 | 332.3336 | age_years | infant mortality (k<1)
2830 | 0 | 84 | <1.5h | LIB | CS | PJM | 2015 | 1 | 4 | 1.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 91.5 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 1.3195 | age_years | infant mortality (k<1)
6304 | 0 | 36 | <1.5h | LIB | CT |  | 2015 | 1 | 1.2 | 1 | N | N | coastal | other | LIB | CT | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 4 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0.060894 | age_years | infant mortality (k<1)
6377 | 0 | 36 | <1.5h | LIB | CS | PJM | 2017 | 1 | 1 | 1 | Y | N | coastal | PJM | LIB | CS | <=2019 | 1 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 3 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 0.043264 | age_years | infant mortality (k<1)
8063 | 2 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 269.1 | 263 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 2501.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 165.5389 | age_years | infant mortality (k<1)
10156 | 0 | 34 | <1.5h | LIB | CS | CISO | 2023 | 0 | 16 | 16 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 13.5 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 0.053505 | age_years | infant mortality (k<1)
10444 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 69 | 69 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 4203 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 236.7426 | age_years | infant mortality (k<1)
10493 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 8 | 16 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 613.5 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 5.2359 | age_years | infant mortality (k<1)
50064 | 0 | 24 | <1.5h | LIB | CS | CISO | 2022 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 12 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 0.04756 | age_years | infant mortality (k<1)
50300 | 9 | 84 | <1.5h | LIB | BL | CISO | 2019.5 | 0 | 40 | 40 | N | Y | inland | CISO | LIB | BL | <=2019 | 0 | 1 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 1235.5 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 33.5635 | age_years | infant mortality (k<1)
54134 | 8 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 0 | 20 | 20 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 729.5 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 38.9115 | age_years | infant mortality (k<1)
54296 | 0 | 76 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.3 | 0.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 1 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 0.017183 | age_years | infant mortality (k<1)
54639 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 14 | 14 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 751.5 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 3.2392 | age_years | infant mortality (k<1)
55370 | 1 | 36 | <1.5h | LIB | CT | PJM | 2016 | 0 | 10.4 | 10.4 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
56961 | 10 | 84 | <1.5h | LIB | BL | ERCO | 2012 | 0 | 36 | 13.6 | N | N | arid | ERCO | LIB | BL | <=2019 | 0 | 0 | 0.038835 | ba_g+dur_band+vintage_g | 0 | 0.038835 | 227.5 | UNATTRIBUTED | inf | 0.3725 | 5.4106 | 0.019717 | 11.3102 | age_years | infant mortality (k<1)
56981 | 0 | 84 | <1.5h | LIB | CS | ERCO | 2018 | 1 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.038835 | ba_g+dur_band+vintage_g | 0 | 0.038835 | 43.5 | UNATTRIBUTED | inf | 0.3725 | 5.4106 | 0.019717 | 2.1626 | age_years | infant mortality (k<1)
56984 | 1 | 36 | <1.5h | LIB | CS | ERCO | 2018 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.038835 | ba_g+dur_band+vintage_g | 0 | 0.038835 | 68 | UNATTRIBUTED | inf | 0.3725 | 5.4106 | 0.019717 | 3.3806 | age_years | infant mortality (k<1)
57206 | 0 | 36 | 1.5-2.5h | LIB | CS |  | 2022 | 0 | 46.5 | 93 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.017143 | ba_g+dur_band+vintage_g | 0 | 0.017143 | 268.5 | UNATTRIBUTED | inf | 0.18593 | 5.4106 | 0.019717 | 5.8924 | age_years | infant mortality (k<1)
57242 | 0 | 30 | 2.5-4.5h | LIB | CS |  | 2022 | 1 | 39 | 156 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 3159 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 30.2357 | age_years | infant mortality (k<1)
57325 | 0 | 84 | <1.5h | LIB | CS | PJM | 2014 | 1 | 20 | 8.3 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 446 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 6.4319 | age_years | infant mortality (k<1)
57447 | 2 | 78 | <1.5h | LIB | CS | PJM | 2011 | 0 | 16 | 16 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 628.5 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 9.0637 | age_years | infant mortality (k<1)
57560 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 19 | 76 | Y | N | arid | AZPS | LIB | CS | 2024+ | 1 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 1891 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 61.5453 | age_years | infant mortality (k<1)
57561 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1278.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.16367 | age_years | infant mortality (k<1)
57562 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 17 | 51 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1289 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.16501 | age_years | infant mortality (k<1)
57563 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 16 | 48 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1141 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.14607 | age_years | infant mortality (k<1)
57583 | 0 | 84 | <1.5h | NIB | BL |  | 2003 | 0 | 40 | 11 | N | Y | inland | other | other | BL | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 17 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0.2588 | age_years | infant mortality (k<1)
57584 | 4 | 78 | 1.5-2.5h | LIB | CS | CISO | 2015 | 0 | 2.5 | 5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 13.5 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 0.23198 | age_years | infant mortality (k<1)
57996 | 3 | 36 | <1.5h | LIB | CS |  | 2012 | 0 | 11 | 4.4 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 106.5 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 1.6213 | age_years | infant mortality (k<1)
57997 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 35 | 105 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2396 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.30673 | age_years | infant mortality (k<1)
58236 | 0 | 62 | 1.5-2.5h | LIB | CS | MISO | 2020 | 1 | 0.3 | 0.6 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
58256 | 0 | 41 | >4.5h | NAB | CS | PNM | 2012 | 1 | 1.8 | 8.3 | N | N | inland | other | other | CS | <=2019 | 0 | 0 | 0.012931 | dur_band+climate_region | 0 | 0.012931 |  | UNATTRIBUTED | inf | 0.14373 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
58383 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 14 | 42 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1015.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.13 | age_years | infant mortality (k<1)
58405 | 0 | 36 | <1.5h | LIB | CS |  | 2012 | 1 | 3 | 3 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 0.5 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0.0076118 | age_years | infant mortality (k<1)
58462 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 230 | 920 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 23132.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 727.3445 | age_years | infant mortality (k<1)
58585 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2017 | 1 | 0.5 | 1 | N | N | industrial | CISO | LIB | CS | <=2019 | 0 | 0 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 2 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 0.034367 | age_years | infant mortality (k<1)
58639 | 0 | 48 | <1.5h | LIB | CS |  | 2015 | 1 | 6 | 4.6 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 |  | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
59020 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 32 | 96 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2334.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.29885 | age_years | infant mortality (k<1)
59118 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 16.4 | 32.8 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 548.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 37.2362 | age_years | infant mortality (k<1)
59150 | 0 | 36 | <1.5h | LIB | CS | CISO | 2021 | 1 | 75 | 75 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 7373 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 23.5966 | age_years | infant mortality (k<1)
59256 | 2 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 2 | 14 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 |  | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
59257 | 1 | 31 | >4.5h | NAB | CS | CISO | 2013 | 0 | 4 | 28 | Y | Y | inland | CISO | other | CS | <=2019 | 1 | 1 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 |  | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
59444 | 0 | 24 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 10 | 30 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 840.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.1076 | age_years | infant mortality (k<1)
59871 | 0 | 13 | <1.5h | LIB | CS | CISO | 2024 | 1 | 150 | 150 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 12527 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 705.6091 | age_years | infant mortality (k<1)
59939 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021.4861 | 1 | 72 | 288 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 6176.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 194.2048 | age_years | infant mortality (k<1)
59949 | 2 | 70 | <1.5h | LIB | BL | PJM | 2015 | 0 | 11 | 5 | N | N | inland | PJM | LIB | BL | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
59957 | 0 | 84 | <1.5h | LIB | CT | PJM | 2014.75 | 1 | 36 | 13.5 | Y | Y | inland | PJM | LIB | CT | <=2019 | 1 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
59959 | 2 | 34 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
59960 | 0 | 30 | <1.5h | LIB | CS | PJM | 2015 | 0 | 19.8 | 7.9 | N | Y | inland | PJM | LIB | CS | <=2019 | 0 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
59993 | 0 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 10 | 40 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 13 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0016642 | age_years | infant mortality (k<1)
60014 | 0 | 48 | 1.5-2.5h | LIB | CS | FPL | 2021 | 1 | 409 | 900 | N | Y | coastal | other | LIB | CS | 2020-21 | 0 | 1 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 6521 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 61.8365 | age_years | infant mortality (k<1)
60016 | 1 | 74 | <1.5h | LIB | CS | BPAT | 2015.5 | 0 | 2 | 1 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 0 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60061 | 0 | 84 | 2.5-4.5h | LIB | CS | FPL | 2018 | 1 | 4 | 16 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 110.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.014146 | age_years | infant mortality (k<1)
60092 | 0 | 57 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 12058.5 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 174.0994 | age_years | infant mortality (k<1)
60093 | 0 | 36 | >4.5h | LIB | CS | CISO | 2021 | 1 | 63 | 301.2 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 7022 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 101.3829 | age_years | infant mortality (k<1)
60094 | 0 | 51 | >4.5h | LIB | CS | CISO | 2021 | 1 | 115 | 538.6 | Y | N | arid | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 11924 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 172.1575 | age_years | infant mortality (k<1)
60095 | 0 | 36 | <1.5h | LIB | CS | CISO | 2022 | 1 | 47 | 47 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 4070 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 16.1308 | age_years | infant mortality (k<1)
60123 | 0 | 76 | 2.5-4.5h | LIB | CS | ERCO | 2019 | 1 | 9.9 | 42 | N | Y | arid | ERCO | LIB | CS | <=2019 | 0 | 1 | 0.014363 | dur_band+climate_region | 0 | 0.014363 | 29.5 | UNATTRIBUTED | inf | 0.15832 | 5.4106 | 0.019717 | 0.54242 | age_years | infant mortality (k<1)
60231 | 0 | 36 | <1.5h | LIB | CS | CISO | 2016 | 1 | 2 | 2 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.029655 | dur_band+climate_region | 0 | 0.029655 | 25 | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 | 0.94908 | age_years | infant mortality (k<1)
60233 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 88 | 352 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 8494.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 267.0886 | age_years | infant mortality (k<1)
60249 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2020 | 0 | 1 | 2 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 0 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60297 | 0 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 10 | 4.1 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 75.5 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 1.0888 | age_years | infant mortality (k<1)
60299 | 0 | 24 | <1.5h | LIB | CS | PJM | 2016 | 1 | 7 | 7 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 |  | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
60316 | 0 | 24 | <1.5h | LIB | CS | PJM | 2022 | 1 | 40 | 48 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 308 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.039429 | age_years | infant mortality (k<1)
60390 | 0 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 31.5 | 12.5 | N | Y | inland | PJM | LIB | CT | <=2019 | 0 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60441 | 0 | 67 | <1.5h | LIB | BL | PGE | 2013 | 1 | 5 | 5 | N | N | inland | other | LIB | BL | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 |  | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
60444 | 0 | 36 | 1.5-2.5h | LIB | CT | PSEI | 2016 | 0 | 2 | 4.4 | Y | Y | inland | other | LIB | CT | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60467 | 0 | 14 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 41 | 164 | Y | N | arid | AZPS | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3200.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.40972 | age_years | infant mortality (k<1)
60491 | 0 | 64 | <1.5h | LIB | CT | LDWP | 2019 | 1 | 1.5 | 1.5 | N | Y | arid | other | LIB | CT | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 0 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60506 | 0 | 48 | <1.5h | NAB | BL | ERCO | 2010 | 1 | 4 | 4 | N | N | arid | ERCO | other | BL | <=2019 | 0 | 0 | 0.038835 | ba_g+dur_band+vintage_g | 0 | 0.038835 |  | UNATTRIBUTED | inf | 0.3725 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
60518 | 0 | 72 | 1.5-2.5h | LIB | CS | ISNE | 2015 | 1 | 2 | 3.4 | N | Y | inland | ISNE | LIB | CS | <=2019 | 0 | 1 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 0 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60546 | 0 | 36 | 2.5-4.5h | LIB | CS |  | 2017 | 1 | 13 | 52 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1150.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.14728 | age_years | infant mortality (k<1)
60562 | 0 | 71 | 2.5-4.5h | LIB | OT | ISNE | 2018 | 1 | 1 | 4 | N | Y | inland | ISNE | LIB | other | <=2019 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 52.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0067208 | age_years | infant mortality (k<1)
60565 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2013.3333 | 1 | 1.5 | 4.5 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 0 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60566 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2015 | 1 | 1 | 2 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 1082.5 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 18.601 | age_years | infant mortality (k<1)
60567 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2015 | 1 | 2 | 6 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 0 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60568 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2014 | 1 | 1 | 3 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 0 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60569 | 5 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 7.5 | 30 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 405 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 11.5214 | age_years | infant mortality (k<1)
60570 | 2 | 84 | 2.5-4.5h | LIB | CS | CISO | 2017 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 0 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60607 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2017 | 1 | 0.8 | 3.3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00044806 | age_years | infant mortality (k<1)
60609 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2016 | 1 | 0.8 | 3 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60641 | 2 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 10 | 40 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 758.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 23.8492 | age_years | infant mortality (k<1)
60649 | 1 | 36 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 165.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 1.6099 | age_years | infant mortality (k<1)
60654 | 0 | 48 | 2.5-4.5h | LIB | CS | WALC | 2021 | 1 | 90 | 360 | Y | Y | arid | other | LIB | CS | 2020-21 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 7749.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.99206 | age_years | infant mortality (k<1)
60656 | 0 | 36 | <1.5h | LIB | CS | PJM | 2016 | 0 | 20 | 7.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 2935 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 42.3263 | age_years | infant mortality (k<1)
60660 | 1 | 33 | <1.5h | LIB | CS | PJM | 2016 | 0 | 6 | 2 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 593 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 8.5518 | age_years | infant mortality (k<1)
60661 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2016 | 0 | 20 | 80 | Y | Y | arid | CISO | LIB | CS | <=2019 | 1 | 1 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 1040.5 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 29.6002 | age_years | infant mortality (k<1)
60690 | 3 | 84 | <1.5h | LIB | CS | ERCO | 2017 | 0 | 30 | 12.6 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.038835 | ba_g+dur_band+vintage_g | 0 | 0.038835 | 463.5 | UNATTRIBUTED | inf | 0.3725 | 5.4106 | 0.019717 | 23.0429 | age_years | infant mortality (k<1)
60698 | 0 | 65 | <1.5h | LIB | CS | CISO | 2020 | 1 | 20 | 9 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 14 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 0.044806 | age_years | infant mortality (k<1)
60760 | 1 | 24 | 2.5-4.5h | LIB | BL | CISO | 2016 | 0 | 2 | 8 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 |  | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
60815 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2017 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.026316 | ba_g+dur_band+vintage_g | 0 | 0.026316 | 6.5 | UNATTRIBUTED | inf | 0.27079 | 5.4106 | 0.019717 | 0.21897 | age_years | infant mortality (k<1)
60906 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.1 | 6.1 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 23 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0.65141 | age_years | infant mortality (k<1)
60959 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2017 | 1 | 2 | 3.9 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 7 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0.19825 | age_years | infant mortality (k<1)
60974 | 0 | 36 | <1.5h | LIB | CS | LDWP | 2017 | 1 | 2 | 1 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 0 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
60996 | 0 | 36 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 2.5 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 74 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 1.1265 | age_years | infant mortality (k<1)
61068 | 0 | 72 | >4.5h | LIB | CS |  | 2018 | 1 | 20 | 100 | N | Y | coastal | other | LIB | CS | <=2019 | 0 | 1 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 1857 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 23.0522 | age_years | infant mortality (k<1)
61098 | 0 | 55 | <1.5h | LIB | CS | NEVP | 2021 | 1 | 25 | 25 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 2105 | UNATTRIBUTED | inf | 0.10609 | 5.4106 | 0.019717 | 25.1845 | age_years | infant mortality (k<1)
61107 | 0 | 36 | 2.5-4.5h | FLB | CS | CISO | 2017 | 1 | 2 | 8 | N | Y | coastal | CISO | other | CS | <=2019 | 0 | 1 | 0.022222 | ba_g+dur_band+vintage_g | 0 | 0.022222 | 106 | UNATTRIBUTED | inf | 0.23407 | 5.4106 | 0.019717 | 3.0155 | age_years | infant mortality (k<1)
61168 | 0 | 14 | 2.5-4.5h | LIB | CS | LDWP | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 14026 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 571.0239 | age_years | infant mortality (k<1)
61169 | 0 | 6 | 2.5-4.5h | LIB | CS | LDWP | 2025 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 13805 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 562.0266 | age_years | infant mortality (k<1)
61186 | 1 | 32 | <1.5h | LIB | CS | ISNE | 2023 | 0 | 1 | 1.1 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 2 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.0086206 | age_years | infant mortality (k<1)
61197 | 0 | 84 | <1.5h | LIB | CS | TEPC | 2017 | 1 | 10 | 10 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 6 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0.091341 | age_years | infant mortality (k<1)
61204 | 3 | 60 | 2.5-4.5h | LIB | BL | CISO | 2021 | 0 | 100 | 400 | Y | N | coastal | CISO | LIB | BL | 2020-21 | 1 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 7946.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 249.8581 | age_years | infant mortality (k<1)
61334 | 0 | 36 | >4.5h | LIB | CT | MISO | 2019 | 1 | 1 | 4.6 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.012931 | dur_band+climate_region | 0 | 0.012931 | 0 | UNATTRIBUTED | inf | 0.14373 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61365 | 1 | 31 | <1.5h | LIB | CS | CISO | 2023 | 0 | 40 | 40 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 3338 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 13.2296 | age_years | infant mortality (k<1)
61366 | 4 | 54 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 30 | 120 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 2929.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 92.1109 | age_years | infant mortality (k<1)
61431 | 0 | 84 | <1.5h | LIB | CS | LDWP | 2018 | 1 | 20 | 10 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 337 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 5.1303 | age_years | infant mortality (k<1)
61439 | 0 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2017 | 1 | 1 | 2.2 | Y | Y | arid | other | LIB | CS | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61473 | 0 | 36 | <1.5h | LIB | BL | PJM | 2015 | 1 | 1 | 1 | Y | Y | inland | PJM | LIB | BL | <=2019 | 1 | 1 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61552 | 0 | 22 | <1.5h | LIB | CS | PJM | 2024 | 1 | 6 | 6 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 455 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 12.3605 | age_years | infant mortality (k<1)
61661 | 13 | 84 | <1.5h | LIB | BL | CISO | 2018 | 0 | 40 | 38 | N | Y | coastal | CISO | LIB | BL | <=2019 | 0 | 1 | 0.029655 | dur_band+climate_region | 0 | 0.029655 | 1280.5 | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 | 48.6121 | age_years | infant mortality (k<1)
61667 | 0 | 9 | 1.5-2.5h | LIB | CS | TEC | 2025 | 1 | 40 | 80 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 447 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 11.9215 | age_years | infant mortality (k<1)
61678 | 0 | 84 | 2.5-4.5h | LIB | CS | SRP | 2018 | 1 | 10 | 40 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1032 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.13211 | age_years | infant mortality (k<1)
61721 | 0 | 72 | >4.5h | LIB | CS | CISO | 2019 | 1 | 1 | 6.9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 16.5 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 0.25027 | age_years | infant mortality (k<1)
61722 | 1 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.5 | 33.5 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 455 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 6.9013 | age_years | infant mortality (k<1)
61723 | 1 | 36 | >4.5h | LIB | CS | CISO | 2018 | 0 | 5.8 | 34.8 | N | N | coastal | CISO | LIB | CS | <=2019 | 0 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 378 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 5.7334 | age_years | infant mortality (k<1)
61730 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 1 | 1 | 2 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 19.5 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0.55228 | age_years | infant mortality (k<1)
61737 | 0 | 12 | <1.5h | LIB | CS | PJM | 2021 | 1 | 6.2 | 6.2 | N | Y | coastal | PJM | LIB | CS | 2020-21 | 0 | 1 | 0.029655 | dur_band+climate_region | 0 | 0.029655 |  | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
61739 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2017 | 0 | 1 | 1.3 | Y | N | industrial | NYIS | LIB | CS | <=2019 | 1 | 0 | 0.024896 | dur_band | 0 | 0.024896 | 0 | UNATTRIBUTED | inf | 0.25826 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61741 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2018 | 1 | 1.5 | 3 | N | N | inland | ERCO | LIB | CS | <=2019 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61763 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 647.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.08289 | age_years | infant mortality (k<1)
61795 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2020 | 1 | 1 | 2 | Y | N | industrial | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 2.5 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 0.040341 | age_years | infant mortality (k<1)
61801 | 2 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 2194.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 103.4356 | age_years | infant mortality (k<1)
61803 | 1 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 10 | 40 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 705 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 33.2295 | age_years | infant mortality (k<1)
61861 | 0 | 84 | 2.5-4.5h | LIB | BL | SRP | 2019 | 1 | 10 | 40 | N | N | arid | other | LIB | BL | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61891 | 2 | 83 | <1.5h | LIB | CS | PJM | 2018 | 0 | 19.8 | 19.8 | Y | N | inland | PJM | LIB | CS | <=2019 | 1 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 2740 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 39.5141 | age_years | infant mortality (k<1)
61892 | 1 | 83 | <1.5h | LIB | CS | PJM | 2019 | 0 | 19.8 | 19.8 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 2919 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 42.0955 | age_years | infant mortality (k<1)
61901 | 0 | 36 | 1.5-2.5h | LIB | CS | TVA | 2017 | 1 | 1 | 2 | Y | N | inland | other | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61909 | 1 | 36 | <1.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 1 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 0 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61923 | 2 | 36 | <1.5h | LIB | CS | PJM | 2018 | 0 | 1 | 1 | N | N | coastal | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 127 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 1.8315 | age_years | infant mortality (k<1)
61925 | 0 | 84 | <1.5h | LIB | CS | PNM | 2018 | 0 | 1 | 1 | N | Y | arid | other | LIB | CS | <=2019 | 0 | 1 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 4.5 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0.068506 | age_years | infant mortality (k<1)
61956 | 0 | 36 | 1.5-2.5h | LIB | CS | SCEG | 2018 | 1 | 4 | 8 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 23 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0029444 | age_years | infant mortality (k<1)
61990 | 0 | 36 | 1.5-2.5h | LIB | CT | MISO | 2017 | 1 | 0.3 | 0.5 | N | N | inland | MISO | LIB | CT | <=2019 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
61995 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2018 | 1 | 0.5 | 0.9 | N | N | arid | CISO | LIB | CS | <=2019 | 0 | 0 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 0 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62027 | 0 | 36 | 1.5-2.5h | OTH | CS | PJM | 2016 | 1 | 1 | 2 | Y | Y | coastal | PJM | other | CS | <=2019 | 1 | 1 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 0 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62147 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2019 | 0 | 20 | 8.4 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 2179 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 59.1945 | age_years | infant mortality (k<1)
62175 | 3 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 200 | 800 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 17609 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 442.3839 | age_years | infant mortality (k<1)
62219 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 1 | 3 | 3 | N | N | inland | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.026316 | ba_g+dur_band+vintage_g | 0 | 0.026316 | 19.5 | UNATTRIBUTED | inf | 0.27079 | 5.4106 | 0.019717 | 0.65692 | age_years | infant mortality (k<1)
62235 | 0 | 13 | 2.5-4.5h | LIB | CS | SCEG | 2024 | 1 | 66 | 198 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 1632.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 66.462 | age_years | infant mortality (k<1)
62248 | 0 | 25 | >4.5h | LIB | CS | NEVP | 2023 | 1 | 75 | 375 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 8731 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 126.0573 | age_years | infant mortality (k<1)
62257 | 4 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2018 | 0 | 2 | 4.2 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 26.5 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0.75054 | age_years | infant mortality (k<1)
62373 | 0 | 84 | 2.5-4.5h | LIB | CS | WACM | 2018 | 0 | 4 | 16 | N | N | arid | other | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62381 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 94 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.012034 | age_years | infant mortality (k<1)
62382 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 92 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.011777 | age_years | infant mortality (k<1)
62383 | 0 | 72 | 2.5-4.5h | LIB | OT | ISNE | 2019 | 1 | 2 | 8 | Y | Y | inland | ISNE | LIB | other | <=2019 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 105.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.013506 | age_years | infant mortality (k<1)
62441 | 0 | 24 | <1.5h | LIB | CS | CISO | 2020 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 48.5 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 0.15522 | age_years | infant mortality (k<1)
62444 | 0 | 84 | <1.5h | LIB | CT | PJM | 2015 | 1 | 18 | 12.1 | N | N | inland | PJM | LIB | CT | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 1974 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 28.4675 | age_years | infant mortality (k<1)
62490 | 0 | 46 | 2.5-4.5h | LIB | CS | FPL | 2021 | 1 | 30 | 75 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 558 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.071433 | age_years | infant mortality (k<1)
62494 | 0 | 2 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 1 | 252 | 1008 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 8863.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 360.8492 | age_years | infant mortality (k<1)
62497 | 2 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 9 | 36 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 0 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62499 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 6 | 24 | Y | Y | coastal | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 0 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62541 | 0 | 34 | 1.5-2.5h | LIB | CS | FPC | 2023 | 1 | 17.3 | 36 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.017143 | ba_g+dur_band+vintage_g | 0 | 0.017143 | 160 | UNATTRIBUTED | inf | 0.18593 | 5.4106 | 0.019717 | 3.5113 | age_years | infant mortality (k<1)
62561 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 63.3 | 108.6 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 0 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62562 | 1 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 63.3 | 81 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 0 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62564 | 4 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 182.5 | 730 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 0 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62569 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2018 | 0 | 1.1 | 4 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62585 | 1 | 36 | <1.5h | LIB | CT | ISNE | 2019 | 0 | 3 | 3 | N | N | coastal | ISNE | LIB | CT | <=2019 | 0 | 0 | 0.026316 | ba_g+dur_band+vintage_g | 0 | 0.026316 | 16.5 | UNATTRIBUTED | inf | 0.27079 | 5.4106 | 0.019717 | 0.55586 | age_years | infant mortality (k<1)
62604 | 0 | 41 | 1.5-2.5h | LIB | BL | ISNE | 2022 | 0 | 25 | 38 | N | N | coastal | ISNE | LIB | BL | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 64.5 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.55047 | age_years | infant mortality (k<1)
62609 | 2 | 76 | <1.5h | LIB | CS | ERCO | 2019 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | <=2019 | 1 | 1 | 0.038835 | ba_g+dur_band+vintage_g | 0 | 0.038835 | 156.5 | UNATTRIBUTED | inf | 0.3725 | 5.4106 | 0.019717 | 7.7804 | age_years | infant mortality (k<1)
62644 | 4 | 80 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 5 | 10 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 42.5 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 1.2037 | age_years | infant mortality (k<1)
62652 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3.3 | 6.6 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 98.5 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 2.7897 | age_years | infant mortality (k<1)
62682 | 0 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62683 | 0 | 77 | 1.5-2.5h | LIB | BL | SWPP | 2019 | 1 | 6 | 13.1 | N | N | industrial | other | LIB | BL | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62695 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 19 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.052496 | age_years | infant mortality (k<1)
62714 | 2 | 36 | <1.5h | LIB | CS |  | 2019 | 0 | 1 | 0.9 | N | N | coastal | other | LIB | CS | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 11 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0.16746 | age_years | infant mortality (k<1)
62733 | 0 | 36 | >4.5h | LIB | BL | NYIS | 2018 | 0 | 5 | 40 | Y | N | coastal | NYIS | LIB | BL | <=2019 | 1 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 25 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.31034 | age_years | infant mortality (k<1)
62734 | 3 | 36 | >4.5h | LIB | BL | NYIS | 2019 | 0 | 5 | 40 | N | N | coastal | NYIS | LIB | BL | <=2019 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 0 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62745 | 0 | 45 | 2.5-4.5h | LIB | CS | BPAT | 2022 | 1 | 30 | 120 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 1836 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 17.5729 | age_years | infant mortality (k<1)
62753 | 0 | 72 | <1.5h | LIB | CS | ERCO | 2020 | 1 | 9.9 | 10 | Y | Y | inland | ERCO | LIB | CS | 2020-21 | 1 | 1 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 14 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 0.13619 | age_years | infant mortality (k<1)
62754 | 1 | 20 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 2 | 4 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 0 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62801 | 0 | 24 | <1.5h | LIB | CS | CISO | 2021 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 908 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 2.906 | age_years | infant mortality (k<1)
62835 | 2 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 1.5 | 3 | N | Y | coastal | ISNE | LIB | CS | <=2019 | 0 | 1 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 6 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0.16993 | age_years | infant mortality (k<1)
62839 | 0 | 36 | >4.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 10 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 0 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62844 | 0 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 150 | 300 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 6721.5 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 149.6846 | age_years | infant mortality (k<1)
62856 | 0 | 83 | <1.5h | LIB | CS | PJM | 2018 | 1 | 20 | 20 | N | N | inland | PJM | LIB | CS | <=2019 | 0 | 0 | 0.011265 | ba_g+dur_band+vintage_g | 0 | 0.011265 | 0 | UNATTRIBUTED | inf | 0.12644 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
62862 | 2 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 74 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 2.0103 | age_years | infant mortality (k<1)
62874 | 3 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 2 | 6 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 83.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 2.6255 | age_years | infant mortality (k<1)
62875 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 3 | 12 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 86 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 2.7041 | age_years | infant mortality (k<1)
62889 | 1 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 20 | 80 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 1815.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 57.0839 | age_years | infant mortality (k<1)
62907 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2019 | 0 | 1.9 | 1.9 | N | N | inland | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.026316 | ba_g+dur_band+vintage_g | 0 | 0.026316 | 155 | UNATTRIBUTED | inf | 0.27079 | 5.4106 | 0.019717 | 5.2217 | age_years | infant mortality (k<1)
62908 | 3 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 0 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 9.5 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0.19144 | age_years | infant mortality (k<1)
62937 | 0 | 83 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 6 | 12 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 4 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0.080608 | age_years | infant mortality (k<1)
62964 | 0 | 16 | <1.5h | LIB | CS | AZPS | 2023 | 0 | 50 | 50 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0.030215 | dur_band+climate_region | 0 | 0.030215 | 4547.5 | UNATTRIBUTED | inf | 0.30412 | 5.4106 | 0.019717 | 175.8975 | age_years | infant mortality (k<1)
62968 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 4 | Y | N | coastal | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 53 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.45232 | age_years | infant mortality (k<1)
62969 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 74.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.20584 | age_years | infant mortality (k<1)
62970 | 0 | 24 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 64.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.17821 | age_years | infant mortality (k<1)
62971 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 2.9 | 6 | Y | N | inland | ISNE | other | CT | 2022-23 | 1 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 62.5 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.5334 | age_years | infant mortality (k<1)
62972 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2021 | 1 | 2 | 4.2 | Y | N | inland | ISNE | other | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 57 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.15749 | age_years | infant mortality (k<1)
62973 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 1.6 | 3.2 | Y | N | coastal | ISNE | other | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 36.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.10085 | age_years | infant mortality (k<1)
62974 | 0 | 12 | 1.5-2.5h | NIB | CT | ISNE | 2023 | 1 | 3.8 | 7.9 | Y | Y | inland | ISNE | other | CT | 2022-23 | 1 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 154 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 1.3143 | age_years | infant mortality (k<1)
62975 | 0 | 36 | 1.5-2.5h | NIB | CT | ISNE | 2020 | 1 | 3.9 | 7.9 | Y | Y | inland | ISNE | other | CT | 2020-21 | 1 | 1 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 114 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.31497 | age_years | infant mortality (k<1)
62976 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2020 | 1 | 2 | 4 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 16 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.044207 | age_years | infant mortality (k<1)
62977 | 0 | 12 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 4 | 8 | Y | N | inland | ISNE | LIB | CT | 2022-23 | 1 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 51.5 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.43952 | age_years | infant mortality (k<1)
62978 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3 | 6 | Y | N | inland | ISNE | LIB | CT | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 65 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.17959 | age_years | infant mortality (k<1)
62981 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2018 | 0 | 2 | 4.2 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 35.5 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0.71539 | age_years | infant mortality (k<1)
62999 | 0 | 36 | <1.5h | LIB | CT | NYIS | 2020 | 1 | 3 | 4.4 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 0 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63000 | 0 | 36 | 1.5-2.5h | LIB | CT | NYIS | 2020 | 1 | 4 | 8.8 | N | N | inland | NYIS | LIB | CT | 2020-21 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63011 | 0 | 36 | >4.5h | LIB | CT | ISNE | 2020 | 1 | 1.5 | 7.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.012931 | dur_band+climate_region | 0 | 0.012931 | 100.5 | UNATTRIBUTED | inf | 0.14373 | 5.4106 | 0.019717 | 1.6637 | age_years | infant mortality (k<1)
63022 | 0 | 36 | 1.5-2.5h | LIB | CS | WACM | 2018 | 0 | 4.2 | 8.5 | N | N | industrial | other | LIB | CS | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 238 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.030468 | age_years | infant mortality (k<1)
63044 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 4.3 | 14 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 196 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.025091 | age_years | infant mortality (k<1)
63064 | 0 | 64 | <1.5h | LIB | CS | CPLW | 2020 | 0 | 8.8 | 8.8 | Y | Y | inland | other | LIB | CS | 2020-21 | 1 | 1 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 31 | UNATTRIBUTED | inf | 0.10609 | 5.4106 | 0.019717 | 0.37089 | age_years | infant mortality (k<1)
63090 | 0 | 36 | 1.5-2.5h | LIB | CS | MISO | 2018 | 1 | 3 | 6 | N | N | inland | MISO | LIB | CS | <=2019 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 9 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0.18137 | age_years | infant mortality (k<1)
63172 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 150 | 600 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 14374.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 137.5825 | age_years | infant mortality (k<1)
63186 | 0 | 36 | <1.5h | LIB | CS | JEA | 2019 | 1 | 5 | 3.8 | N | N | inland | other | LIB | CS | <=2019 | 0 | 0 | 0.011892 | ba_g+dur_band+vintage_g | 0 | 0.011892 | 0 | UNATTRIBUTED | inf | 0.13299 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63214 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 3 | 6.6 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 0 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63238 | 0 | 24 | <1.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 20 | Y | N | inland | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 0 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63255 | 0 | 57 | <1.5h | LIB | BL | ERCO | 2021 | 1 | 40 | 40 | Y | Y | arid | ERCO | LIB | BL | 2020-21 | 1 | 1 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 125 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 1.216 | age_years | infant mortality (k<1)
63264 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 32 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 1.7069 | age_years | infant mortality (k<1)
63280 | 0 | 36 | >4.5h | LIB | CT |  | 2021 | 1 | 14 | 70 | N | Y | coastal | other | LIB | CT | 2020-21 | 0 | 1 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 1353 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 16.7957 | age_years | infant mortality (k<1)
63324 | 0 | 36 | <1.5h | LIB | BL | MISO | 2019 | 1 | 5 | 5 | N | N | inland | MISO | LIB | BL | <=2019 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 64.5 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 1.7522 | age_years | infant mortality (k<1)
63337 | 0 | 36 | <1.5h | LIB | CT | NYIS | 2022 | 1 | 3 | 3 | N | N | inland | NYIS | LIB | CT | 2022-23 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 55 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 1.4941 | age_years | infant mortality (k<1)
63338 | 0 | 36 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 63 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.27155 | age_years | infant mortality (k<1)
63339 | 0 | 17 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.026667 | ba_g+dur_band+vintage_g | 0 | 0.026667 | 4.5 | UNATTRIBUTED | inf | 0.27385 | 5.4106 | 0.019717 | 0.15362 | age_years | infant mortality (k<1)
63340 | 0 | 33 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.019355 | ba_g+dur_band+vintage_g | 0 | 0.019355 | 49 | UNATTRIBUTED | inf | 0.20726 | 5.4106 | 0.019717 | 1.2141 | age_years | infant mortality (k<1)
63341 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 3 | 12.8 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.019355 | ba_g+dur_band+vintage_g | 0 | 0.019355 | 52.5 | UNATTRIBUTED | inf | 0.20726 | 5.4106 | 0.019717 | 1.3008 | age_years | infant mortality (k<1)
63352 | 0 | 21 | <1.5h | LIB | CS | NEVP | 2024 | 1 | 380 | 380 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.030215 | dur_band+climate_region | 0 | 0.030215 | 38646 | UNATTRIBUTED | inf | 0.30412 | 5.4106 | 0.019717 | 1494.8287 | age_years | infant mortality (k<1)
63398 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 1 | 1.6 | 3.8 | N | N | coastal | ISNE | LIB | CS | <=2019 | 0 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 104 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 2.9455 | age_years | infant mortality (k<1)
63415 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 1.6 | 6.6 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63420 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 0.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 5 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 0.016002 | age_years | infant mortality (k<1)
63421 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.2 | 0.2 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 0 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63422 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.3 | 0.3 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 0 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63458 | 1 | 24 | 1.5-2.5h | FLB | CS | SWPP | 2020 | 0 | 10 | 20 | Y | N | inland | other | other | CS | 2020-21 | 1 | 0 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 376.5 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 3.5702 | age_years | infant mortality (k<1)
63468 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 1.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 15 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 0.8001 | age_years | infant mortality (k<1)
63469 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.5 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 42.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.11742 | age_years | infant mortality (k<1)
63470 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.9 | 5.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 50 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.13815 | age_years | infant mortality (k<1)
63472 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.3 | 2.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 22.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.062166 | age_years | infant mortality (k<1)
63473 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 1.8 | 3.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 52 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.14367 | age_years | infant mortality (k<1)
63474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 65 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.17959 | age_years | infant mortality (k<1)
63475 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.3 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 63 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.17406 | age_years | infant mortality (k<1)
63486 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.5 | 0.8 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 18 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 0.3093 | age_years | infant mortality (k<1)
63510 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 0.5 | 0.5 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 0.5 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 0.0016002 | age_years | infant mortality (k<1)
63522 | 0 | 43 | 1.5-2.5h | LIB | OT | SOCO | 2022 | 1 | 40 | 80 | N | N | inland | other | LIB | other | 2022-23 | 0 | 0 | 0.017143 | ba_g+dur_band+vintage_g | 0 | 0.017143 | 1540.5 | UNATTRIBUTED | inf | 0.18593 | 5.4106 | 0.019717 | 33.8072 | age_years | infant mortality (k<1)
63535 | 0 | 36 | 2.5-4.5h | LIB | BL | SOCO | 2020 | 1 | 1 | 4 | Y | N | inland | other | LIB | BL | 2020-21 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 93 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.011905 | age_years | infant mortality (k<1)
63585 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 3 | 12 | Y | N | coastal | NYIS | LIB | CS | 2020-21 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 98 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.012546 | age_years | infant mortality (k<1)
63609 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 9 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 91 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 1.3803 | age_years | infant mortality (k<1)
63610 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.2 | 6.3 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 73 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 1.1072 | age_years | infant mortality (k<1)
63611 | 0 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 2.5 | 15 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 218 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 3.3066 | age_years | infant mortality (k<1)
63612 | 0 | 24 | >4.5h | LIB | CS | CISO | 2017 | 0 | 1 | 6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 35 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 0.53087 | age_years | infant mortality (k<1)
63613 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 2 | 13 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 66 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 1.0011 | age_years | infant mortality (k<1)
63614 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1 | 5 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 59 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 0.8949 | age_years | infant mortality (k<1)
63615 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.5 | 8.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 182 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 2.7605 | age_years | infant mortality (k<1)
63616 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 4.9 | 32.6 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 326 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 4.9447 | age_years | infant mortality (k<1)
63617 | 0 | 24 | >4.5h | LIB | CS | CISO | 2019 | 0 | 1.3 | 7.2 | Y | N | coastal | CISO | LIB | CS | <=2019 | 1 | 0 | 0.011848 | ba_g+dur_band+vintage_g | 0 | 0.011848 | 146 | UNATTRIBUTED | inf | 0.13253 | 5.4106 | 0.019717 | 2.2145 | age_years | infant mortality (k<1)
63685 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 100 | 400 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 9551.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 239.9585 | age_years | infant mortality (k<1)
63721 | 0 | 49 | 1.5-2.5h | LIB | CS | SOCO | 2021 | 1 | 40 | 80 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 2340.5 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 22.1942 | age_years | infant mortality (k<1)
63722 | 0 | 36 | 1.5-2.5h | LIB | CS | PSCO | 2021 | 1 | 1 | 2 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 37.5 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 0.3556 | age_years | infant mortality (k<1)
63723 | 0 | 6 | 2.5-4.5h | LIB | CS | HECO | 2025 | 1 | 52 | 208 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 4320.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 175.8954 | age_years | infant mortality (k<1)
63727 | 0 | 47 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 140.3 | 561 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 15233 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 382.6926 | age_years | infant mortality (k<1)
63728 | 0 | 38 | 1.5-2.5h | LIB | CS | PNM | 2022 | 1 | 12.5 | 25 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.017143 | ba_g+dur_band+vintage_g | 0 | 0.017143 | 540.5 | UNATTRIBUTED | inf | 0.18593 | 5.4106 | 0.019717 | 11.8616 | age_years | infant mortality (k<1)
63731 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 125 | 500 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 6763.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 64.7354 | age_years | infant mortality (k<1)
63735 | 1 | 23 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 11 | 44 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 1053.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 33.1247 | age_years | infant mortality (k<1)
63737 | 0 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 125 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 3352 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 32.6071 | age_years | infant mortality (k<1)
63757 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 6598 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 436.6283 | age_years | infant mortality (k<1)
63763 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 5.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 30.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.08427 | age_years | infant mortality (k<1)
63774 | 0 | 9 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 0.7 | 2.1 | N | N | coastal | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00064008 | age_years | infant mortality (k<1)
63775 | 1 | 36 | 1.5-2.5h | LIB | BL | SOCO | 2020 | 0 | 0.2 | 0.4 | N | N | inland | other | LIB | BL | 2020-21 | 0 | 0 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 0 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
63776 | 0 | 31 | 2.5-4.5h | LIB | CS | PSCO | 2023 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 6764.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 64.745 | age_years | infant mortality (k<1)
63804 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2 | 3.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 17.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.048351 | age_years | infant mortality (k<1)
63805 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 44 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.12157 | age_years | infant mortality (k<1)
63834 | 3 | 66 | 2.5-4.5h | LIB | BL | CISO | 2020 | 0 | 250 | 1000 | N | N | coastal | CISO | LIB | BL | 2020-21 | 0 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 12078.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 379.7787 | age_years | infant mortality (k<1)
63843 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2021.75 | 1 | 80 | 320 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 7844 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 197.0617 | age_years | infant mortality (k<1)
63848 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 225 | 900 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 26478.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 665.2088 | age_years | infant mortality (k<1)
63849 | 0 | 23 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 135 | 540 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 16258.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 408.4558 | age_years | infant mortality (k<1)
63859 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 1 | 147 | 147 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 13900.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 782.9743 | age_years | infant mortality (k<1)
63891 | 0 | 57 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 9420.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 296.2044 | age_years | infant mortality (k<1)
63892 | 0 | 52 | <1.5h | LIB | CS | ERCO | 2021 | 1 | 55.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 1015.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 9.8784 | age_years | infant mortality (k<1)
63900 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 1 | 30 | 120 | N | Y | coastal | other | LIB | CS | 2022-23 | 0 | 1 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 3080 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 29.4796 | age_years | infant mortality (k<1)
63905 | 0 | 43 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 91.2 | 80.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 2243 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 148.4324 | age_years | infant mortality (k<1)
63913 | 0 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 5017.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 48.024 | age_years | infant mortality (k<1)
63930 | 0 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 60 | 242 | N | Y | inland | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 5428.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 170.6858 | age_years | infant mortality (k<1)
63933 | 0 | 20 | 1.5-2.5h | LIB | CS | NEVP | 2024 | 1 | 100 | 150 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 10988.5 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 293.0634 | age_years | infant mortality (k<1)
63943 | 0 | 45 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 60 | 240 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 6549 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 164.5279 | age_years | infant mortality (k<1)
63995 | 2 | 23 | <1.5h | LIB | CS | FPC | 2021 | 0 | 11 | 10.1 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 5 | UNATTRIBUTED | inf | 0.10609 | 5.4106 | 0.019717 | 0.059821 | age_years | infant mortality (k<1)
63996 | 0 | 24 | 2.5-4.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 14.3 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 39 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 0.37328 | age_years | infant mortality (k<1)
63998 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 5.5 | 5.5 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 11 | UNATTRIBUTED | inf | 0.20148 | 5.4106 | 0.019717 | 0.26403 | age_years | infant mortality (k<1)
63999 | 0 | 24 | <1.5h | LIB | CS | FPC | 2022 | 0 | 8.3 | 11.7 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 18 | UNATTRIBUTED | inf | 0.20148 | 5.4106 | 0.019717 | 0.43205 | age_years | infant mortality (k<1)
64000 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.2 | 6 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 48 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.13262 | age_years | infant mortality (k<1)
64050 | 0 | 35 | <1.5h | LIB | CS | CPLE | 2023 | 1 | 2 | 2 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 0 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64084 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64087 | 0 | 22 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64089 | 0 | 31 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 6631.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 438.8452 | age_years | infant mortality (k<1)
64090 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64092 | 0 | 21 | 2.5-4.5h | LIB | CS | NYIS | 2019 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | <=2019 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64103 | 0 | 58 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 35 | 140 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 1919.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 60.3539 | age_years | infant mortality (k<1)
64105 | 0 | 43 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 50 | 200 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 3994.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 100.3522 | age_years | infant mortality (k<1)
64128 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 2 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.0055259 | age_years | infant mortality (k<1)
64129 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.1 | 6.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 108.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.29978 | age_years | infant mortality (k<1)
64140 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 1.4 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 13.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.0373 | age_years | infant mortality (k<1)
64147 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.5 | 6.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 50 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.13815 | age_years | infant mortality (k<1)
64148 | 0 | 46 | 2.5-4.5h | LIB | CS | NEVP | 2022 | 1 | 25 | 100 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 2345 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 22.4447 | age_years | infant mortality (k<1)
64164 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 120 | 190 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 4966.5 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 274.1959 | age_years | infant mortality (k<1)
64170 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 0.9 | 1.8 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 14.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.040063 | age_years | infant mortality (k<1)
64182 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 3.7 | 9 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 84.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.23347 | age_years | infant mortality (k<1)
64185 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 1.9 | 3.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 50 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.13815 | age_years | infant mortality (k<1)
64187 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 0.7 | 2.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 15.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0019842 | age_years | infant mortality (k<1)
64197 | 0 | 28 | <1.5h | LIB | CS | CISO | 2023 | 1 | 137 | 137 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 13407 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 53.1366 | age_years | infant mortality (k<1)
64198 | 0 | 36 | 2.5-4.5h | LIB | CS | BPAT | 2020 | 1 | 1 | 4 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 87.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.011201 | age_years | infant mortality (k<1)
64202 | 0 | 12 |  |  |  | ERCO |  | 1 |  |  |  |  | inland | ERCO | other | other | 2020-21 | 0 | 0 | 0.019216 | fleet | 0 | 0.019216 | 1901.5 | UNATTRIBUTED | inf | 0.20594 | 5.4106 | 0.019717 | 46.7763 | age_years | infant mortality (k<1)
64207 | 0 | 24 | <1.5h | LIB | CS | MISO | 2020 | 0 | 5 | 5 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 80.5 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 2.1869 | age_years | infant mortality (k<1)
64213 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 9.4 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 64 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.5462 | age_years | infant mortality (k<1)
64222 | 0 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 10 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0012802 | age_years | infant mortality (k<1)
64223 | 0 | 36 | 2.5-4.5h | LIB | CS | SWPP | 2021 | 1 | 0.7 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 8.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0010881 | age_years | infant mortality (k<1)
64231 | 0 | 12 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 1 | 1 | 4.4 | N | N | inland | ISNE | LIB | CS | 2024+ | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 32.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0041605 | age_years | infant mortality (k<1)
64256 | 0 | 17 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 60 | 240 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 5987.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 243.762 | age_years | infant mortality (k<1)
64293 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 449.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.3726 | age_years | infant mortality (k<1)
64294 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 437 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.251 | age_years | infant mortality (k<1)
64295 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 473 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.6012 | age_years | infant mortality (k<1)
64296 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 432 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.2024 | age_years | infant mortality (k<1)
64297 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 486.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.7325 | age_years | infant mortality (k<1)
64298 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 399.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 3.8862 | age_years | infant mortality (k<1)
64312 | 0 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 2925 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 28.4534 | age_years | infant mortality (k<1)
64314 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 423.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.1197 | age_years | infant mortality (k<1)
64315 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 458 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.4553 | age_years | infant mortality (k<1)
64316 | 1 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 445 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 29.4483 | age_years | infant mortality (k<1)
64317 | 0 | 51 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 110 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 2799 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 27.2277 | age_years | infant mortality (k<1)
64318 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 804 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 53.2054 | age_years | infant mortality (k<1)
64319 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 473.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 4.606 | age_years | infant mortality (k<1)
64321 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 407.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 3.964 | age_years | infant mortality (k<1)
64322 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 19.8 | 19.8 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 874.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 57.8708 | age_years | infant mortality (k<1)
64374 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 5 | 15 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64375 | 0 | 24 | <1.5h | LIB | CS | MISO | 2021 | 0 | 2.5 | 2.9 | N | N | inland | MISO | LIB | CS | 2020-21 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 0 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64395 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2.5 | 5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 39.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.10914 | age_years | infant mortality (k<1)
64400 | 0 | 36 | <1.5h | LIB | CS | HECO | 2021 | 1 | 1.9 | 1.9 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 104 | UNATTRIBUTED | inf | 0.10609 | 5.4106 | 0.019717 | 1.2443 | age_years | infant mortality (k<1)
64423 | 3 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 16.5 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 203 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 11.6535 | age_years | infant mortality (k<1)
64424 | 1 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 17.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 12.5 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 0.71758 | age_years | infant mortality (k<1)
64425 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2020 | 0 | 9.9 | 11.9 | N | N | coastal | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 5.5 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 0.053502 | age_years | infant mortality (k<1)
64426 | 0 | 56 | 1.5-2.5h | LIB | CS | TEPC | 2021 | 1 | 30 | 60 | N | Y | arid | other | LIB | CS | 2020-21 | 0 | 1 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 1502 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 14.243 | age_years | infant mortality (k<1)
64432 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.2 | 4.7 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 13 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.035918 | age_years | infant mortality (k<1)
64436 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 1 | 2.3 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 8 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.022103 | age_years | infant mortality (k<1)
64442 | 0 | 10 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 0.7 | 3 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.019355 | ba_g+dur_band+vintage_g | 0 | 0.019355 | 9 | UNATTRIBUTED | inf | 0.20726 | 5.4106 | 0.019717 | 0.223 | age_years | infant mortality (k<1)
64446 | 0 | 36 | <1.5h | LIB | CS | BPAT | 2021 | 1 | 1 | 1.4 | Y | N | coastal | other | LIB | CS | 2020-21 | 1 | 0 | 0.0093458 | ba_g+dur_band+vintage_g | 0 | 0.0093458 | 14 | UNATTRIBUTED | inf | 0.10609 | 5.4106 | 0.019717 | 0.1675 | age_years | infant mortality (k<1)
64450 | 0 | 36 | <1.5h | LIB | CS | PJM | 2021 | 1 | 10 | 10 | N | N | inland | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 42 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 1.141 | age_years | infant mortality (k<1)
64453 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 3 | 12 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64481 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 132 | 528 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 13892 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 349.0032 | age_years | infant mortality (k<1)
64489 | 0 | 29 | 2.5-4.5h | OTH | CS | CISO | 2023 | 1 | 75 | 300 | N | N | arid | CISO | other | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 6828 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 171.5371 | age_years | infant mortality (k<1)
64508 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 14 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0017922 | age_years | infant mortality (k<1)
64509 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00051206 | age_years | infant mortality (k<1)
64510 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 5.1 | 10 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 38 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0048646 | age_years | infant mortality (k<1)
64511 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 2.5 | 5 | Y | N | coastal | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 16.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0021123 | age_years | infant mortality (k<1)
64512 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.5 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00038405 | age_years | infant mortality (k<1)
64513 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2023 | 1 | 0.6 | 1.1 | Y | N | inland | CPLE | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00051206 | age_years | infant mortality (k<1)
64514 | 0 | 36 | <1.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 2.5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 15 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0.40749 | age_years | infant mortality (k<1)
64516 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 16 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0020483 | age_years | infant mortality (k<1)
64520 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2022 | 1 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 15 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0019202 | age_years | infant mortality (k<1)
64522 | 0 | 36 | 1.5-2.5h | LIB | CS | CPLE | 2021 | 1 | 1.3 | 2 | N | N | inland | CPLE | LIB | CS | 2020-21 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 8.5 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0.17129 | age_years | infant mortality (k<1)
64528 | 0 | 55 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 100 | 200 | Y | N | coastal | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 3780 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 216.9958 | age_years | infant mortality (k<1)
64529 | 0 | 11 | 2.5-4.5h | LIB | CS | TVA | 2025 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 2765 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 112.5682 | age_years | infant mortality (k<1)
64545 | 2 | 16 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 73 | 108.6 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 1935.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 128.0834 | age_years | infant mortality (k<1)
64546 | 0 | 24 | 2.5-4.5h | LIB | BL | FPL | 2019 | 0 | 10 | 40 | N | N | coastal | other | LIB | BL | <=2019 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 218 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.027907 | age_years | infant mortality (k<1)
64564 | 0 | 41 | 2.5-4.5h | LIB | CT | CISO | 2022 | 1 | 110 | 440 | N | N | arid | CISO | LIB | CT | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 9496.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 238.5768 | age_years | infant mortality (k<1)
64601 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2020 | 1 | 0.4 | 1 | N | N | coastal | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 12 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 0.37731 | age_years | infant mortality (k<1)
64611 | 0 | 36 | <1.5h | LIB | CS | CISO | 2020 | 1 | 8.3 | 3.4 | N | N | inland | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 845.5 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 2.7059 | age_years | infant mortality (k<1)
64612 | 2 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 0 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
64614 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 10 | 40 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 823.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 20.6885 | age_years | infant mortality (k<1)
64617 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 2.6 | 9.5 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 175 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.022403 | age_years | infant mortality (k<1)
64618 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 9 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 145 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 1.8 | age_years | infant mortality (k<1)
64619 | 0 | 33 | >4.5h | LIB | CS | ISNE | 2023 | 1 | 0.8 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 69 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.85654 | age_years | infant mortality (k<1)
64620 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 5.1 | N | Y | inland | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 90 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.011521 | age_years | infant mortality (k<1)
64624 | 0 | 49 | <1.5h | LIB | CS | CISO | 2021 | 1 | 50 | 50 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 5021.5 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 16.0708 | age_years | infant mortality (k<1)
64627 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 17 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 0.90678 | age_years | infant mortality (k<1)
64630 | 0 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 20 | 50 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 1453.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 36.5157 | age_years | infant mortality (k<1)
64633 | 0 | 11 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 240 | 960 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 24396 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 1149.882 | age_years | infant mortality (k<1)
64636 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 200 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 8455 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 476.2453 | age_years | infant mortality (k<1)
64640 | 0 | 36 | <1.5h | LIB | CS | CPLW | 2022 | 1 | 4.4 | 4.4 | N | Y | inland | other | LIB | CS | 2022-23 | 0 | 1 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 18.5 | UNATTRIBUTED | inf | 0.20148 | 5.4106 | 0.019717 | 0.44406 | age_years | infant mortality (k<1)
64656 | 0 | 18 | 2.5-4.5h | LIB | CS | HECO | 2024 | 1 | 12.5 | 50 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 1251 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 50.9305 | age_years | infant mortality (k<1)
64664 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 92 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 4.9073 | age_years | infant mortality (k<1)
64672 | 0 | 31 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.6 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 1596 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 88.1137 | age_years | infant mortality (k<1)
64686 | 0 | 36 | <1.5h | LIB | OT | NYIS | 2022 | 1 | 24.7 | 20 | N | Y | inland | NYIS | LIB | other | 2022-23 | 0 | 1 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 1020 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 27.7092 | age_years | infant mortality (k<1)
64695 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 3.7 | 15 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 186.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 1.785 | age_years | infant mortality (k<1)
64696 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 4.5 | 20.2 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 225 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.028804 | age_years | infant mortality (k<1)
64701 | 0 | 40 | 1.5-2.5h | LIB | CS | CISO | 2022 | 0 | 125 | 250 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 7244 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.92735 | age_years | infant mortality (k<1)
64712 | 2 | 50 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 100 | 200 | N | N | arid | CISO | LIB | CS | 2020-21 | 0 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 5802.5 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 93.6319 | age_years | infant mortality (k<1)
64713 | 1 | 50 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 10979.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 345.2233 | age_years | infant mortality (k<1)
64719 | 0 | 36 | 2.5-4.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 7.5 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 28 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0035844 | age_years | infant mortality (k<1)
64726 | 0 | 35 | 1.5-2.5h | LIB | CT | ISNE | 2022 | 1 | 3.6 | 8 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 67 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.5718 | age_years | infant mortality (k<1)
64727 | 0 | 36 | 2.5-4.5h | LIB | OT | ISNE | 2022 | 1 | 3 | 8 | N | N | coastal | ISNE | LIB | other | 2022-23 | 0 | 0 | 0.015 | ba_g+dur_band+vintage_g | 0 | 0.015 | 43.5 | UNATTRIBUTED | inf | 0.16473 | 5.4106 | 0.019717 | 0.8353 | age_years | infant mortality (k<1)
64731 | 0 | 36 | 1.5-2.5h | OTH | CS | ISNE | 2021 | 1 | 2.3 | 4.8 | N | N | inland | ISNE | other | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 0.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.0013815 | age_years | infant mortality (k<1)
64743 | 0 | 36 | <1.5h | LIB | CS | CISO | 2022 | 0 | 5 | 5 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 351.5 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 1.3931 | age_years | infant mortality (k<1)
64752 | 0 | 24 | >4.5h | LIB | CS | FPC | 2023 | 1 | 2.5 | 18 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 35.5 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.44069 | age_years | infant mortality (k<1)
64759 | 0 | 24 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 4.5 | 13.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015 | ba_g+dur_band+vintage_g | 0 | 0.015 | 142.5 | UNATTRIBUTED | inf | 0.16473 | 5.4106 | 0.019717 | 2.7363 | age_years | infant mortality (k<1)
64760 | 3 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 0 | 3 | 10 | Y | Y | coastal | ISNE | LIB | CS | 2022-23 | 1 | 1 | 0.015 | ba_g+dur_band+vintage_g | 0 | 0.015 | 87.5 | UNATTRIBUTED | inf | 0.16473 | 5.4106 | 0.019717 | 1.6802 | age_years | infant mortality (k<1)
64761 | 0 | 6 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 2 | 11.9 | N | N | coastal | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 42.5 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.52758 | age_years | infant mortality (k<1)
64763 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | 2020-21 | 1 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 41.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.11466 | age_years | infant mortality (k<1)
64764 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2020 | 0 | 1.5 | 3.1 | Y | Y | inland | ISNE | LIB | CS | 2020-21 | 1 | 1 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 35.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.098084 | age_years | infant mortality (k<1)
64765 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2019 | 0 | 4.9 | 10 | Y | N | inland | ISNE | LIB | CS | <=2019 | 1 | 0 | 0.022124 | ba_g+dur_band+vintage_g | 0 | 0.022124 | 46.5 | UNATTRIBUTED | inf | 0.23317 | 5.4106 | 0.019717 | 1.317 | age_years | infant mortality (k<1)
64766 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 2.2 | 8.8 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 44.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 1.3992 | age_years | infant mortality (k<1)
64811 | 1 | 23 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 24.8 | 25 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 565.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 37.4224 | age_years | infant mortality (k<1)
64844 | 0 | 13 | 1.5-2.5h | PBB | CS | ISNE | 2024 | 1 | 1.4 | 2.8 | Y | N | inland | ISNE | other | CS | 2024+ | 1 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 23 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0.46349 | age_years | infant mortality (k<1)
64851 | 0 | 23 | <1.5h | LIB | CS | CISO | 2023 | 1 | 131 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 11681 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 46.2958 | age_years | infant mortality (k<1)
64852 | 0 | 29 | <1.5h | LIB | CS | CISO | 2023 | 1 | 149 | 4.6 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 12083.5 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 47.8911 | age_years | infant mortality (k<1)
64864 | 0 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 88 | 352 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 8291 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 390.7883 | age_years | infant mortality (k<1)
64875 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 23 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.063548 | age_years | infant mortality (k<1)
64876 | 0 | 36 | <1.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 286 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 15.2552 | age_years | infant mortality (k<1)
64877 | 0 | 44 | 2.5-4.5h | LIB | CS | CISO | 2021 | 1 | 11 | 31.5 | Y | Y | arid | CISO | LIB | CS | 2020-21 | 1 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 495 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 15.5641 | age_years | infant mortality (k<1)
64878 | 0 | 41 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 144 | 272 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6838.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.87544 | age_years | infant mortality (k<1)
64879 | 0 | 44 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 120 | 250 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4492 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.57505 | age_years | infant mortality (k<1)
64908 | 0 | 19 | >4.5h | LIB | CS | CISO | 2024 | 1 | 40 | 200 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.012931 | dur_band+climate_region | 0 | 0.012931 | 3315 | UNATTRIBUTED | inf | 0.14373 | 5.4106 | 0.019717 | 54.8758 | age_years | infant mortality (k<1)
64915 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 524.5 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 30.1096 | age_years | infant mortality (k<1)
64916 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 9.9 | 19.8 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 444 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 25.4884 | age_years | infant mortality (k<1)
64917 | 0 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 7.5 | 15 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 401.5 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 23.0486 | age_years | infant mortality (k<1)
64921 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 20 | 80 | Y | Y | coastal | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 |  | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
64928 | 0 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 33 | 70 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1792.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.22947 | age_years | infant mortality (k<1)
64929 | 0 | 42 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 40 | 83.5 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1178 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.1508 | age_years | infant mortality (k<1)
64970 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2021 | 1 | 5 | 20.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 99 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.012674 | age_years | infant mortality (k<1)
64980 | 0 | 36 | 2.5-4.5h | LIB | BL | ISNE | 2021 | 1 | 0.5 | 2.1 | N | N | coastal | ISNE | LIB | BL | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00038405 | age_years | infant mortality (k<1)
64993 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 40 | 160 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 1829 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 45.9492 | age_years | infant mortality (k<1)
65007 | 0 | 3 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 100 | 400 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 4 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 0.18965 | age_years | infant mortality (k<1)
65011 | 0 | 2 | 2.5-4.5h | ECC | OT | MISO | 2025 | 1 | 75 | 300 | N | N | inland | MISO | other | other | 2024+ | 0 | 0 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 4.5 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 0.21336 | age_years | infant mortality (k<1)
65014 | 0 | 18 | 1.5-2.5h | LIB | CS | ISNE | 2024 | 1 | 2.5 | 4.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 4.5 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 0.10021 | age_years | infant mortality (k<1)
65015 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 3.8 | 12.8 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015 | ba_g+dur_band+vintage_g | 0 | 0.015 | 153.5 | UNATTRIBUTED | inf | 0.16473 | 5.4106 | 0.019717 | 2.9476 | age_years | infant mortality (k<1)
65018 | 0 | 15 | 2.5-4.5h | LIB | OT | SOCO | 2024 | 0 | 65 | 260 | N | Y | inland | other | LIB | other | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 7460 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 303.7101 | age_years | infant mortality (k<1)
65028 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 1 | 51.8 | 84.5 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 1679 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 92.696 | age_years | infant mortality (k<1)
65029 | 0 | 36 | 1.5-2.5h | LIB | BL | MISO | 2021 | 1 | 0.3 | 0.5 | Y | N | inland | MISO | LIB | BL | 2020-21 | 1 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
65035 | 2 | 16 | 2.5-4.5h | LIB | CS | NYIS | 2023 | 0 | 7.5 | 30 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.019355 | ba_g+dur_band+vintage_g | 0 | 0.019355 | 646 | UNATTRIBUTED | inf | 0.20726 | 5.4106 | 0.019717 | 16.0061 | age_years | infant mortality (k<1)
65044 | 1 | 24 | 2.5-4.5h | LIB | CS | PJM | 2023 | 0 | 20 | 80 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 1729 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 24.3696 | age_years | infant mortality (k<1)
65053 | 0 | 34 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 112 | 448 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 13042 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 327.649 | age_years | infant mortality (k<1)
65054 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1 | 5.4 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 33.5 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.41586 | age_years | infant mortality (k<1)
65055 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.2 | 4.8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 20.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.05664 | age_years | infant mortality (k<1)
65056 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 3.3 | 6.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 36.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.10085 | age_years | infant mortality (k<1)
65057 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.3 | 4.9 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 23.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.064929 | age_years | infant mortality (k<1)
65058 | 0 | 30 | <1.5h | LIB | CS | HECO | 2023 | 1 | 36 | 4.6 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 2776.5 | UNATTRIBUTED | inf | 0.20148 | 5.4106 | 0.019717 | 66.6444 | age_years | infant mortality (k<1)
65098 | 0 | 21 | 1.5-2.5h | LIB | CS | SWPP | 2020 | 0 | 1.5 | 3 | N | N | inland | other | LIB | CS | 2020-21 | 0 | 0 | 0.0074074 | ba_g+dur_band+vintage_g | 0 | 0.0074074 | 17 | UNATTRIBUTED | inf | 0.085053 | 5.4106 | 0.019717 | 0.16121 | age_years | infant mortality (k<1)
65114 | 0 | 36 | >4.5h | LIB | CS | ISNE | 2021 | 1 | 1.5 | 8 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 81.5 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 1.0117 | age_years | infant mortality (k<1)
65140 | 0 | 39 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 350 | 1400 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 42235.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 1061.0657 | age_years | infant mortality (k<1)
65154 | 0 | 12 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 2 | 4.3 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 16 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.13655 | age_years | infant mortality (k<1)
65174 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2 | 4.5 | N | N | coastal | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 37 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.10223 | age_years | infant mortality (k<1)
65217 | 0 | 36 | 2.5-4.5h | LIB | OT | NYIS | 2021 | 1 | 4.5 | 17 | N | N | inland | NYIS | LIB | other | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 43.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0055687 | age_years | infant mortality (k<1)
65239 | 1 | 7 | >4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 24.6 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 255 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 3.1655 | age_years | infant mortality (k<1)
65240 | 2 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 48 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 4.0332 | age_years | infant mortality (k<1)
65241 | 1 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 38 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 3.193 | age_years | infant mortality (k<1)
65242 | 0 | 35 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 2.5 | 3.8 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 0 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
65243 | 2 | 24 | 2.5-4.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 21.5 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0.30303 | age_years | infant mortality (k<1)
65244 | 2 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 25.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 2.1427 | age_years | infant mortality (k<1)
65245 | 1 | 24 | <1.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 5 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.029655 | dur_band+climate_region | 0 | 0.029655 | 25.5 | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 | 0.96807 | age_years | infant mortality (k<1)
65246 | 1 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 38.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 3.235 | age_years | infant mortality (k<1)
65247 | 1 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 34.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 2.8989 | age_years | infant mortality (k<1)
65248 | 2 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 2.5 | 5 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 22.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 1.8906 | age_years | infant mortality (k<1)
65249 | 1 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 31 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 2.6048 | age_years | infant mortality (k<1)
65250 | 2 | 24 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 48 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 4.0332 | age_years | infant mortality (k<1)
65259 | 0 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 1228.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 81.297 | age_years | infant mortality (k<1)
65271 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 125 | 125 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 1227 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 81.1978 | age_years | infant mortality (k<1)
65291 | 0 | 19 | 2.5-4.5h | LIB | CS | TVA | 2024 | 1 | 50 | 200 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 2637.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 107.3774 | age_years | infant mortality (k<1)
65382 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 1 | 2 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 39.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0050566 | age_years | infant mortality (k<1)
65396 | 0 | 2 | <1.5h | LIB | CS | CISO | 2025 | 0 | 15 | 15 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 1080.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 60.8614 | age_years | infant mortality (k<1)
65397 | 3 | 14 | <1.5h | LIB | CS | CISO | 2024 | 0 | 30 | 30 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 1606 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 90.4613 | age_years | infant mortality (k<1)
65408 | 0 | 9 | 2.5-4.5h | LIB | CT | CISO | 2021 | 1 | 0.7 | 3 | Y | N | coastal | CISO | LIB | CT | 2020-21 | 1 | 0 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 24 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 0.75462 | age_years | infant mortality (k<1)
65409 | 0 | 36 | 1.5-2.5h | LIB | CT | CISO | 2021 | 1 | 0.5 | 0.9 | N | N | coastal | CISO | LIB | CT | 2020-21 | 0 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 22 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 0.355 | age_years | infant mortality (k<1)
65410 | 3 | 29 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 190 | 380 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 7814 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 431.4037 | age_years | infant mortality (k<1)
65422 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 510 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 20.763 | age_years | infant mortality (k<1)
65429 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 555 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 22.5951 | age_years | infant mortality (k<1)
65433 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 426 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 17.3432 | age_years | infant mortality (k<1)
65441 | 0 | 36 | 2.5-4.5h | LIB | CS | MISO | 2022 | 1 | 1 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 6.5 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0.091615 | age_years | infant mortality (k<1)
65456 | 1 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 112.5 | 450 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 9593 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 452.1568 | age_years | infant mortality (k<1)
65457 | 2 | 11 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 18390 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 866.7949 | age_years | infant mortality (k<1)
65468 | 0 | 12 | 2.5-4.5h | LIB | BL | PJM | 2019 | 1 | 0.6 | 2.1 | Y | Y | coastal | PJM | LIB | BL | <=2019 | 1 | 1 | 0.024635 | dur_band+climate_region | 0 | 0.024635 | 11.5 | UNATTRIBUTED | inf | 0.25593 | 5.4106 | 0.019717 | 0.36268 | age_years | infant mortality (k<1)
65469 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2022 | 1 | 0.8 | 3.1 | N | N | industrial | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 53 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 1.3315 | age_years | infant mortality (k<1)
65472 | 0 | 24 | 2.5-4.5h | LIB | CS | NEVP | 2021 | 0 | 10 | 40 | N | N | arid | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 898.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.11502 | age_years | infant mortality (k<1)
65489 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 10262 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 679.5003 | age_years | infant mortality (k<1)
65490 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 8758.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 579.9458 | age_years | infant mortality (k<1)
65491 | 3 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 200 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 7961.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 527.1723 | age_years | infant mortality (k<1)
65492 | 0 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 175 | 175 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 8880 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 587.9909 | age_years | infant mortality (k<1)
65493 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 50 | 50 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 2595 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 171.8284 | age_years | infant mortality (k<1)
65499 | 0 | 36 | 1.5-2.5h | LIB | CS | PJM | 2022 | 0 | 10.5 | 24.6 | Y | Y | inland | PJM | LIB | CS | 2022-23 | 1 | 1 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 1144 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 23.0538 | age_years | infant mortality (k<1)
65530 | 4 | 24 | 1.5-2.5h | LIB | CS | MISO | 2022 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 140 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 2.8213 | age_years | infant mortality (k<1)
65531 | 1 | 24 | 1.5-2.5h | LIB | CS | MISO | 2023 | 0 | 5 | 10 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 121.5 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 2.4485 | age_years | infant mortality (k<1)
65562 | 0 | 24 | 2.5-4.5h | MAB | BL | CISO | 2024 | 1 | 1.6 | 5.9 | N | N | arid | CISO | other | BL | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 85 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 4.0064 | age_years | infant mortality (k<1)
65568 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 1 | 0.6 | 1.1 | Y | N | coastal | CISO | LIB | CS | 2020-21 | 1 | 0 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 24.5 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 0.39534 | age_years | infant mortality (k<1)
65588 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 70 | 140 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 4197 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 284.923 | age_years | infant mortality (k<1)
65589 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 8060.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 547.2055 | age_years | infant mortality (k<1)
65591 | 2 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 126 | 504 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 10586 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 498.9609 | age_years | infant mortality (k<1)
65614 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 2.1 | 4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 70 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0089611 | age_years | infant mortality (k<1)
65633 | 0 | 29 | <1.5h | LIB | CS | MISO | 2023 | 0 | 3.6 | 3 | N | N | inland | MISO | LIB | CS | 2022-23 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 1 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0.027166 | age_years | infant mortality (k<1)
65635 | 1 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 587 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 27.5763 | age_years | infant mortality (k<1)
65644 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 7236 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 491.2325 | age_years | infant mortality (k<1)
65645 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 160 | 320 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 8723 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 592.1809 | age_years | infant mortality (k<1)
65650 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 1.7 | N | N | inland | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 27.5 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 1.4669 | age_years | infant mortality (k<1)
65656 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 20 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 1183.5 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 55.5989 | age_years | infant mortality (k<1)
65657 | 1 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 65 | 40 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 3090 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 174.0506 | age_years | infant mortality (k<1)
65669 | 0 | 36 | 2.5-4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 3.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.015 | ba_g+dur_band+vintage_g | 0 | 0.015 | 40 | UNATTRIBUTED | inf | 0.16473 | 5.4106 | 0.019717 | 0.7681 | age_years | infant mortality (k<1)
65670 | 0 | 35 | >4.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 5 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.009697 | dur_band+climate_region | 0 | 0.009697 | 27.5 | UNATTRIBUTED | inf | 0.10985 | 5.4106 | 0.019717 | 0.34138 | age_years | infant mortality (k<1)
65672 | 0 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 169 | 676 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 18683.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 469.3781 | age_years | infant mortality (k<1)
65673 | 3 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 47 | 188 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 5100 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 128.1253 | age_years | infant mortality (k<1)
65674 | 0 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 136 | 136 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 9030.5 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 35.791 | age_years | infant mortality (k<1)
65675 | 0 | 26 | <1.5h | LIB | CS | CISO | 2023 | 1 | 100 | 100 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 2440.5 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 9.6725 | age_years | infant mortality (k<1)
65677 | 0 | 30 | <1.5h | LIB | CS | CISO | 2023 | 1 | 18.8 | 18.8 | Y | Y | arid | CISO | LIB | CS | 2022-23 | 1 | 1 | 0.003096 | ba_g+dur_band+vintage_g | 0 | 0.003096 | 548.5 | UNATTRIBUTED | inf | 0.03647 | 5.4106 | 0.019717 | 2.1739 | age_years | infant mortality (k<1)
65692 | 0 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 0 | 20 | 42 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 2304 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 46.4301 | age_years | infant mortality (k<1)
65693 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 5777 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 392.1849 | age_years | infant mortality (k<1)
65694 | 2 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 802 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 53.073 | age_years | infant mortality (k<1)
65695 | 0 | 39 | <1.5h | LIB | CS | ERCO | 2022 | 1 | 100 | 100 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 1932 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 127.8517 | age_years | infant mortality (k<1)
65696 | 3 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 2297 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 152.0059 | age_years | infant mortality (k<1)
65698 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 227 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 6370 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 432.4421 | age_years | infant mortality (k<1)
65699 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 111 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 3123 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 172.4179 | age_years | infant mortality (k<1)
65700 | 0 | 30 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 50 | 107 | N | N | inland | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 3040.5 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 167.8632 | age_years | infant mortality (k<1)
65701 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 50 | 50 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 800 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 52.9407 | age_years | infant mortality (k<1)
65711 | 0 | 17 | 2.5-4.5h | LIB | CS | IID | 2024 | 1 | 150 | 600 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 14331 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 583.441 | age_years | infant mortality (k<1)
65733 | 1 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 10 | 20 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 588 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 27.6233 | age_years | infant mortality (k<1)
65734 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 15606.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 392.0759 | age_years | infant mortality (k<1)
65735 | 0 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 125 | 500 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 14596.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 366.7021 | age_years | infant mortality (k<1)
65743 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 50 | 200 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 4762 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 224.4523 | age_years | infant mortality (k<1)
65744 | 0 | 22 | 2.5-4.5h | LIB | CT | CISO | 2024 | 1 | 136 | 544 | N | Y | arid | CISO | LIB | CT | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 12977.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 611.682 | age_years | infant mortality (k<1)
65809 | 2 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 172.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 11.4153 | age_years | infant mortality (k<1)
65810 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 186 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 12.3087 | age_years | infant mortality (k<1)
65811 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 186 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 12.3087 | age_years | infant mortality (k<1)
65812 | 0 | 21 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 136 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 9.0053 | age_years | infant mortality (k<1)
65813 | 3 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 182.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 12.0771 | age_years | infant mortality (k<1)
65814 | 3 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 184.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 12.2094 | age_years | infant mortality (k<1)
65815 | 0 | 24 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 1 | 2.1 | Y | N | coastal | NYIS | LIB | CS | 2022-23 | 1 | 0 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 2 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 0.044539 | age_years | infant mortality (k<1)
65829 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 159 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 10.522 | age_years | infant mortality (k<1)
65830 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 157.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 10.4227 | age_years | infant mortality (k<1)
65831 | 2 | 36 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 179.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 11.8786 | age_years | infant mortality (k<1)
65832 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 130 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 8.6029 | age_years | infant mortality (k<1)
65833 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 177.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 11.7462 | age_years | infant mortality (k<1)
65834 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2022 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 186 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 12.3087 | age_years | infant mortality (k<1)
65835 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 182.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 12.0771 | age_years | infant mortality (k<1)
65836 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2021 | 0 | 10.4 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2020-21 | 1 | 0 | 0.0075988 | ba_g+dur_band+vintage_g | 0 | 0.0075988 | 191 | UNATTRIBUTED | inf | 0.087152 | 5.4106 | 0.019717 | 1.858 | age_years | infant mortality (k<1)
65837 | 3 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 106 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 7.0188 | age_years | infant mortality (k<1)
65857 | 2 | 30 | 2.5-4.5h | LIB | CS | CISO | 2022 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 22207 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 557.8976 | age_years | infant mortality (k<1)
65860 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 160 | 320 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 8869.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 602.1264 | age_years | infant mortality (k<1)
65861 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 10423 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 707.5893 | age_years | infant mortality (k<1)
65866 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 593 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 24.1421 | age_years | infant mortality (k<1)
65888 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | coastal | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 524 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 21.333 | age_years | infant mortality (k<1)
65927 | 0 | 1 | 2.5-4.5h | LIB | CS | FPL | 2025 | 1 | 74.5 | 223.5 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 547 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 22.2694 | age_years | infant mortality (k<1)
65933 | 4 | 32 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 80 | 320 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 6966.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 175.0166 | age_years | infant mortality (k<1)
65945 | 0 | 36 | 2.5-4.5h | LIB | CS | PJM | 2022 | 1 | 1.5 | 4.3 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0.024635 | dur_band+climate_region | 0 | 0.024635 | 12 | UNATTRIBUTED | inf | 0.25593 | 5.4106 | 0.019717 | 0.37845 | age_years | infant mortality (k<1)
65950 | 0 | 32 | 2.5-4.5h | LIB | CS | ISNE | 2023 | 1 | 1.8 | 6.4 | N | Y | coastal | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.015 | ba_g+dur_band+vintage_g | 0 | 0.015 | 120 | UNATTRIBUTED | inf | 0.16473 | 5.4106 | 0.019717 | 2.3043 | age_years | infant mortality (k<1)
65951 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 12 | 12 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 2050.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.2625 | age_years | infant mortality (k<1)
65952 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 20 | 20 | N | N | inland | PJM | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 3327 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.42591 | age_years | infant mortality (k<1)
65953 | 0 | 24 | <1.5h | LIB | CS | PJM | 2023 | 0 | 7 | 7 | N | N | coastal | PJM | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 1143.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.14639 | age_years | infant mortality (k<1)
65956 | 0 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 88 | 264 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 6630.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 63.4625 | age_years | infant mortality (k<1)
65962 | 0 | 24 | >4.5h | LIB | CS | CISO | 2024 | 1 | 10 | 47.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 761.5 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 10.9945 | age_years | infant mortality (k<1)
65963 | 0 | 30 | 2.5-4.5h | LIB | CS | AZPS | 2023 | 1 | 60 | 240 | N | N | arid | AZPS | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 6495.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.83153 | age_years | infant mortality (k<1)
65980 | 2 | 31 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 131 | 524 | N | N | arid | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 13311 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 334.407 | age_years | infant mortality (k<1)
65987 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 325 | 1300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 39866.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 1001.5502 | age_years | infant mortality (k<1)
65988 | 0 | 30 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 8284.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 208.1282 | age_years | infant mortality (k<1)
66006 | 3 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 73.2 | 120 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 3429.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 232.8195 | age_years | infant mortality (k<1)
66007 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 4593 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 253.5753 | age_years | infant mortality (k<1)
66008 | 0 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 101 | 200 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 4727 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 260.9733 | age_years | infant mortality (k<1)
66009 | 5 | 36 | 1.5-2.5h | LIB | CS | ERCO | 2022 | 0 | 203 | 400 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 5889 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 325.1262 | age_years | infant mortality (k<1)
66023 | 0 | 14 | <1.5h | LIB | CS | CISO | 2024 | 1 | 1 | 1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 0 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66050 | 2 | 40 | 2.5-4.5h | LIB | CT | CISO | 2022 | 0 | 127 | 508 | N | Y | inland | CISO | LIB | CT | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 12855 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 322.9511 | age_years | infant mortality (k<1)
66067 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2023 | 0 | 185 | 565 | N | N | coastal | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 14604 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 139.7792 | age_years | infant mortality (k<1)
66075 | 0 | 36 | 1.5-2.5h | LIB | CT | ISNE | 2021 | 1 | 2 | 3.3 | N | N | coastal | ISNE | LIB | CT | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 101 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.27906 | age_years | infant mortality (k<1)
66076 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 1 | 1 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 71 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.30603 | age_years | infant mortality (k<1)
66128 | 0 | 10 | 2.5-4.5h | LIB | CS | TEC | 2025 | 1 | 40 | 103 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 779.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 31.7349 | age_years | infant mortality (k<1)
66129 | 0 | 10 | 1.5-2.5h | LIB | CS | TEC | 2024 | 1 | 15 | 30 | Y | Y | coastal | other | LIB | CS | 2024+ | 1 | 1 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 226.5 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 6.0408 | age_years | infant mortality (k<1)
66137 | 0 | 21 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 40.4 | 80 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 2080 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 141.2056 | age_years | infant mortality (k<1)
66163 | 0 | 30 | 2.5-4.5h | LIB | CS | PNM | 2023 | 1 | 20 | 80 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 1975.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 18.9081 | age_years | infant mortality (k<1)
66170 | 1 | 24 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 368.8 | N | N | arid | ERCO | LIB | CS | 2022-23 | 0 | 0 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 7464 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 412.0805 | age_years | infant mortality (k<1)
66180 | 0 | 28 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 3.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 0 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66181 | 0 | 29 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 5 | 7.8 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 0 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66182 | 0 | 33 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 0 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66208 | 1 | 28 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 132 | 528 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 15161.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 380.8963 | age_years | infant mortality (k<1)
66218 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2020 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66222 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2021 | 1 | 4 | 8 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66228 | 0 | 36 | <1.5h | LIB | CS | NYIS | 2021 | 1 | 2 | 2 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 0 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66232 | 0 | 36 | 1.5-2.5h | LIB | CS | NYIS | 2022 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66263 | 0 | 19 | 2.5-4.5h | LIB | CS | SRP | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 33877.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 1379.2145 | age_years | infant mortality (k<1)
66265 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 828.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 46.667 | age_years | infant mortality (k<1)
66266 | 2 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 648.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 36.5281 | age_years | infant mortality (k<1)
66270 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 162 | 648 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 12611 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 594.4073 | age_years | infant mortality (k<1)
66278 | 1 | 21 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 740.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 41.7102 | age_years | infant mortality (k<1)
66279 | 1 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 652 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 36.7252 | age_years | infant mortality (k<1)
66280 | 0 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 10 | 10 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 1082.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 60.974 | age_years | infant mortality (k<1)
66281 | 2 | 22 | <1.5h | LIB | CS | CISO | 2024 | 0 | 20 | 20 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 859 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 48.3849 | age_years | infant mortality (k<1)
66285 | 1 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 200 | 800 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 20915 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 985.8084 | age_years | infant mortality (k<1)
66286 | 1 | 7 | 1.5-2.5h | LIB | CS | CISO | 2025 | 0 | 200 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 10781 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 506.4737 | age_years | infant mortality (k<1)
66325 | 0 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 116 | 464 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 4738.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 192.9129 | age_years | infant mortality (k<1)
66326 | 1 | 10 | 2.5-4.5h | FLB | CS | IPCO | 2024 | 0 | 40 | 160 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 3490.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 142.1046 | age_years | infant mortality (k<1)
66327 | 2 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 4 | 16 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 267 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 10.8701 | age_years | infant mortality (k<1)
66328 | 1 | 12 | 1.5-2.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 4 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 140 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 3.7338 | age_years | infant mortality (k<1)
66329 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 2 | 8 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 0 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66330 | 0 | 12 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 3 | 12 | N | N | inland | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 274.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 11.1754 | age_years | infant mortality (k<1)
66333 | 1 | 18 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 90 | 360 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 10478 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 426.5784 | age_years | infant mortality (k<1)
66334 | 0 | 20 | 2.5-4.5h | LIB | CS | SRP | 2024 | 0 | 250 | 1000 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 30035 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 1222.7794 | age_years | infant mortality (k<1)
66336 | 1 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 102.6 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 5791.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 393.1693 | age_years | infant mortality (k<1)
66337 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 11481 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 779.414 | age_years | infant mortality (k<1)
66338 | 2 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 223.4 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 11024.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 729.9894 | age_years | infant mortality (k<1)
66357 | 0 | 30 | 2.5-4.5h | LIB | CS | NEVP | 2023 | 1 | 65 | 260 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 6979.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 66.8028 | age_years | infant mortality (k<1)
66394 | 1 | 23 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 60 | 160 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 3423.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 161.3634 | age_years | infant mortality (k<1)
66408 | 0 | 31 | 2.5-4.5h | LIB | CS | EPE | 2023 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2022-23 | 0 | 0 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 3308 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 31.6618 | age_years | infant mortality (k<1)
66420 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 262.5 | 250 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 8277 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 548.0632 | age_years | infant mortality (k<1)
66423 | 0 | 26 | 2.5-4.5h | LIB | CS | CISO | 2023 | 0 | 68.8 | 275.2 | N | Y | coastal | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 7325.5 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 184.0356 | age_years | infant mortality (k<1)
66461 | 0 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 116.6 | 400 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 10026 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 472.5658 | age_years | infant mortality (k<1)
66462 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 88 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 8473 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 399.3667 | age_years | infant mortality (k<1)
66474 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 6.4 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 0 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66488 | 0 | 27 | 1.5-2.5h | LIB | CS | NYIS | 2023 | 1 | 2 | 4 | N | N | inland | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66494 | 0 | 19 | 2.5-4.5h | LIB | CS | CISO | 2024.0882 | 0 | 680 | 2720 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 71677 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 3378.4263 | age_years | infant mortality (k<1)
66499 | 0 | 36 | 1.5-2.5h | LIB | CT | PJM | 2021 | 1 | 1.2 | 2.4 | N | N | coastal | PJM | LIB | CT | 2020-21 | 0 | 0 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 2 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 0.044539 | age_years | infant mortality (k<1)
66500 | 0 | 36 | 1.5-2.5h | LIB | CS | CISO | 2021 | 0 | 85 | 212 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.012605 | ba_g+dur_band+vintage_g | 0 | 0.012605 | 4968.5 | UNATTRIBUTED | inf | 0.14038 | 5.4106 | 0.019717 | 80.1741 | age_years | infant mortality (k<1)
66502 | 0 | 36 | 2.5-4.5h | LIB | CS | CISO | 2021 | 0 | 54 | 216 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.024561 | ba_g+dur_band+vintage_g | 0 | 0.024561 | 3759.5 | UNATTRIBUTED | inf | 0.25527 | 5.4106 | 0.019717 | 118.2082 | age_years | infant mortality (k<1)
66505 | 1 | 15 | 1.5-2.5h | LIB | CS | CISO | 2024 | 0 | 6 | 12 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 212 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 9.9594 | age_years | infant mortality (k<1)
66533 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 10 | 20 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 |  | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 |  | age_years | infant mortality (k<1)
66540 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 100 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 8494 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 562.4319 | age_years | infant mortality (k<1)
66574 | 0 | 15 | >4.5h | LIB | CS | PNM | 2024 | 1 | 100 | 561.4 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 10717.5 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 154.7382 | age_years | infant mortality (k<1)
66575 | 2 | 21 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 230 | 920 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 24158 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 1138.6641 | age_years | infant mortality (k<1)
66598 | 0 | 15 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 75 | 300 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 4250.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 200.3432 | age_years | infant mortality (k<1)
66599 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 0 | 7.3 | 7.1 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 423.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 23.8545 | age_years | infant mortality (k<1)
66606 | 1 | 2 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 175 | 350 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 2393 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 53.291 | age_years | infant mortality (k<1)
66616 | 0 | 30 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 5008 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 331.4087 | age_years | infant mortality (k<1)
66617 | 0 | 17 | 2.5-4.5h | LIB | CT | CISO | 2024 | 0 | 100 | 400 | N | N | coastal | CISO | LIB | CT | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 12037 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 567.3524 | age_years | infant mortality (k<1)
66619 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 1.2 | 4.6 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 104 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 4.9019 | age_years | infant mortality (k<1)
66620 | 0 | 29 | >4.5h | LIB | CS | CISO | 2023 | 1 | 40 | 300 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 3569.5 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 51.5361 | age_years | infant mortality (k<1)
66627 | 0 | 31 | 2.5-4.5h | LIB | CS | SRP | 2023 | 1 | 260 | 1040 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 26072.5 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 249.5475 | age_years | infant mortality (k<1)
66636 | 0 | 25 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 100 | 400 | N | Y | arid | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 9634 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 242.0311 | age_years | infant mortality (k<1)
66637 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 15386 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 725.2043 | age_years | infant mortality (k<1)
66648 | 1 | 10 | >4.5h | LIB | CS | CISO | 2025 | 0 | 2 | 9 | Y | Y | arid | CISO | LIB | CS | 2024+ | 1 | 1 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 24 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 0.34651 | age_years | infant mortality (k<1)
66650 | 2 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 13 | 52 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 1254.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 59.1296 | age_years | infant mortality (k<1)
66659 | 1 | 10 | <1.5h | LIB | CS | CISO | 2025 | 0 | 97 | 97 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 2732.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 153.9137 | age_years | infant mortality (k<1)
66660 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 2132 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 120.0893 | age_years | infant mortality (k<1)
66661 | 0 | 8 | <1.5h | LIB | CS | CISO | 2025 | 0 | 99.4 | 99.4 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 2374.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 133.7486 | age_years | infant mortality (k<1)
66662 | 0 | 5 | <1.5h | LIB | CS | CISO | 2025 | 0 | 32 | 32 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 733 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 41.2877 | age_years | infant mortality (k<1)
66666 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 125 | 500 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 12549.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 591.5086 | age_years | infant mortality (k<1)
66669 | 1 | 17 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 25 | 100 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 2180.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 102.7758 | age_years | infant mortality (k<1)
66688 | 0 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 1 | 103.6 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 3953.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 261.7818 | age_years | infant mortality (k<1)
66690 | 1 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100 | 100 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 2817.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 186.5613 | age_years | infant mortality (k<1)
66694 | 0 | 14 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 300 | 1200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 34752 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 1414.817 | age_years | infant mortality (k<1)
66699 | 0 | 4 | <1.5h | LIB | CS | CISO | 2025 | 1 | 59.7 | 59.7 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 4105.5 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 231.2507 | age_years | infant mortality (k<1)
66716 | 4 | 26 | 2.5-4.5h | LIB | CS | SRP | 2023 | 0 | 100 | 400 | Y | Y | arid | other | LIB | CS | 2022-23 | 1 | 1 | 0.0074766 | ba_g+dur_band+vintage_g | 0 | 0.0074766 | 7273 | UNATTRIBUTED | inf | 0.085813 | 5.4106 | 0.019717 | 69.612 | age_years | infant mortality (k<1)
66717 | 0 | 22 | 2.5-4.5h | OTH | CS | CPLE | 2023 | 1 | 18 | 72 | N | N | inland | CPLE | other | CS | 2022-23 | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 0 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66726 | 0 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 70 | 200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 7330 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 345.4925 | age_years | infant mortality (k<1)
66727 | 1 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 149 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 1.2716 | age_years | infant mortality (k<1)
66728 | 2 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 0 | 5 | 10 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 135 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 1.1521 | age_years | infant mortality (k<1)
66757 | 1 | 14 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 6250 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 294.5877 | age_years | infant mortality (k<1)
66758 | 1 | 23 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 18.3 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 3258.5 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 88.5201 | age_years | infant mortality (k<1)
66764 | 0 | 23 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66765 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2020 | 1 | 2.5 | 10 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66767 | 0 | 24 | 2.5-4.5h | LIB | CS | NYIS | 2021 | 1 | 2.5 | 9.5 | N | N | inland | NYIS | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 25.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0032644 | age_years | infant mortality (k<1)
66772 | 0 | 22 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 28 | 112 | N | Y | inland | CISO | LIB | CS | 2022-23 | 0 | 1 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 2906 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 73.0063 | age_years | infant mortality (k<1)
66773 | 0 | 20 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 80 | 320 | N | Y | inland | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 7680.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 362.013 | age_years | infant mortality (k<1)
66782 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 174.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 11.5546 | age_years | infant mortality (k<1)
66783 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | coastal | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 107.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 7.1181 | age_years | infant mortality (k<1)
66784 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 124 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.2107 | age_years | infant mortality (k<1)
66788 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 134 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.8728 | age_years | infant mortality (k<1)
66789 | 1 | 23 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 127 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.4093 | age_years | infant mortality (k<1)
66790 | 0 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 197 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 13.0444 | age_years | infant mortality (k<1)
66791 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 168.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 11.1573 | age_years | infant mortality (k<1)
66792 | 0 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 94 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 6.2242 | age_years | infant mortality (k<1)
66794 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 101 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 6.6877 | age_years | infant mortality (k<1)
66795 | 1 | 18 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 145 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 9.6012 | age_years | infant mortality (k<1)
66799 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.7 | 1.3 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
66801 | 0 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 2294 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 155.7335 | age_years | infant mortality (k<1)
66804 | 1 | 17 | 1.5-2.5h | LIB | CT | ERCO | 2024 | 0 | 150 | 300 | N | Y | inland | ERCO | LIB | CT | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 10807 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 733.658 | age_years | infant mortality (k<1)
66807 | 0 | 24 | 2.5-4.5h | LIB | CS | CISO | 2023 | 1 | 3 | 12 | N | N | inland | CISO | LIB | CS | 2022-23 | 0 | 0 | 0.019625 | ba_g+dur_band+vintage_g | 0 | 0.019625 | 384 | UNATTRIBUTED | inf | 0.20982 | 5.4106 | 0.019717 | 9.6471 | age_years | infant mortality (k<1)
66814 | 0 | 21 | 2.5-4.5h | LIB | CS | PNM | 2024 | 1 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 5684.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 231.4263 | age_years | infant mortality (k<1)
66871 | 0 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 300 | 467 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 9676.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 656.9114 | age_years | infant mortality (k<1)
66872 | 0 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 158.3 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 4434 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 301.0123 | age_years | infant mortality (k<1)
66885 | 0 | 12 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 25 | 100 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 1544.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 72.7985 | age_years | infant mortality (k<1)
66890 | 0 | 1 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 38 | 152 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 4 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 0.18854 | age_years | infant mortality (k<1)
66905 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 100 | 157.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 2260 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 153.4253 | age_years | infant mortality (k<1)
66925 | 0 | 23 | <1.5h | LIB | BL | TEPC | 2023 | 1 | 20 | 20 | N | N | arid | other | LIB | BL | 2022-23 | 0 | 0 | 0.01875 | ba_g+dur_band+vintage_g | 0 | 0.01875 | 2244 | UNATTRIBUTED | inf | 0.20148 | 5.4106 | 0.019717 | 53.8627 | age_years | infant mortality (k<1)
66926 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | Y | inland | ERCO | LIB | CS | 2022-23 | 1 | 1 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 161.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 10.6874 | age_years | infant mortality (k<1)
66927 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 76 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 5.0294 | age_years | infant mortality (k<1)
66928 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 82.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 5.4595 | age_years | infant mortality (k<1)
66929 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 101 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 6.6838 | age_years | infant mortality (k<1)
66930 | 2 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 149 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 9.8602 | age_years | infant mortality (k<1)
66931 | 3 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 109.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 7.2463 | age_years | infant mortality (k<1)
66932 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 77.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 5.1286 | age_years | infant mortality (k<1)
66933 | 3 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 145.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 9.6286 | age_years | infant mortality (k<1)
66934 | 3 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 97.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 6.4521 | age_years | infant mortality (k<1)
66935 | 1 | 24 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 10 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 98.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 6.5183 | age_years | infant mortality (k<1)
66946 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 45 | 180 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 5659 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 266.7315 | age_years | infant mortality (k<1)
66949 | 2 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 40 | 160 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 4135 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 194.8992 | age_years | infant mortality (k<1)
66950 | 1 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 59 | 236 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 6534.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 307.9974 | age_years | infant mortality (k<1)
66951 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 150 | 600 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 9087 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 428.307 | age_years | infant mortality (k<1)
66966 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 0 | 2.1 | 4.3 | N | N | inland | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 40.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.1119 | age_years | infant mortality (k<1)
67019 | 0 | 16 | <1.5h | LIB | CS | ERCO | 2024 | 1 | 100 | 100 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 2238 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 148.1896 | age_years | infant mortality (k<1)
67036 | 1 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 76 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 1.5315 | age_years | infant mortality (k<1)
67037 | 0 | 13 | 1.5-2.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 5 | N | N | inland | PJM | LIB | CS | 2024+ | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 85 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 1.7129 | age_years | infant mortality (k<1)
67039 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 92 | 368 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 11494 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 541.7586 | age_years | infant mortality (k<1)
67040 | 1 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 103 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 8.6547 | age_years | infant mortality (k<1)
67041 | 1 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 15 | 30 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 145.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 12.2258 | age_years | infant mortality (k<1)
67042 | 1 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 10 | 20 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 91.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 7.6884 | age_years | infant mortality (k<1)
67043 | 1 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 48 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 4.0332 | age_years | infant mortality (k<1)
67044 | 1 | 13 | 1.5-2.5h | LIB | CS | CPLE | 2024 | 0 | 5 | 10 | N | N | coastal | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 58.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 4.9155 | age_years | infant mortality (k<1)
67083 | 1 | 16 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 174 | 407.4 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 9349 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 634.6783 | age_years | infant mortality (k<1)
67091 | 0 | 19 | 2.5-4.5h | LIB | CS | NEVP | 2024 | 1 | 85 | 340 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 10076 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 410.2123 | age_years | infant mortality (k<1)
67092 | 0 | 18 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 15 | 60 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 1518.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 71.573 | age_years | infant mortality (k<1)
67093 | 1 | 22 | <1.5h | LIB | CS | CISO | 2020 | 0 | 77 | 77 | N | Y | arid | CISO | LIB | CS | 2020-21 | 0 | 1 | 0.0025 | ba_g+dur_band+vintage_g | 0 | 0.0025 | 1735 | UNATTRIBUTED | inf | 0.029554 | 5.4106 | 0.019717 | 5.5527 | age_years | infant mortality (k<1)
67122 | 3 | 24 | 1.5-2.5h | LIB | CS | SWPP | 2023 | 0 | 1 | 2.4 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.017143 | ba_g+dur_band+vintage_g | 0 | 0.017143 | 46.5 | UNATTRIBUTED | inf | 0.18593 | 5.4106 | 0.019717 | 1.0205 | age_years | infant mortality (k<1)
67162 | 0 | 19 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 121 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.01549 | age_years | infant mortality (k<1)
67170 | 0 | 22 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 2.4 | 8.9 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 116 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 5.4675 | age_years | infant mortality (k<1)
67175 | 3 | 23 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 300 | 600 | Y | N | arid | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 13821 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 763.0446 | age_years | infant mortality (k<1)
67183 | 0 | 14 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 60 | 240 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 5888 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 239.7112 | age_years | infant mortality (k<1)
67185 | 0 | 18 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 2 | 8.9 | Y | N | inland | ISNE | LIB | CS | 2024+ | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 164.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.021059 | age_years | infant mortality (k<1)
67186 | 0 | 17 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 5 | 22.4 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 418 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.053511 | age_years | infant mortality (k<1)
67187 | 0 | 14 | 2.5-4.5h | LIB | CS | ISNE | 2024 | 0 | 3 | 8.9 | N | Y | inland | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 212.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.027203 | age_years | infant mortality (k<1)
67236 | 3 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 9298.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 631.25 | age_years | infant mortality (k<1)
67237 | 2 | 19 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 207.9 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 10541 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 715.6 | age_years | infant mortality (k<1)
67275 | 0 | 36 | 2.5-4.5h | LIB | CS | NYIS | 2022 | 1 | 1.3 | 5.1 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.019355 | ba_g+dur_band+vintage_g | 0 | 0.019355 | 0 | UNATTRIBUTED | inf | 0.20726 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
67278 | 0 | 3 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 1.1 | 2.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 2 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 0.093957 | age_years | infant mortality (k<1)
67281 | 0 | 20 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 1 | 4 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.026667 | ba_g+dur_band+vintage_g | 0 | 0.026667 | 0 | UNATTRIBUTED | inf | 0.27385 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
67282 | 0 | 18 | 1.5-2.5h | LIB | CS | NYIS | 2024 | 1 | 5 | 10.5 | N | N | inland | NYIS | LIB | CS | 2024+ | 0 | 0 | 0.015742 | dur_band+climate_region | 0 | 0.015742 | 0 | UNATTRIBUTED | inf | 0.17213 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
67284 | 0 | 22 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 70.5 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 3063.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 207.9727 | age_years | infant mortality (k<1)
67285 | 0 | 19 | 2.5-4.5h | LIB | CS | AZPS | 2024 | 1 | 215 | 860 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 23676 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 770.5698 | age_years | infant mortality (k<1)
67291 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 33868.5 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 1102.2995 | age_years | infant mortality (k<1)
67296 | 0 | 36 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 0.4 | 0.9 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 1 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 0.0085344 | age_years | infant mortality (k<1)
67299 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 100 | 400 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 10309 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 485.9048 | age_years | infant mortality (k<1)
67300 | 0 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 1052.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 42.8492 | age_years | infant mortality (k<1)
67301 | 0 | 20 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 823.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 33.5262 | age_years | infant mortality (k<1)
67302 | 2 | 15 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 723.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 29.455 | age_years | infant mortality (k<1)
67303 | 1 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 754 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 30.6967 | age_years | infant mortality (k<1)
67304 | 1 | 16 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 1109 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 45.1494 | age_years | infant mortality (k<1)
67305 | 0 | 18 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 1177.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 47.9382 | age_years | infant mortality (k<1)
67306 | 2 | 19 | 2.5-4.5h | LIB | CS | WACM | 2024 | 0 | 11.8 | 47 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 1210 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 49.2613 | age_years | infant mortality (k<1)
67307 | 1 | 18 | 2.5-4.5h | LIB | CS | PSCO | 2024 | 0 | 7.8 | 31.3 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 841 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 34.2386 | age_years | infant mortality (k<1)
67321 | 0 | 10 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 70 | 268 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 6484 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 211.0312 | age_years | infant mortality (k<1)
67323 | 0 | 9 | 1.5-2.5h | LIB | CS | PSCO | 2025 | 1 | 11.2 | 20 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 201 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 5.3607 | age_years | infant mortality (k<1)
67328 | 1 | 6 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 75 | 300 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 8034 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 261.4782 | age_years | infant mortality (k<1)
67454 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 170 | 680 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 20475 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 666.3886 | age_years | infant mortality (k<1)
67455 | 0 | 8 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 0 | 85 | 340 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 10185.5 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 331.5019 | age_years | infant mortality (k<1)
67474 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 300 | 1200 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 31962 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 1040.2497 | age_years | infant mortality (k<1)
67489 | 0 | 20 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 45 | 180 | Y | Y | inland | MISO | LIB | CS | 2024+ | 1 | 1 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 7351 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 348.5355 | age_years | infant mortality (k<1)
67493 | 1 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 129.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.5749 | age_years | infant mortality (k<1)
67494 | 0 | 20 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 126.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.3762 | age_years | infant mortality (k<1)
67495 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 174.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 11.5546 | age_years | infant mortality (k<1)
67496 | 0 | 17 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 164.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 10.8924 | age_years | infant mortality (k<1)
67498 | 1 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 185 | 740 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 16536 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 779.4084 | age_years | infant mortality (k<1)
67503 | 0 | 9 | 2.5-4.5h | LIB | CS | AZPS | 2025 | 1 | 213.8 | 855 | N | N | arid | AZPS | LIB | CS | 2024+ | 0 | 0 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 24594 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 800.4474 | age_years | infant mortality (k<1)
67545 | 0 | 14 | >4.5h | LIB | CS | MISO | 2024 | 1 | 5 | 30.6 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.012931 | dur_band+climate_region | 0 | 0.012931 | 521 | UNATTRIBUTED | inf | 0.14373 | 5.4106 | 0.019717 | 8.6245 | age_years | infant mortality (k<1)
67549 | 0 | 7 | 2.5-4.5h | LIB | CT | IPCO | 2025 | 0 | 150 | 600 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 17424 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 709.3627 | age_years | infant mortality (k<1)
67573 | 1 | 6 | 2.5-4.5h | FLB | CS | IPCO | 2025 | 0 | 82 | 328 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 9267 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 377.2764 | age_years | infant mortality (k<1)
67577 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2022 | 1 | 1 | 2.2 | N | N | inland | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 301.5 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 2.5731 | age_years | infant mortality (k<1)
67578 | 0 | 24 | 1.5-2.5h | LIB | CS | ISNE | 2023 | 1 | 2 | 4.6 | N | N | coastal | ISNE | LIB | CS | 2022-23 | 0 | 0 | 0.0066667 | ba_g+dur_band+vintage_g | 0 | 0.0066667 | 344 | UNATTRIBUTED | inf | 0.076884 | 5.4106 | 0.019717 | 2.9358 | age_years | infant mortality (k<1)
67579 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 0 | 82 | 328 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 8077.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 380.7252 | age_years | infant mortality (k<1)
67598 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 9219 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 625.853 | age_years | infant mortality (k<1)
67680 | 0 | 6 | >4.5h | LIB | CS | CISO | 2025 | 0 | 400 | 1800 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 20756.5 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 299.6803 | age_years | infant mortality (k<1)
67695 | 0 | 16 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 30 | 127 | Y | N | arid | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 1766 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 83.2387 | age_years | infant mortality (k<1)
67698 | 1 | 14 | 1.5-2.5h | LIB | CS | PGE | 2024 | 0 | 17 | 34 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 789.5 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 21.056 | age_years | infant mortality (k<1)
67710 | 0 | 5 | 2.5-4.5h | OTH | OT | PNM | 2025 | 1 | 57.8 | 231.4 | N | N | arid | other | other | other | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 5449 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 221.8387 | age_years | infant mortality (k<1)
67711 | 1 | 6 | 2.5-4.5h | LIB | CS | PGE | 2025 | 0 | 200 | 800 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 15765 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 641.8218 | age_years | infant mortality (k<1)
67712 | 1 | 13 | 2.5-4.5h | LIB | CS | PGE | 2024 | 0 | 75 | 300 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 6637.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 270.2247 | age_years | infant mortality (k<1)
67721 | 2 | 14 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 100.3 | 145 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 3587 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 237.5139 | age_years | infant mortality (k<1)
67734 | 2 | 9 | 2.5-4.5h | LIB | CT | CISO | 2025 | 0 | 200 | 800 | Y | Y | arid | CISO | LIB | CT | 2024+ | 1 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 22863 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 1077.6255 | age_years | infant mortality (k<1)
67736 | 1 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 279 | 1116 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 32710 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 1541.7543 | age_years | infant mortality (k<1)
67737 | 1 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 304 | 440.8 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 10426 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 690.3596 | age_years | infant mortality (k<1)
67738 | 1 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 204 | 298 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 6925 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 458.5402 | age_years | infant mortality (k<1)
67739 | 1 | 13 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 120 | 174 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 4031 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 266.9134 | age_years | infant mortality (k<1)
67740 | 1 | 6 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 240 | 480 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 12535 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 850.9672 | age_years | infant mortality (k<1)
67743 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2022 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 0 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
67745 | 0 | 24 | <1.5h | LIB | CS | NYIS | 2022 | 1 | 5 | 2 | N | N | coastal | NYIS | LIB | CS | 2022-23 | 0 | 0 | 0.029655 | dur_band+climate_region | 0 | 0.029655 | 0 | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
67752 | 0 | 7 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 102.6 | 205.1 | Y | N | arid | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 7793 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 529.0457 | age_years | infant mortality (k<1)
67758 | 2 | 11 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 14 | 56 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 835 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 39.5901 | age_years | infant mortality (k<1)
67762 | 0 | 15 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 1 | 72.2 | 115 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 2744 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 186.2827 | age_years | infant mortality (k<1)
67764 | 0 | 5 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 117 | 472 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 11958 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 563.6288 | age_years | infant mortality (k<1)
67828 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 25 | 100 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 2611 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 123.067 | age_years | infant mortality (k<1)
67829 | 0 | 8 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 20 | 80 | N | N | arid | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 2208.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 104.0955 | age_years | infant mortality (k<1)
67843 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 498 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 33.8079 | age_years | infant mortality (k<1)
67845 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 454 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 30.8208 | age_years | infant mortality (k<1)
67850 | 0 | 1 | 2.5-4.5h | LIB | CS | IID | 2025 | 1 | 35 | 140 | N | Y | arid | other | LIB | CS | 2024+ | 0 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 399 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 16.244 | age_years | infant mortality (k<1)
67851 | 0 | 14 | <1.5h | LIB | CS | PJM | 2024 | 0 | 20 | 20 | N | Y | inland | PJM | LIB | CS | 2024+ | 0 | 1 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 2762.5 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 75.0458 | age_years | infant mortality (k<1)
67855 | 2 | 15 | 2.5-4.5h | LIB | CS | AZPS | 2024.59 | 0 | 200 | 808.4 | N | Y | arid | AZPS | LIB | CS | 2024+ | 0 | 1 | 0.025424 | ba_g+dur_band+vintage_g | 0 | 0.025424 | 11719.5 | UNATTRIBUTED | inf | 0.26294 | 5.4106 | 0.019717 | 381.4281 | age_years | infant mortality (k<1)
67860 | 2 | 21 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 6750 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 458.2392 | age_years | infant mortality (k<1)
67861 | 0 | 17 | 1.5-2.5h | OTH | CS | ERCO | 2024 | 0 | 125 | 250 | N | Y | inland | ERCO | other | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 6402.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 434.6484 | age_years | infant mortality (k<1)
67869 | 1 | 13 | 2.5-4.5h | LIB | CT | PGE | 2024 | 0 | 200 | 800 | N | N | inland | other | LIB | CT | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 21922.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 892.5048 | age_years | infant mortality (k<1)
67880 | 1 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 5 | 21.7 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.026667 | ba_g+dur_band+vintage_g | 0 | 0.026667 | 10.5 | UNATTRIBUTED | inf | 0.27385 | 5.4106 | 0.019717 | 0.35844 | age_years | infant mortality (k<1)
67882 | 0 | 12 | 2.5-4.5h | LIB | CS | NYIS | 2025 | 0 | 10 | 43.4 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.026667 | ba_g+dur_band+vintage_g | 0 | 0.026667 | 32.5 | UNATTRIBUTED | inf | 0.27385 | 5.4106 | 0.019717 | 1.1095 | age_years | infant mortality (k<1)
67883 | 1 | 14 | 2.5-4.5h | LIB | CS | NYIS | 2024 | 0 | 8 | 34.1 | Y | N | coastal | NYIS | LIB | CS | 2024+ | 1 | 0 | 0.026667 | ba_g+dur_band+vintage_g | 0 | 0.026667 | 38 | UNATTRIBUTED | inf | 0.27385 | 5.4106 | 0.019717 | 1.2972 | age_years | infant mortality (k<1)
67886 | 1 | 24 | 2.5-4.5h | NIB | CS | NYIS | 2023 | 0 | 3 | 12.4 | Y | N | coastal | NYIS | other | CS | 2022-23 | 1 | 0 | 0.019355 | ba_g+dur_band+vintage_g | 0 | 0.019355 | 8 | UNATTRIBUTED | inf | 0.20726 | 5.4106 | 0.019717 | 0.19822 | age_years | infant mortality (k<1)
67893 | 0 | 12 | 2.5-4.5h | LIB | CS | MISO | 2025 | 1 | 56.3 | 225 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 9601.5 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 455.2393 | age_years | infant mortality (k<1)
67898 | 0 | 1 | 2.5-4.5h | LIB | CS | NEVP | 2025 | 1 | 100 | 400 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 8671 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 353.0122 | age_years | infant mortality (k<1)
67899 | 0 | 24 | <1.5h | LIB | CS | PJM | 2021 | 0 | 6.2 | 6.2 | N | N | coastal | PJM | LIB | CS | 2020-21 | 0 | 0 | 0.029655 | dur_band+climate_region | 0 | 0.029655 | 735.5 | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 | 27.9221 | age_years | infant mortality (k<1)
67905 | 0 | 6 | 2.5-4.5h | LIB | CS | TEPC | 2025 | 0 | 200 | 800 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 23941 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 974.6816 | age_years | infant mortality (k<1)
67931 | 1 | 4 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 113.5 | 454 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 7553.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 356.0269 | age_years | infant mortality (k<1)
67948 | 0 | 24 | >4.5h | LIB | CS | SWPP | 2022 | 0 | 1.8 | 9.1 | N | N | inland | other | LIB | CS | 2022-23 | 0 | 0 | 0.012931 | dur_band+climate_region | 0 | 0.012931 | 28 | UNATTRIBUTED | inf | 0.14373 | 5.4106 | 0.019717 | 0.46351 | age_years | infant mortality (k<1)
67963 | 2 | 9 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 125 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.2769 | age_years | infant mortality (k<1)
67968 | 1 | 9 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 4356 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 295.7171 | age_years | infant mortality (k<1)
67973 | 0 | 3 | <1.5h | LIB | BL | AZPS | 2025 | 0 | 113 | 113 | N | N | arid | AZPS | LIB | BL | 2024+ | 0 | 0 | 0.030215 | dur_band+climate_region | 0 | 0.030215 | 9962 | UNATTRIBUTED | inf | 0.30412 | 5.4106 | 0.019717 | 385.3305 | age_years | infant mortality (k<1)
68012 | 1 | 9 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 99.7 | 398.8 | N | Y | coastal | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 12581 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 592.9933 | age_years | infant mortality (k<1)
68023 | 0 | 2 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 16.7 | 64 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 955.5 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 45.0366 | age_years | infant mortality (k<1)
68058 | 2 | 13 | >4.5h | OTH | CS | WACM | 2024 | 0 | 35.4 | 235 | N | N | arid | other | other | CS | 2024+ | 0 | 0 | 0.011278 | dur_band+climate_region | 0 | 0.011278 | 1684.5 | UNATTRIBUTED | inf | 0.12658 | 5.4106 | 0.019717 | 24.3206 | age_years | infant mortality (k<1)
68064 | 0 | 17 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 1.2 | 2.1 | Y | N | inland | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 175.5 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 8.2447 | age_years | infant mortality (k<1)
68069 | 0 | 24 | <1.5h | LIB | CT | ISNE | 2022 | 1 | 2 | 2.2 | N | N | inland | ISNE | LIB | CT | 2022-23 | 0 | 0 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 31.5 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.13577 | age_years | infant mortality (k<1)
68146 | 2 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 4583 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 311.1275 | age_years | infant mortality (k<1)
68147 | 0 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 45.5 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 2.1573 | age_years | infant mortality (k<1)
68148 | 0 | 13 | 2.5-4.5h | LIB | CS | MISO | 2024 | 1 | 2 | 8 | N | N | inland | MISO | LIB | CS | 2024+ | 0 | 0 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 43 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 2.0388 | age_years | infant mortality (k<1)
68189 | 1 | 11 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 249.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 2254 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 153.018 | age_years | infant mortality (k<1)
68266 | 0 | 24 | 1.5-2.5h | LIB | CS | CISO | 2019 | 1 | 0.3 | 0.5 | N | Y | inland | CISO | LIB | CS | <=2019 | 0 | 1 | 0.013423 | ba_g+dur_band+vintage_g | 0 | 0.013423 | 5.5 | UNATTRIBUTED | inf | 0.14877 | 5.4106 | 0.019717 | 0.094508 | age_years | infant mortality (k<1)
68322 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 300 | 1200 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 3358 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 158.2761 | age_years | infant mortality (k<1)
68324 | 0 | 3 | 2.5-4.5h | LIB | CS | CISO | 2025 | 0 | 150 | 600 | N | Y | arid | CISO | LIB | CS | 2024+ | 0 | 1 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 1833 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 86.3967 | age_years | infant mortality (k<1)
68335 | 0 | 16 | 2.5-4.5h | LIB | CS | PJM | 2024 | 0 | 2.5 | 7.1 | N | Y | coastal | PJM | LIB | CS | 2024+ | 0 | 1 | 0.024635 | dur_band+climate_region | 0 | 0.024635 | 0 | UNATTRIBUTED | inf | 0.25593 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
68423 | 0 | 4 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 100 | 200 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 5663.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 384.4797 | age_years | infant mortality (k<1)
68424 | 1 | 7 | 2.5-4.5h | LIB | CS | MISO | 2025 | 0 | 104.9 | 400 | N | Y | inland | MISO | LIB | CS | 2024+ | 0 | 1 | 0.037037 | ba_g+dur_band+vintage_g | 0 | 0.037037 | 7156 | UNATTRIBUTED | inf | 0.35882 | 5.4106 | 0.019717 | 339.2899 | age_years | infant mortality (k<1)
68475 | 1 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 58 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 1.2916 | age_years | infant mortality (k<1)
68476 | 1 | 8 | 1.5-2.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 11.2 | N | N | coastal | ISNE | LIB | CS | 2024+ | 0 | 0 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 58 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 1.2916 | age_years | infant mortality (k<1)
68493 | 3 | 24 | <1.5h | LIB | CS | ISNE | 2020.8182 | 0 | 3.3 | 3.3 | N | N | industrial | ISNE | LIB | CS | 2020-21 | 0 | 0 | 0.041667 | ba_g+dur_band+vintage_g | 0 | 0.041667 | 87.5 | UNATTRIBUTED | inf | 0.39347 | 5.4106 | 0.019717 | 4.6673 | age_years | infant mortality (k<1)
68496 | 1 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 60 | 120 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 1722 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 116.9019 | age_years | infant mortality (k<1)
68522 | 0 | 9 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 0 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
68523 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 0 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
68524 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 3 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 0.14094 | age_years | infant mortality (k<1)
68525 | 0 | 6 | 1.5-2.5h | LIB | CS | CISO | 2025 | 1 | 0.5 | 1.1 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 0 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
68547 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 94 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 4.4306 | age_years | infant mortality (k<1)
68548 | 0 | 13 | 2.5-4.5h | LIB | CS | CISO | 2024 | 1 | 0.7 | 2.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 52 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 2.451 | age_years | infant mortality (k<1)
68576 | 1 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 260 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 6390 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 260.1485 | age_years | infant mortality (k<1)
68577 | 2 | 8 | 2.5-4.5h | LIB | CS | SWPP | 2025 | 0 | 40 | 160 | Y | N | inland | other | LIB | CS | 2024+ | 1 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 4343.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 176.8318 | age_years | infant mortality (k<1)
68596 | 0 | 1 | 2.5-4.5h | LIB | CS | PACE | 2025 | 0 | 200 | 800 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 2851 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 116.0694 | age_years | infant mortality (k<1)
68605 | 0 | 24 | 2.5-4.5h | LIB | CS | HECO | 2021 | 1 | 0.5 | 1.3 | N | N | coastal | other | LIB | CS | 2020-21 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 9 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0011521 | age_years | infant mortality (k<1)
68611 | 0 | 10 | 1.5-2.5h | LIB | CS | CEA | 2024 | 0 | 40 | 80 | N | N | coastal | other | LIB | CS | 2024+ | 0 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 1 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 0.02667 | age_years | infant mortality (k<1)
68613 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 228.7 | 228.7 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 5939 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 393.252 | age_years | infant mortality (k<1)
68617 | 0 | 2 | 2.5-4.5h | LIB | CT | PNM | 2025 | 0 | 100 | 400 | N | N | arid | other | LIB | CT | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 11974.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 487.5036 | age_years | infant mortality (k<1)
68679 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 45.5 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.19612 | age_years | infant mortality (k<1)
68680 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 2.5 | 2.5 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 50 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.21552 | age_years | infant mortality (k<1)
68683 | 3 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 337.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 22.912 | age_years | infant mortality (k<1)
68684 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 24.8 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 386.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 26.2384 | age_years | infant mortality (k<1)
68685 | 3 | 12 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 10 | 12.4 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 216 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 14.3025 | age_years | infant mortality (k<1)
68686 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 33 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 2.2403 | age_years | infant mortality (k<1)
68687 | 2 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 24.7 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 43.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 2.9531 | age_years | infant mortality (k<1)
68742 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3 | 3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 50 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.21552 | age_years | infant mortality (k<1)
68743 | 0 | 24 | <1.5h | LIB | CS | ISNE | 2022 | 1 | 3.3 | 3.3 | N | Y | inland | ISNE | LIB | CS | 2022-23 | 0 | 1 | 0.003367 | ba_g+dur_band+vintage_g | 0 | 0.003367 | 119 | UNATTRIBUTED | inf | 0.039599 | 5.4106 | 0.019717 | 0.51293 | age_years | infant mortality (k<1)
68773 | 0 | 23 | 1.5-2.5h | LIB | CS | ISNE | 2021 | 1 | 1.3 | 2.8 | N | Y | coastal | ISNE | LIB | CS | 2020-21 | 0 | 1 | 0.0021583 | ba_g+dur_band+vintage_g | 0 | 0.0021583 | 68.5 | UNATTRIBUTED | inf | 0.025567 | 5.4106 | 0.019717 | 0.18926 | age_years | infant mortality (k<1)
68801 | 0 | 3 | 2.5-4.5h | LIB | CS | WALC | 2025 | 0 | 50 | 200 | N | N | arid | other | LIB | CS | 2024+ | 0 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 239 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 9.7301 | age_years | infant mortality (k<1)
68802 | 0 | 8 | <1.5h | LIB | CS | SWPP | 2025 | 0 | 65 | 65 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 8224 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 223.4123 | age_years | infant mortality (k<1)
68809 | 0 | 3 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 220 | 440 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 189 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 12.8307 | age_years | infant mortality (k<1)
68816 | 0 | 20 | 1.5-2.5h | LIB | CS | CISO | 2024 | 1 | 2.6 | 5.3 | Y | N | coastal | CISO | LIB | CS | 2024+ | 1 | 0 | 0.036697 | ba_g+dur_band+vintage_g | 0 | 0.036697 | 21.5 | UNATTRIBUTED | inf | 0.3562 | 5.4106 | 0.019717 | 1.01 | age_years | infant mortality (k<1)
68842 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 150 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 7672 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 508.003 | age_years | infant mortality (k<1)
68868 | 0 | 5 | 2.5-4.5h | LIB | CS | PNM | 2025 | 1 | 50 | 200 | Y | N | arid | other | LIB | CS | 2024+ | 1 | 0 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 5754 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 234.2558 | age_years | infant mortality (k<1)
68874 | 1 | 8 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 13 | 45 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 1183 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 16.674 | age_years | infant mortality (k<1)
68875 | 0 | 7 | 2.5-4.5h | LIB | CS | ISNE | 2025 | 0 | 5 | 22.4 | N | Y | coastal | ISNE | LIB | CS | 2024+ | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 334 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.042757 | age_years | infant mortality (k<1)
68878 | 0 | 9 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 165 | 165 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 6053 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 400.8006 | age_years | infant mortality (k<1)
68879 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 150 | 300 | N | Y | coastal | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 5874 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 398.77 | age_years | infant mortality (k<1)
68891 | 0 | 6 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 1 | 3.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 84 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 3.9593 | age_years | infant mortality (k<1)
68895 | 1 | 8 | <1.5h | LIB | CS | ERCO | 2023 | 0 | 236.3 | 236.3 | Y | N | inland | ERCO | LIB | CS | 2022-23 | 1 | 0 | 0.051693 | ba_g+dur_band+vintage_g | 0 | 0.051693 | 4965.5 | UNATTRIBUTED | inf | 0.46223 | 5.4106 | 0.019717 | 328.5962 | age_years | infant mortality (k<1)
68896 | 1 | 8 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 123.3 | 123 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 3260.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 215.8946 | age_years | infant mortality (k<1)
68906 | 0 | 1 | <1.5h | LIB | CS | DOPD | 2025 | 1 | 200 | 200 | N | Y | inland | other | LIB | CS | 2024+ | 0 | 1 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 9840 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 267.3124 | age_years | infant mortality (k<1)
68912 | 0 | 6 | 2.5-4.5h | LIB | CS | ERCO | 2025 | 0 | 50 | 200 | Y | Y | inland | ERCO | LIB | CS | 2024+ | 1 | 1 | 0.01101 | dur_band+climate_region | 0 | 0.01101 | 1967 | UNATTRIBUTED | inf | 0.12376 | 5.4106 | 0.019717 | 27.7241 | age_years | infant mortality (k<1)
68997 | 0 | 7 | 2.5-4.5h | LIB | CS | CISO | 2025 | 1 | 0.7 | 2.6 | N | N | coastal | CISO | LIB | CS | 2024+ | 0 | 0 | 0.036819 | ba_g+dur_band+vintage_g | 0 | 0.036819 | 55 | UNATTRIBUTED | inf | 0.35714 | 5.4106 | 0.019717 | 2.5924 | age_years | infant mortality (k<1)
69023 | 0 | 2 | 1.5-2.5h | LIB | CS | CPLE | 2025 | 0 | 100 | 200 | N | N | inland | CPLE | LIB | CS | 2024+ | 0 | 0 | 0.065637 | ba_g+dur_band+vintage_g | 0 | 0.065637 | 2900.5 | UNATTRIBUTED | inf | 0.54509 | 5.4106 | 0.019717 | 243.7173 | age_years | infant mortality (k<1)
69026 | 0 | 2 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 283.2 | 283.2 | Y | N | inland | ERCO | LIB | CS | 2024+ | 1 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 13663 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 904.6982 | age_years | infant mortality (k<1)
69045 | 0 | 5 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 200 | 400 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 10338 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 701.8189 | age_years | infant mortality (k<1)
69122 | 0 | 4 | <1.5h | LIB | CS | PSCO | 2025 | 0 | 100 | 100 | N | N | inland | other | LIB | CS | 2024+ | 0 | 0 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 11212 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 304.584 | age_years | infant mortality (k<1)
69128 | 1 | 12 | 1.5-2.5h | LIB | CS | PJM | 2023 | 0 | 1.1 | 2.3 | N | Y | coastal | PJM | LIB | CS | 2022-23 | 0 | 1 | 0.017396 | dur_band+climate_region | 0 | 0.017396 | 58 | UNATTRIBUTED | inf | 0.1884 | 5.4106 | 0.019717 | 1.2916 | age_years | infant mortality (k<1)
69171 | 0 | 2 | 2.5-4.5h | LIB | CS | DUK | 2025 | 0 | 50 | 200 | Y | Y | inland | other | LIB | CS | 2024+ | 1 | 1 | 0.031802 | ba_g+dur_band+vintage_g | 0 | 0.031802 | 5839.5 | UNATTRIBUTED | inf | 0.31725 | 5.4106 | 0.019717 | 237.7366 | age_years | infant mortality (k<1)
69187 | 0 | 1 | 1.5-2.5h | LIB | CS | TEC | 2019 | 1 | 12.6 | 25.2 | Y | N | coastal | other | LIB | CS | <=2019 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 24 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0030724 | age_years | infant mortality (k<1)
69190 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | Y | N | coastal | CISO | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 4 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00051206 | age_years | infant mortality (k<1)
69191 | 0 | 12 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.2 | 0.4 | N | N | coastal | CISO | LIB | CS | 2022-23 | 0 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 8 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.0010241 | age_years | infant mortality (k<1)
69210 | 0 | 12 | 1.5-2.5h | LIB | CS | PGE | 2024 | 1 | 1 | 2 | Y | N | industrial | other | LIB | CS | 2024+ | 1 | 0 | 0.020833 | ba_g+dur_band+vintage_g | 0 | 0.020833 | 6.5 | UNATTRIBUTED | inf | 0.2212 | 5.4106 | 0.019717 | 0.17336 | age_years | infant mortality (k<1)
69244 | 0 | 8 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 58.3 | 114 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 2411.5 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 163.7102 | age_years | infant mortality (k<1)
69250 | 1 | 8 | <1.5h | NAB | CS | FPC | 2025 | 0 | 5 | 5 | N | Y | inland | other | other | CS | 2024+ | 0 | 1 | 0.021221 | dur_band+climate_region | 0 | 0.021221 | 424 | UNATTRIBUTED | inf | 0.22481 | 5.4106 | 0.019717 | 11.5183 | age_years | infant mortality (k<1)
69288 | 0 | 10 | 1.5-2.5h | LIB | CS | CISO | 2023 | 1 | 0.3 | 0.6 | Y | N | arid | CISO | LIB | CS | 2022-23 | 1 | 0 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 7.5 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.00096012 | age_years | infant mortality (k<1)
69298 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 0 | 300 | 680 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 23114 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 1569.1469 | age_years | infant mortality (k<1)
69300 | 1 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 0 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
69301 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 20 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 1.3243 | age_years | infant mortality (k<1)
69302 | 1 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 88 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 5.8269 | age_years | infant mortality (k<1)
69331 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | arid | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 8 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 0.52972 | age_years | infant mortality (k<1)
69333 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 20 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 1.3243 | age_years | infant mortality (k<1)
69334 | 0 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2020 | 0 | 2.3 | 4.5 | N | N | inland | ERCO | LIB | CS | 2020-21 | 0 | 0 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 18 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 1.0333 | age_years | infant mortality (k<1)
69344 | 0 | 10 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 2 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 0.13243 | age_years | infant mortality (k<1)
69345 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 189.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 12.5478 | age_years | infant mortality (k<1)
69346 | 0 | 7 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 187 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 12.3822 | age_years | infant mortality (k<1)
69347 | 0 | 6 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 221.5 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 14.6667 | age_years | infant mortality (k<1)
69348 | 1 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | coastal | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 47 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 3.1121 | age_years | infant mortality (k<1)
69349 | 0 | 11 | <1.5h | LIB | CS | ERCO | 2024 | 0 | 9.9 | 9.9 | N | N | inland | ERCO | LIB | CS | 2024+ | 0 | 0 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 39 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 2.5824 | age_years | infant mortality (k<1)
69350 | 2 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 10 | 23.2 | N | Y | arid | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 368.5 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 20.3445 | age_years | infant mortality (k<1)
69353 | 1 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2023 | 0 | 9.9 | 19.8 | N | Y | inland | ERCO | LIB | CS | 2022-23 | 0 | 1 | 0.043127 | ba_g+dur_band+vintage_g | 0 | 0.043127 | 109.5 | UNATTRIBUTED | inf | 0.404 | 5.4106 | 0.019717 | 6.0454 | age_years | infant mortality (k<1)
69358 | 0 | 3 | <1.5h | LIB | CS | CISO | 2025 | 0 | 11.3 | 11.9 | N | N | inland | CISO | LIB | CS | 2024+ | 0 | 0 | 0.044 | ba_g+dur_band+vintage_g | 0 | 0.044 | 0 | UNATTRIBUTED | inf | 0.41022 | 5.4106 | 0.019717 | 0 | age_years | infant mortality (k<1)
69365 | 0 | 3 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 206 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 13.6403 | age_years | infant mortality (k<1)
69366 | 1 | 12 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 10 | 10 | N | Y | industrial | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 122 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 8.0783 | age_years | infant mortality (k<1)
69407 | 1 | 7 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 75 | 75 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 2149 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 142.2965 | age_years | infant mortality (k<1)
69411 | 2 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 300 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 17.2219 | age_years | infant mortality (k<1)
69413 | 2 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | inland | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 391 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 22.4459 | age_years | infant mortality (k<1)
69414 | 0 | 1 | 1.5-2.5h | LIB | CS | ERCO | 2025 | 1 | 180 | 360 | N | Y | inland | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 3630 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 246.4309 | age_years | infant mortality (k<1)
69415 | 2 | 12 | 1.5-2.5h | LIB | CS | ERCO | 2021 | 0 | 10 | 20 | N | Y | arid | ERCO | LIB | CS | 2020-21 | 0 | 1 | 0.044843 | ba_g+dur_band+vintage_g | 0 | 0.044843 | 437 | UNATTRIBUTED | inf | 0.41615 | 5.4106 | 0.019717 | 25.0866 | age_years | infant mortality (k<1)
69454 | 0 | 9 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 561 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 38.0848 | age_years | infant mortality (k<1)
69456 | 1 | 8 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 418 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 28.3769 | age_years | infant mortality (k<1)
69459 | 0 | 5 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 369 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 25.0504 | age_years | infant mortality (k<1)
69460 | 0 | 12 | 1.5-2.5h | LIB | OT | ERCO | 2025 | 0 | 12 | 20.9 | N | Y | coastal | ERCO | LIB | other | 2024+ | 0 | 1 | 0.05303 | ba_g+dur_band+vintage_g | 0 | 0.05303 | 478 | UNATTRIBUTED | inf | 0.47079 | 5.4106 | 0.019717 | 32.4501 | age_years | infant mortality (k<1)
69576 | 1 | 8 | <1.5h | LIB | CS | ERCO | 2025 | 0 | 9.9 | 13.7 | N | Y | arid | ERCO | LIB | CS | 2024+ | 0 | 1 | 0.051724 | ba_g+dur_band+vintage_g | 0 | 0.051724 | 215 | UNATTRIBUTED | inf | 0.46243 | 5.4106 | 0.019717 | 14.2363 | age_years | infant mortality (k<1)
69727 | 0 | 12 | <1.5h | LIB | CS | PJM | 2022 | 1 | 10.1 | 10.1 | N | Y | inland | PJM | LIB | CS | 2022-23 | 0 | 1 | 0 | ba_g+dur_band+vintage_g | 0 | 0.0001 | 98 | UNATTRIBUTED | inf | 0.0011993 | 5.4106 | 0.019717 | 0.012546 | age_years | infant mortality (k<1)
69803 | 1 | 7 | <1.5h | LIB | CT | NYIS | 2025 | 0 | 4.6 | 4.6 | N | N | coastal | NYIS | LIB | CT | 2024+ | 0 | 0 | 0.029655 | dur_band+climate_region | 0 | 0.029655 | 126 | UNATTRIBUTED | inf | 0.29943 | 5.4106 | 0.019717 | 4.7834 | age_years | infant mortality (k<1)

## episode_length
signature | L_bar
AUGMENTATION | 1
CAPACITY_FADE | 10.5
CELL_DEGRADATION | 4.7349
FULL_OUTAGE | 6.1162
HYBRID_ARTEFACT | 17.2604
PARTIAL_AVAILABILITY | 2.3101
THERMAL_AUX | 9.7549
UNATTRIBUTED | 5.4106
UNDER_DISPATCH | 4.809

## hybrid_quarantine
plant_id | plant_name | state | hybrid_reasons
141 | Agua Fria | AZ | rte_gt_1,pv_same_plant
260 | Dynegy Moss Landing Power Plant Hybrid | CA | rte_gt_1
645 | Big Bend | FL | pv_same_plant
1016 | Butler-Warner Generation Plant | NC | pv_same_plant
2830 | Walter C Beckjord | OH | rte_gt_1
6304 | Kotzebue Hybrid | AK | colocated_firming,pv_same_plant
6377 | Ocracoke Hybrid | NC | rte_gt_1
10444 | Lockhart Solar PV, LLC | CA | pv_same_plant
50064 | University of California Santa Cruz | CA | colocated_firming,pv_same_plant
54296 | Biola University Hybrid | CA | rte_gt_1
56981 | Pyron Wind Farm LLC Hybrid | TX | rte_gt_1
57082 | Kaheawa Wind Power II LLC | HI | colocated_firming
57242 | Mililani South Solar Farm | HI | rte_gt_1,pv_same_plant
57325 | FPL Energy Illinois Wind LLC Hybrid | IL | rte_gt_1
57560 | Chino Valley Solar | AZ | pv_same_plant
57561 | Cotton Center Solar Hybrid | AZ | pv_same_plant
57562 | Paloma Solar Hybrid | AZ | pv_same_plant
57563 | Hyder Solar Hybrid | AZ | pv_same_plant
57693 | DOE Golden NWTC Research Side Hybrid | CO | pv_same_plant
57997 | Foothills Solar Plant Hybrid | AZ | pv_same_plant
58236 | Marshalltown Generating Station | IA | colocated_firming,pv_same_plant
58256 | Los Alamos PV Site | NM | pv_same_plant
58383 | Hyder II Hybrid | AZ | pv_same_plant
58405 | ESS Battery Microgrid | AK | colocated_firming
58462 | McCoy Solar Energy Project Hybrid | CA | pv_same_plant
58537 | OCI Alamo Solar I Hybrid | TX | rte_gt_1,pv_same_plant
58585 | Sierra Nevada Brewing Co Hybrid | CA | pv_same_plant
58625 | Santa Rita Jail Hybrid | CA | pv_same_plant
58639 | KRS I Anahola Solar Hybrid | HI | colocated_firming,pv_same_plant
58640 | KRS II Koloa Solar | HI | pv_same_plant
58899 | Prosperity Energy Storage Facility Hybri | NM | pv_same_plant
59020 | Gila Bend Hybrid | AZ | pv_same_plant
59150 | RE Mustang LLC | CA | pv_same_plant
59296 | Northwest Ohio Wind | OH | colocated_firming,pv_same_plant,dc_tight
59444 | Desert Star Hybrid | AZ | pv_same_plant
59871 | Desert Quartzite | CA | pv_same_plant
59939 | RE Tranquillity | CA | pv_same_plant,dc_coupled
59957 | Grand Ridge Battery Projects | IL | rte_gt_1,dc_coupled
59966 | Camp Lejeune Solar and Energy Storage | NC | pv_same_plant
59993 | Babcock Solar Energy Center Hybrid | FL | rte_gt_1,colocated_firming,pv_same_plant
60014 | Manatee Solar Energy Center | FL | pv_same_plant
60061 | Citrus Solar Energy Center Hybrid | FL | rte_gt_1,colocated_firming,pv_same_plant,dc_tight
60092 | Blythe Solar II, LLC | CA | pv_same_plant
60093 | Blythe Solar 110, LLC | CA | pv_same_plant
60094 | Blythe Solar III, LLC Hybrid | CA | pv_same_plant
60095 | Blythe Solar IV, LLC | CA | pv_same_plant
60123 | Castle Gap Solar Hybrid | TX | pv_same_plant
60231 | Genentech-Oceanside Hybrid | CA | pv_same_plant
60233 | RE Garland | CA | pv_same_plant,dc_coupled
60299 | HMV Minster Energy Storage System | OH | rte_gt_1
60316 | Scott Solar Farm | VA | pv_same_plant
60390 | Beech Ridge Energy Storage | WV | dc_coupled
60441 | Salem Smart Power Center | OR | colocated_firming,dc_coupled
60467 | Red Rock | AZ | pv_same_plant
60491 | Springbok 3 Solar Farm Hybrid | CA | pv_same_plant,dc_coupled
60506 | ETT Presidio NaS Battery | TX | rte_gt_1
60518 | Stafford Hill Solar Hybrid | VT | rte_gt_1,pv_same_plant,dc_coupled
60546 | KIUC Kapaia PV and BA Storage Project Hy | HI | pv_same_plant
60561 | Cedartown Battery Energy Storage Project | GA | colocated_firming
60562 | GMP Solar - Panton Hybrid | VT | rte_gt_1,pv_same_plant,dc_coupled
60565 | Borrego Springs Energy Storage | CA | rte_gt_1
60566 | Pala Energy Storage Yard | CA | rte_gt_1
60567 | Ortega Highway Energy Storage | CA | rte_gt_1
60568 | Canyon Crest Academy | CA | rte_gt_1
60607 | CMEEC - Polaris Park Solar Hybrid | CT | pv_same_plant
60609 | CMEEC - Norwich Stott St Solar Hybrid | CT | rte_gt_1,pv_same_plant
60654 | Townsite Solar Project Hybrid | NV | colocated_firming,pv_same_plant
60698 | Stanton Energy Reliability Center Hybrid | CA | rte_gt_1
60791 | SunAnza | CA | colocated_firming,pv_same_plant
60815 | Hampshire College Hybrid | MA | pv_same_plant
60906 | Mt. Tom Solar Project Hybrid | MA | pv_same_plant,dc_coupled
60959 | Chocksett Rd Energy Storage Project | MA | rte_gt_1
60964 | Apache Solar I | AZ | pv_same_plant
60974 | Glendale Battery Energy Storage System | CA | rte_gt_1
60996 | Iron Horse Battery Storage Hybrid | AZ | pv_same_plant
61068 | AES Lawai Solar Hybrid | HI | rte_gt_1,pv_same_plant,dc_tight
61098 | Battle Mountain Solar Project | NV | rte_gt_1,pv_same_plant,dc_coupled
61107 | Vanadium Redox Flow Battery Plant | CA | colocated_firming
61168 | Eland Solar & Storage Center, Phase 1 Hy | CA | pv_same_plant
61169 | Eland Solar & Storage Center, Phase 2 Hy | CA | pv_same_plant
61197 | Pima Energy Storage System | AZ | rte_gt_1
61334 | Volkman Road Solar Array Hybrid | IN | pv_same_plant
61431 | Beacon BESS 1 | CA | colocated_firming
61439 | Panasonic Carport Solar Hybrid | CO | rte_gt_1,pv_same_plant
61446 | RE Gaskell West 2 LLC | CA | pv_same_plant
61473 | Hopewell Valley High School Hybrid | NJ | colocated_firming,pv_same_plant
61552 | Fort Detrick Solar PV | MD | pv_same_plant,dc_coupled
61647 | ENO Paterson Solar | LA | colocated_firming,pv_same_plant
61667 | Wimauma Solar and Battery Storage | FL | colocated_firming,pv_same_plant
61678 | Pinal Central Energy Center Hybrid | AZ | rte_gt_1,pv_same_plant
61679 | Cox Battery Energy Storage | MO | rte_gt_1
61721 | Baldwin (CA) | CA | rte_gt_1
61730 | MA Solar Storage 1 Hybrid | MA | pv_same_plant,dc_coupled
61737 | Navy Yard Peaker Station | PA | rte_gt_1
61741 | Kingsberry Energy Storage System | TX | colocated_firming
61763 | Sunshine Gateway Solar Energy Center | FL | pv_same_plant
61795 | Pacific Union College BESS | CA | rte_gt_1
61851 | Campbell Industrial Park BESS | HI | rte_gt_1,colocated_firming
61861 | AES ES GILBERT | AZ | rte_gt_1
61901 | Redstone Arsenal Hybrid | AL | rte_gt_1,pv_same_plant
61956 | MCRD Parris Island PV Hybrid | SC | rte_gt_1,pv_same_plant,dc_coupled
61990 | TAC-Distributed Energy Resource Hybrid | IL | pv_same_plant
61993 | Gavilan Community College Solar Project | CA | pv_same_plant
61995 | UC Merced Solar Hybrid | CA | rte_gt_1,pv_same_plant
62027 | Caldwell Wastewater Treatment Plant Hybr | NJ | colocated_firming,pv_same_plant
62219 | Ashburnham Energy Storage Project | MA | rte_gt_1
62235 | Lone Star Solar | SC | colocated_firming,pv_same_plant,dc_coupled
62241 | NorWest Energy 9 LLC | OR | pv_same_plant
62248 | Arrow Canyon Solar Hybrid | NV | rte_gt_1,pv_same_plant,dc_tight
62381 | GMP Solar/Storage-Milton Hybrid | VT | rte_gt_1,pv_same_plant
62382 | GMP Solar/Storage-Ferrisburgh Hybrid | VT | rte_gt_1,pv_same_plant
62383 | GMP Solar/Storage-Essex Hybrid | VT | rte_gt_1,pv_same_plant
62441 | Kearny Mesa Storage LLC | CA | colocated_firming
62444 | Meyersdale Battery | PA | rte_gt_1
62490 | Echo River Solar | FL | pv_same_plant
62494 | Skeleton Creek Energy Center Hybrid | OK | pv_same_plant
62529 | Hale Kuawehi Solar Hybrid | HI | pv_same_plant
62541 | Lake Placid Solar Power Plant | FL | colocated_firming,pv_same_plant,dc_coupled
62561 | Roadrunner, LLC Hybrid | TX | pv_same_plant
62579 | Plainfield Community Solar LLC | MA | colocated_firming,pv_same_plant
62617 | Searcy Solar Hybrid | AR | pv_same_plant,dc_coupled
62652 | Happy Hollow CSG Hybrid | MA | pv_same_plant,dc_tight
62682 | Noland Wastewater Treatment Plant Hybrid | AR | rte_gt_1,pv_same_plant
62683 | Westside Wastewater Treatment Plant Hybr | AR | rte_gt_1,pv_same_plant
62695 | CED Northampton Solar LLC Hybrid | MA | colocated_firming,pv_same_plant
62745 | Wheatridge Hybrid | OR | pv_same_plant,dc_coupled
62753 | Prospect Storage | TX | rte_gt_1
62839 | 98th Street Battery Storage Station | NY | rte_gt_1
62856 | Marengo Battery Storage LLC | IL | rte_gt_1
62937 | Athens BESS | MN | colocated_firming
62968 | Syncarpha Tewksbury Hybrid CSG | MA | pv_same_plant
62969 | Syncarpha Puddon I Hybrid CSG | MA | pv_same_plant
62970 | Syncarpha Puddon II Hybrid CSG | MA | pv_same_plant
62971 | Syncarpha Westminster Hybrid CSG | MA | pv_same_plant
62972 | Syncarpha Leicester Hybrid CSG | MA | rte_gt_1,pv_same_plant,dc_coupled
62973 | Syncarpha Halifax Hybrid CSG | MA | rte_gt_1,pv_same_plant
62974 | Syncarpha Millbury Hybrid (CSG) | MA | pv_same_plant
62975 | Syncarpha Blandford Hybrid CSG | MA | rte_gt_1,pv_same_plant
62976 | Syncarpha Northampton Hybrid CSG | MA | pv_same_plant
62977 | Syncarpha Northbridge I Hybrid(CSG) | MA | pv_same_plant
62978 | Syncarpha Northbridge II Hybrid CSG | MA | pv_same_plant
62999 | Finchville Solar, LLC Hybrid CSG | NY | rte_gt_1,pv_same_plant,dc_tight
63000 | RT 52 Walden Solar 1, LLC Hybrid | NY | rte_gt_1,pv_same_plant
63011 | Cronin Road Solar 1, LLC CSG Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
63044 | Ryan Road Solar LLC Hybrid(CSG) | MA | pv_same_plant,dc_tight
63090 | Athens - Coopers Corner BESS | MN | colocated_firming
63091 | UC Santa Cruz Solar | CA | pv_same_plant
63150 | Pohatcong Solar Farm | NJ | pv_same_plant
63172 | Arroyo Solar Energy Storage Hybrid | NM | pv_same_plant
63186 | Imeson Solar | FL | pv_same_plant,dc_tight
63214 | Middleton Solar Park | MA | pv_same_plant
63255 | 2W Permian Solar Project Hybrid | TX | pv_same_plant
63264 | Partridge Hill Solar Hybrid | MA | pv_same_plant,dc_tight
63280 | AES Kekaha Solar, LLC Hybrid | HI | rte_gt_1,pv_same_plant,dc_tight
63324 | Camp Atterbury Microgrid Hybrid | IN | rte_gt_1,pv_same_plant
63337 | Lansing Renewables, LLC | NY | pv_same_plant,dc_coupled
63338 | Granby Solar, LLC CSG | MA | pv_same_plant,dc_coupled
63339 | Hales Mills Solar, LLC | NY | pv_same_plant,dc_coupled
63340 | Owlville Creek Solar 2, LLC | NY | pv_same_plant,dc_coupled
63341 | Owlville Creek Solar, LLC | NY | pv_same_plant,dc_coupled
63352 | Gemini Solar Hybrid | NV | pv_same_plant,dc_coupled
63398 | Kearsarge Amesbury Hybrid | MA | colocated_firming,pv_same_plant
63415 | Middletown Solar 1, LLC Hybrid CSG | NY | rte_gt_1,pv_same_plant,dc_tight
63420 | Fresno Bullard High School Hybrid | CA | rte_gt_1,pv_same_plant
63421 | Fresno Hoover High School Hybrid | CA | rte_gt_1,pv_same_plant
63422 | Fresno Sunnyside High School Hybrid | CA | pv_same_plant
63435 | Partridge Solar Project CSG Hybrid | MA | pv_same_plant
63468 | Hurteau Solar Project Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
63469 | Alicea Solar Project Hybrid CSG | MA | pv_same_plant,dc_tight
63470 | McDougle-Mitchell Solar Project Hybrid C | MA | pv_same_plant,dc_tight
63472 | Cycz Solar Project CSG Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
63473 | West A&B Solar Project Hybrid CSG | MA | pv_same_plant,dc_tight
63474 | Annese Solar Project Hybrid CSG | MA | pv_same_plant,dc_tight
63475 | Randall Solar Project Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
63486 | D'Arrigo Brothers - Phase 4 | CA | pv_same_plant
63510 | Walnut Unified School District Walnut HS | CA | pv_same_plant
63522 | Hickory Park Solar Hybrid | GA | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled
63535 | Solar BESS Hybrid | GA | pv_same_plant
63554 | Mohave Electric Cooperative at Joy Lane | AZ | pv_same_plant
63585 | NY3 Battery | NY | rte_gt_1
63721 | Cool Springs Solar (Hybrid) | GA | rte_gt_1,pv_same_plant,dc_coupled
63722 | Rawhide Prairie Solar Hybrid | CO | pv_same_plant
63723 | Ho'Ohana Solar 1 | HI | colocated_firming,pv_same_plant
63727 | Slate Hybrid | CA | colocated_firming,pv_same_plant
63728 | Taos Mesa Energy Facility Hybrid | NM | pv_same_plant
63731 | Neptune Energy Center Hybrid | CO | colocated_firming,pv_same_plant
63763 | CES Agawam Tuckahoe Solar Hybrid | MA | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled
63774 | Mount Kisco Landfill Solar & Storage CSG | NY | colocated_firming,pv_same_plant
63776 | Thunder Wolf Energy Center Hybrid | CO | colocated_firming,pv_same_plant
63804 | Partridgeville Hybrid CSG | MA | pv_same_plant
63805 | Williamsville Hybrid CSG | MA | pv_same_plant
63843 | Johanna Energy Center, LLC | CA | colocated_firming
63848 | Solar Blue | CA | pv_same_plant
63849 | Chestnut | CA | pv_same_plant
63859 | Golden Field Solar III, LLC | CA | pv_same_plant
63891 | Saticoy | CA | rte_gt_1
63892 | Lily Solar Hybrid | TX | pv_same_plant
63900 | AES Waikoloa Solar Hybrid | HI | rte_gt_1,pv_same_plant,dc_tight
63905 | Azure Sky Solar | TX | pv_same_plant
63913 | Dodge Flat | NV | rte_gt_1,pv_same_plant,dc_tight
63930 | Cal Flats BESS | CA | rte_gt_1,colocated_firming
63933 | Dry Lake Solar Energy Center | NV | pv_same_plant
64000 | Amaterasu LLC | MA | pv_same_plant,dc_tight
64042 | Montague Road Solar | MA | colocated_firming,pv_same_plant
64050 | Fort Bragg - Camp Mackall PV BESS System | NC | pv_same_plant,dc_coupled
64084 | Blanchard Road 1 Community Solar | NY | pv_same_plant,dc_tight
64087 | Blanchard Road 2 Community Solar | NY | pv_same_plant,dc_tight
64090 | NYS Rte 12 Community Solar | NY | pv_same_plant,dc_tight
64092 | Great Lakes Seaway Community Solar | NY | pv_same_plant,dc_tight
64103 | Desert Harvest II LLC | CA | pv_same_plant,dc_coupled
64105 | Maverick Solar 6, LLC | CA | rte_gt_1,pv_same_plant,dc_coupled
64128 | Ware Palmer Road Solar LLC CSG | MA | colocated_firming,pv_same_plant,dc_coupled
64129 | East Brookfield Adams Road Solar LLC CSG | MA | colocated_firming,pv_same_plant,dc_coupled
64140 | BWC Stony Brook, LLC Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
64147 | ZPD-PT Solar Project 2017-038 Hybrid LLC | MA | rte_gt_1,pv_same_plant,dc_tight
64148 | Fish Springs | NV | rte_gt_1,pv_same_plant,dc_tight
64170 | BWC Muddy Brook, LLC Hybrid | MA | pv_same_plant,dc_tight
64182 | BWC Lake Lashaway, LLC Hybrid | MA | pv_same_plant,dc_tight
64185 | ZPD-PT Solar Project 2017-023 LLC Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
64187 | ZPD-PT Solar Project 2017-021 LLC Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
64197 | Fifth Standard Solar PV, LLC (Hybrid) | CA | pv_same_plant
64198 | Horn Rapids Solar, Storage and Training | WA | rte_gt_1,colocated_firming,pv_same_plant
64202 | Big Star Solar, LLC (Hybrid) | TX | pv_same_plant
64210 | Bellefield Solar and Energy Storage Farm | CA | pv_same_plant
64213 | Auburn Solar Project | MA | pv_same_plant,dc_coupled
64222 | Burt County Solar Hybrid | NE | colocated_firming,pv_same_plant
64223 | Dodge County Solar Hybrid | NE | colocated_firming,pv_same_plant
64231 | Hadley 3 Solar (North) | MA | pv_same_plant
64232 | Hadley 3 Solar (South) | MA | colocated_firming,pv_same_plant
64256 | AES Maui Kuihelani Solar Hybrid | HI | pv_same_plant,dc_coupled
64374 | Norwich Solar and Energy Storage CSG | NY | rte_gt_1,colocated_firming,pv_same_plant,dc_tight
64395 | ZPD-PT Solar Project 2017-006 LLC Hybrid | MA | rte_gt_1,pv_same_plant,dc_tight
64400 | BYU - Hawaii | HI | pv_same_plant
64426 | Wilmot Energy Center LLC | AZ | pv_same_plant
64432 | Breckenridge Solar | MA | pv_same_plant
64436 | Wilmarth Solar | MA | pv_same_plant
64442 | Mt Pleasant Community Center | NY | pv_same_plant
64446 | Arlington Microgrid | WA | colocated_firming,pv_same_plant
64450 | Grissom Solar, LLC | NC | pv_same_plant
64453 | Volney II | NY | colocated_firming,pv_same_plant,dc_tight
64481 | Arlington Energy Center II | CA | pv_same_plant
64489 | Resurgence Solar | CA | pv_same_plant
64508 | Hall Solar Energy Storage | NC | pv_same_plant
64509 | South River H4 Solar Energy Storage | NC | pv_same_plant
64510 | Arba Solar Energy Storage | NC | pv_same_plant
64511 | Rose Acre Solar Energy Storage | NC | pv_same_plant
64512 | Hamlet Solar Energy Storage | NC | pv_same_plant
64513 | Wake RJ3 Solar Energy Storage | NC | pv_same_plant
64514 | Ludie Brown Solar Energy Storage | NC | pv_same_plant
64516 | Lowe Solar Energy Storage | NC | pv_same_plant
64520 | Spencer Meadow Solar Energy Storage | NC | pv_same_plant
64522 | Old Cedar Solar Energy Storage | NC | rte_gt_1,pv_same_plant
64529 | Golden Triangle | MS | pv_same_plant
64534 | Darien Solar | WI | pv_same_plant
64564 | Arlington Energy Center III | CA | pv_same_plant
64601 | County of San Diego COC Hybrid | CA | rte_gt_1,pv_same_plant
64611 | SEPV Sierra | CA | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled
64617 | Kearsarge William Way | MA | pv_same_plant
64618 | Kearsarge Haverhill | MA | pv_same_plant
64619 | Kearsarge Upper Union | MA | pv_same_plant
64620 | Kearsarge Montague BD(CSG) | MA | pv_same_plant
64624 | Hudson - High Desert Hybrid | CA | pv_same_plant,dc_coupled
64627 | Blodgett Solar CSG | MA | pv_same_plant
64630 | Rabbitbrush Solar, LLC | CA | pv_same_plant,dc_tight
64633 | Rexford Solar Farm | CA | pv_same_plant
64640 | Hot Springs Energy Storage & Microgrid | NC | pv_same_plant,dc_coupled
64656 | AES West Oahu Solar Hybrid | HI | rte_gt_1,pv_same_plant,dc_coupled
64664 | Clark Road Solar 1, LLC | MA | colocated_firming,pv_same_plant,dc_coupled
64672 | Blue Jay Solar I, LLC | TX | pv_same_plant
64686 | Orangeville Storage | NY | rte_gt_1,dc_coupled
64695 | Angel Fire Energy Facility | NM | pv_same_plant
64696 | Dunstable Solar 1, LLC | MA | rte_gt_1,pv_same_plant,dc_tight
64719 | Glenmere Lake | NY | rte_gt_1,pv_same_plant,dc_tight
64726 | West Haydenville PJ Community Solar | MA | rte_gt_1,pv_same_plant,dc_tight
64727 | Brookwood Drive Community Solar | MA | pv_same_plant,dc_tight
64731 | Maple(CSG) | MA | pv_same_plant
64752 | John Hopkins Middle School Microgrid | FL | rte_gt_1,pv_same_plant,dc_coupled
64759 | Old Middleboro Road Solar | MA | pv_same_plant,dc_coupled
64766 | Redwood Coast Airport Microgrid | CA | colocated_firming,pv_same_plant,dc_coupled
64844 | Three Rivers Solar LLC | MA | pv_same_plant,dc_coupled
64851 | Daggett 2 | CA | rte_gt_1,pv_same_plant
64852 | Daggett 3 | CA | pv_same_plant
64864 | Chaparral Springs | CA | pv_same_plant,dc_tight
64875 | 276 Federal Rd(CSG) | MA | rte_gt_1,pv_same_plant
64876 | 0 Hammond St CSG | MA | rte_gt_1,pv_same_plant
64877 | Edwards Sanborn E3 | CA | rte_gt_1,pv_same_plant
64878 | Edwards Sanborn E1A | CA | rte_gt_1,pv_same_plant
64879 | Edwards Sanborn E2 | CA | pv_same_plant
64881 | NMSU Solar and Storage | NM | colocated_firming,pv_same_plant
64908 | Scarlet Solar (CA) | CA | pv_same_plant
64928 | Edwards Sanborn S3 | CA | rte_gt_1,pv_same_plant
64929 | Edwards Sanborn S1 | CA | rte_gt_1,pv_same_plant
64970 | 59 Federal Rd(CSG) | MA | pv_same_plant
64980 | UMass Boston | MA | pv_same_plant
64993 | BigBeau Solar, LLC | CA | rte_gt_1,pv_same_plant,dc_coupled
65007 | Grant County | WI | rte_gt_1,pv_same_plant
65011 | Wood County | WI | rte_gt_1,pv_same_plant
65014 | ASD Cotuit MA Solar LLC | MA | pv_same_plant,dc_coupled
65015 | ASD Wallum MA Solar LLC(CSG) | MA | colocated_firming,pv_same_plant,dc_coupled
65028 | Roseland Solar Project, LLC | TX | pv_same_plant
65029 | Bissell Solar and Battery Generator | MI | rte_gt_1,colocated_firming,pv_same_plant
65053 | Blythe Mesa Solar II | CA | colocated_firming,pv_same_plant
65054 | 71 Charlotte Furnace Rd Hybrid(CSG) | MA | rte_gt_1,pv_same_plant
65055 | 77 Farm to Market Rd Hybrid(CSG) | MA | rte_gt_1,pv_same_plant
65056 | 160 Tihonet Rd Hybrid(CSG) | MA | rte_gt_1,pv_same_plant
65057 | 299 Farm to Market Rd Hybrid(CSG) | MA | rte_gt_1,pv_same_plant
65058 | Waiawa Solar Power Hybrid | HI | rte_gt_1,pv_same_plant
65114 | 196 Tremont St(CSG) | MA | pv_same_plant
65132 | University of the Pacific | CA | pv_same_plant
65154 | UMass PV Lot 22 | MA | pv_same_plant,dc_coupled
65174 | Cranberry Highway Solar LLC | MA | rte_gt_1,pv_same_plant,dc_coupled
65217 | South Goshen Community Solar | NY | pv_same_plant,dc_tight
65242 | Charlemont A | MA | pv_same_plant,dc_coupled
65271 | Noble Solar | TX | pv_same_plant
65291 | Golden Triangle II | MS | pv_same_plant,dc_coupled
65351 | General Dynamics | AR | pv_same_plant
65382 | Lincoln WWTF Hybrid | CA | pv_same_plant
65408 | Gilead Oceanside Solar Project | CA | pv_same_plant
65409 | Gilead Foster City Solar Project | CA | rte_gt_1,pv_same_plant
65422 | FPL Chipola River Solar Energy Center | FL | pv_same_plant
65429 | FPL Shirer Branch Solar Energy Center | FL | pv_same_plant
65433 | Blackwater River Solar Energy Center | FL | pv_same_plant
65441 | USS Itasca Clean Energy Solar LLC | MN | pv_same_plant
65468 | Highland Park Borough Solar | NJ | colocated_firming,pv_same_plant
65469 | Sealed Air Madera Solar Project | CA | pv_same_plant,dc_coupled
65562 | Amazon Bakersfield 1 Solar Project | CA | pv_same_plant
65568 | Google Moffett Park Solar Project | CA | pv_same_plant,dc_coupled
65569 | Gilead Sciences La Verne Rooftop Solar | CA | pv_same_plant
65614 | Orange Coast College PH2 Solar Project | CA | rte_gt_1,pv_same_plant
65644 | Lumina II Solar Project | TX | pv_same_plant
65645 | Lumina Solar Project | TX | pv_same_plant
65650 | Brockelman Road Solar 2 | MA | colocated_firming,pv_same_plant,dc_coupled
65664 | Sandrini Solar 100 | CA | colocated_firming,pv_same_plant
65669 | Faunce Corner Community Solar | MA | pv_same_plant
65670 | Ventura | MA | pv_same_plant
65674 | Edwards Sanborn E1B | CA | pv_same_plant
65675 | Edwards Sanborn E4 | CA | pv_same_plant,dc_coupled
65676 | Edwards Sanborn E5 | CA | pv_same_plant
65677 | Edwards Sanborn S4 | CA | pv_same_plant,dc_coupled
65693 | TX10 Hummingbird Storage | TX | dc_coupled
65695 | TX12 Silicon Hill Storage | TX | rte_gt_1
65697 | Walnut Grove Demonstration Plant | MS | pv_same_plant,dc_coupled
65698 | TX15 Limousin Oak Storage | TX | dc_coupled
65711 | Vikings Energy Farm | CA | pv_same_plant
65734 | Oberon Solar Project | CA | colocated_firming,pv_same_plant
65735 | Oberon II Solar Project | CA | colocated_firming,pv_same_plant
65743 | Victory Pass | CA | rte_gt_1,pv_same_plant
65744 | Arica Solar | CA | pv_same_plant
65815 | NY - Mines Press | NY | colocated_firming,pv_same_plant,dc_coupled
65820 | Ocotillo Wells | CA | pv_same_plant
65866 | Canoe | FL | pv_same_plant
65886 | Tenmile Creek | FL | pv_same_plant
65888 | Kayak | FL | pv_same_plant
65927 | Fourmile Creek | FL | pv_same_plant
65940 | Shasta College PH2 Solar Project | CA | pv_same_plant
65945 | Brookville Smart Bus Depot Microgrid | MD | pv_same_plant
65950 | Kearsarge 100 Sohier Rd | MA | pv_same_plant
65956 | Storey Solar and Storage | AZ | pv_same_plant
65962 | Mesquite Solar 4, LLC | AZ | rte_gt_1,pv_same_plant
65963 | Mesquite Solar 5, LLC | AZ | pv_same_plant
65967 | Paris Solar | WI | pv_same_plant
65987 | Desert Peak Energy Storage I | CA | rte_gt_1
65988 | Desert Peak Energy Storage II | CA | rte_gt_1
66023 | Grossmont-Cuyamaca-Cuyamaca Col. Solar & | CA | colocated_firming,pv_same_plant
66048 | Middleton Biogas Solar, LLC | WI | colocated_firming,pv_same_plant,dc_coupled
66075 | Blacksmith Road Solar 1 | MA | colocated_firming,pv_same_plant
66076 | Electric Avenue Lunenburg Solar 1 | MA | pv_same_plant,dc_coupled
66128 | Lake Mabel Solar and Battery Storage | FL | colocated_firming,pv_same_plant
66129 | Dover Solar and Battery Storage | FL | colocated_firming,pv_same_plant
66137 | Zier Solar | TX | pv_same_plant
66163 | Jicarilla Solar 1 LLC | NM | pv_same_plant
66178 | South 49th 013445 SCS Norfolk, LLC | NE | pv_same_plant
66180 | Huxley Solar | MA | colocated_firming,pv_same_plant,dc_tight
66181 | Beacon Solar, LLC | MA | colocated_firming,pv_same_plant,dc_tight
66182 | Town of Amherst Solar | MA | colocated_firming,pv_same_plant,dc_tight
66218 | Dubois Solar (Hybrid) | NY | rte_gt_1,pv_same_plant,dc_coupled
66222 | Landau II Solar (Hybrid) | NY | rte_gt_1,pv_same_plant,dc_coupled
66228 | Salt Point Solar (Hybrid) | NY | rte_gt_1,pv_same_plant,dc_coupled
66232 | Svenski Solar (Hybrid) | NY | pv_same_plant,dc_tight
66263 | Eleven Mile Solar Center | AZ | pv_same_plant
66270 | Proxima | CA | pv_same_plant
66271 | Ameresco HCE Solar LLC | CO | pv_same_plant
66357 | Yellow Pine Solar | NV | pv_same_plant
66408 | Buena Vista Energy Center | NM | pv_same_plant,dc_coupled
66420 | Five Wells Solar Center - Hybrid | TX | colocated_firming,pv_same_plant
66474 | MA Blackstone | MA | pv_same_plant,dc_coupled
66488 | Davis Solar | NY | pv_same_plant,dc_tight
66499 | Federalsburg Energy Storage 1 LLC | MD | pv_same_plant,dc_coupled
66501 | Cicero Energy Storage 1 LLC | NY | pv_same_plant,dc_coupled
66503 | Cicero Energy Storage 2 LLC | NY | pv_same_plant,dc_coupled
66509 | CA Manteca 730 Spreckels Ave | CA | pv_same_plant,dc_coupled
66517 | TX Houston 7080 Express Lane | TX | pv_same_plant
66532 | BCE Los Alamitos 2 | CA | pv_same_plant
66533 | BCE Los Alamitos 1 | CA | pv_same_plant
66540 | Shamrock Wind | TX | colocated_firming
66574 | San Juan Solar I | NM | pv_same_plant
66598 | Baldy Mesa Solar & Storage | CA | pv_same_plant,dc_coupled
66608 | Craighead Electric Solar One | AR | pv_same_plant
66620 | Resurgence Solar II | CA | pv_same_plant
66627 | Sonoran Solar Energy | AZ | pv_same_plant
66629 | Envoy Solar, LLC | MO | pv_same_plant
66636 | McFarland A Solar and Storage | AZ | pv_same_plant
66637 | McFarland B Solar and Storage | AZ | pv_same_plant,dc_coupled
66688 | Bright Arrow Solar, LLC | TX | pv_same_plant
66694 | Atrisco Energy Storage | NM | rte_gt_1
66699 | Lockhart Solar PV II | CA | pv_same_plant
66717 | Eastover Solar | SC | pv_same_plant,dc_coupled
66764 | SCH - (2A) 156 Barhydt Rd Glenville | NY | colocated_firming,pv_same_plant,dc_coupled
66765 | SCH County - (2B) 4982 Rynex Corners Rd | NY | pv_same_plant,dc_coupled
66767 | Source Power Company - Richland | NY | pv_same_plant,dc_coupled
66772 | Estrella Solar & Storage | CA | pv_same_plant
66773 | Raceway Solar & Storage | CA | pv_same_plant
66799 | Bishop Ranch - BR 1-Y | CA | pv_same_plant
66800 | Bishop Ranch - BR 8-P | CA | pv_same_plant
66801 | Fence Post Solar Hybrid Project, LLC | TX | pv_same_plant
66807 | SEPV Cuyama Hybrid | CA | pv_same_plant,dc_coupled
66814 | Sky Ranch Solar | NM | pv_same_plant
66871 | GulfStar Power, LLC | TX | pv_same_plant
66872 | Estonian Solar Project, LLC | TX | pv_same_plant
66885 | Baldy Mesa 2_Silver Peak Hybrid | CA | pv_same_plant,dc_coupled
66890 | SF Azalea, LLC | CA | pv_same_plant
66905 | Ables Springs Solar & Storage | TX | pv_same_plant
66925 | SR McNeal | AZ | pv_same_plant
66951 | Scarlet II Hybrid | CA | pv_same_plant
67019 | Copperhead Solar, LLC | TX | pv_same_plant
67039 | Northern Orchard Solar PV, LLC | CA | pv_same_plant,dc_coupled
67091 | Yellow Pine II | NV | pv_same_plant
67092 | Paulsell | CA | pv_same_plant
67119 | Ring Road | MA | pv_same_plant,dc_coupled
67170 | Amazon SAN3 Solar Project | CA | pv_same_plant,dc_coupled
67178 | Mohave Energy - Hybrid | AZ | colocated_firming,pv_same_plant,dc_coupled
67241 | 401 South | MA | pv_same_plant
67242 | 5 Berry | MA | pv_same_plant,dc_tight
67275 | White Plains_RFP-Gedney Way Landfill | NY | colocated_firming,pv_same_plant
67276 | Upland | MA | pv_same_plant,dc_coupled
67277 | Bishop Ranch - BR 15-DD | CA | pv_same_plant
67278 | Bishop Ranch - BR 2600 | CA | pv_same_plant
67281 | FFP - NY Urbanski | NY | rte_gt_1,colocated_firming,pv_same_plant,dc_coupled
67282 | FFP - NY Varano | NY | colocated_firming,pv_same_plant,dc_coupled
67284 | Ganado Solar | TX | pv_same_plant
67285 | Sun Streams 3 | AZ | colocated_firming,pv_same_plant
67288 | Foster Clean Power A | CA | pv_same_plant,dc_coupled
67291 | Sun Streams 4 | AZ | colocated_firming,pv_same_plant
67296 | CVEC Round 4 Brewster Captn Golf Course | MA | colocated_firming,pv_same_plant
67321 | Yuma Solar + Storage | AZ | pv_same_plant
67322 | Mamm Creek | CO | colocated_firming,pv_same_plant,dc_coupled
67323 | High Mesa CO | CO | colocated_firming,pv_same_plant,dc_coupled
67457 | 665 Scenic Highway | MA | pv_same_plant,dc_coupled
67464 | 1 Commercial | MA | pv_same_plant,dc_coupled
67474 | Harquahala 2 | AZ | pv_same_plant
67489 | Cavalry Solar Hybrid | IN | pv_same_plant
67503 | Serrano | AZ | colocated_firming,pv_same_plant
67528 | Milagro Solar I | NM | pv_same_plant
67545 | Marshall Solar Plus LLC | MN | colocated_firming,pv_same_plant
67577 | Monument Valley | MA | pv_same_plant,dc_tight
67578 | Sandwich | MA | pv_same_plant,dc_tight
67695 | Holtville | CA | rte_gt_1
67710 | TAG | NM | pv_same_plant
67743 | Bishop Ranch BR 1-X | CA | pv_same_plant
67745 | White Plains RFP Shapham Place | NY | colocated_firming,pv_same_plant
67762 | Stampede Solar Hybrid | TX | pv_same_plant
67764 | Rosamond South 1 | CA | pv_same_plant
67843 | Farmersville West | TX | rte_gt_1
67850 | Arrowleaf Solar and Storage | CA | pv_same_plant
67859 | Foster Clean Power B | CA | pv_same_plant,dc_coupled
67867 | Liberty Hybrid Solar and Storage Project | TX | pv_same_plant
67893 | Dunns Bridge II Solar | IN | pv_same_plant
67898 | Escape Solar Plant | NV | pv_same_plant
68023 | BCE Seal Beach | CA | colocated_firming,pv_same_plant
68064 | CA- US Foods- Livermore | CA | colocated_firming,pv_same_plant
68069 | Old Frontier Solar III | MA | pv_same_plant,dc_coupled
68147 | Coffeen Solar BESS | IL | pv_same_plant
68148 | Baldwin Solar BESS | IL | pv_same_plant
68266 | North Juvenile Detention Center Solar | CA | pv_same_plant
68460 | Roadrunner Crossing Energy Storage | TX | colocated_firming
68522 | Bishop Ranch - BR 8-O | CA | pv_same_plant
68523 | Bishop Ranch - BR 8-Q | CA | pv_same_plant
68524 | Bishop Ranch - BR 15-AA | CA | pv_same_plant
68525 | Bishop Ranch - BR 15-CC | CA | pv_same_plant
68547 | Tipton 1 - (CA) | CA | pv_same_plant
68548 | Tipton 2 - (CA) | CA | pv_same_plant
68605 | Mauna Loa Macadamia Nut | HI | pv_same_plant
68679 | Partridge Solar | MA | pv_same_plant
68680 | Saddleback Solar | MA | pv_same_plant
68742 | Skyline Solar | MA | pv_same_plant
68743 | Adams Grove Solar | MA | pv_same_plant
68773 | Apollo | MA | colocated_firming,pv_same_plant,dc_coupled
68816 | Google Bayhill Solar PV and Microgrid | CA | pv_same_plant,dc_coupled
68868 | Shallow Basket | NM | pv_same_plant
68891 | Visalia - (CA) | CA | pv_same_plant
68906 | Pine Forest Solar I | TX | pv_same_plant
68950 | Marston Mills Solar | MA | pv_same_plant
68997 | Thermo Fisher Pleasanton | CA | pv_same_plant,dc_coupled
69042 | Kit Carson Co-Op | NM | pv_same_plant
69072 | Fresno-Clovis RWRF | CA | pv_same_plant
69073 | 20 Bedford | MA | pv_same_plant,dc_coupled
69075 | 376 Nash | MA | pv_same_plant,dc_coupled
69076 | 342 Circuit | MA | pv_same_plant,dc_coupled
69129 | Dudley Landfill Solar LLC | MA | pv_same_plant,dc_coupled
69131 | Hampden Landfill Solar LLC | MA | pv_same_plant,dc_coupled
69187 | Big Bend 1 Solar and Battery Storage | FL | pv_same_plant
69190 | GreenStruxure BBU004, LLC | CA | pv_same_plant,dc_coupled
69191 | GreenStruxure REP009, LLC | CA | dc_coupled
69210 | Salem Henningsen | OR | pv_same_plant
69288 | Palm Springs DAC PV | CA | pv_same_plant
69414 | Blevins Solar & Storage | TX | pv_same_plant
69544 | 0 Middle | MA | pv_same_plant,dc_coupled
69545 | 15 Lincoln | MA | pv_same_plant,dc_coupled
69568 | NL MA - Division | MA | pv_same_plant,dc_coupled
69680 | BHER Ravenswood Solar 1 | WV | pv_same_plant
69712 | San Diego Sockers | CA | pv_same_plant
69727 | Martinsville BESS | VA | rte_gt_1
70111 | Kern Co Sheriff | CA | pv_same_plant
70307 | Milk Street Solar, LLC | MA | pv_same_plant
70384 | Yorktown NY 1, LLC | NY | pv_same_plant

## assumptions
id | area | assumption | value | rationale | validated
B1 | Data | EIA-923 2025 file is the Final release (spec named the early release) | Final | EIA now serves Final | yes
B2 | Data | Battery rows = Page 1 Energy Storage with prime mover BA and fuel MWH; Quantity = charge; Grossgen = discharge | - | Spec | yes
B3 | Data | EIA-923 annual respondents (dominant 2019-2022) have EIA-allocated monthly values: excluded from the regression and from monthly signatures (ANNUAL_RESPONDENT) | - | Same finding as gas build | yes
B4 | Capacity | E_rated per plant-year from each EIA-860 vintage (Operable + retired that year); plants missing from a vintage borrow the nearest vintage (flagged) | - | Spec: time-varying E_rated | yes
B5 | Hybrid | Hybrid if RTE>1 in any month or Co-Located Renewable Firming=Y or DC coupled=Y or PV at the same Plant Id; excluded from fleet efficiency stats | - | Spec + 2025 860 coupling fields | yes
B6 | Decomposition | Usable months: C>0 D>0 C/D<3 EFC>0.10 monthly respondent; >=10 months; eta in (0.5 1] | 10 / 0.10 | Spec | yes
B7 | Decomposition | Seasonal P_aux fitted jointly with one shared intercept (eta is not seasonal) and season-specific slopes; >=3 months per season | - | Separate small fits are unstable | partly
B8 | Decomposition | Naive RTE for the gap = site mean of monthly apparent RTE (reproduces spec 0.844); throughput-weighted also reported | - | Definition not stated in spec | partly
B9 | Peers | UTI peers: same BA + duration band + age +-3y; healthy (RTE>=0.75 & throughput>0; standalone); >=3 peers; ladder drop age then national same band | 3 | Spec + coverage | no
B10 | In service | Site in service from first active month; trailing zeros stay in service (live outage) unless 860 lists the site retired | - | Pre-commissioning zero rows otherwise read as outages | partly
B11 | Signatures | Partial availability fractions {1/2 2/3 3/4 4/5 5/6 7/8} of trailing-6-month UTI median +-0.04 flat +-0.06 >=2 months with onset from >=0.9 | - | Spec M5 (quantised) | no
B12 | Signatures | Thermal/aux: HVAC excess above enclosure-type p90 (standalone fitted sites) or P_aux trend >20%/yr; applied to deficit months (summer for HVAC) | - | Spec rule 4 | no
B13 | Signatures | Hybrid sites skip efficiency-based rules 4-6 (their efficiency is contaminated) but keep availability rules 1-3 | - | Deviation from strict first-match order | partly
B14 | Deficit | Deficit = eta_true<0.86 or UTI<0.75 or P_aux>1% nameplate or monthly RTE >5 pts below duration-band median | - | Spec HEALTHY test | no
B15 | Fade | EPC = D/max(1 round(EFC)) / E_rated(year); slope of 12-month rolling p90; >=24 months and >50% months EFC>=0.5 else insufficient_history | - | Spec M6 | yes
B16 | Warranty | Contracted cycle life 6000 EFC when unknown (all sites) | 6000 | Spec (flagged) | no
B17 | Warranty | Operating envelope on monthly mean ambient -10..30 degC (assumed) | -10/30 | No contract data | no
B18 | Warranty | Cumulative EFC before 2019 = first-12-month EFC rate x months since COD | estimate | No pre-2019 load | no
B19 | Asymmetry | Realised asymmetry uses peak monthly average power (MWh/h); true peak power needs interval data | proxy | - | no
B20 | Loss | MWh at stake: outage/partial = shortfall vs trailing 6-month median (else peer EFC x E_rated); efficiency signatures = extra charge vs band-median RTE; thermal = excess aux MW x hours | - | Spec R6 (MWh not $) | partly
B21 | Reliability | Credibility tau = phi/lambda_pool; pool ladder BA+duration band+vintage -> duration band+climate -> duration band -> fleet; min 5 sites & 60 exposure-months | - | Spec R5 | no
B22 | Weather | nClimGrid county monthly mean (NSRDB needs an API key) | - | Spec fallback | partly
B23 | Money | No dollar figures: lost BESS MWh have no PPA price; monetisation needs nodal price data | - | Guardrail 6 | yes
B24 | Owner | Owner = EIA-860 Schedule 4 majority owner else operator; customer group / SSI-prospect not supplied | - | No CRM input | -